STATEMENT OF REQUIREMENTS

for the

Supply and Installation of High Speed Industrial Doors

Reference No: HO_BF_DS 18 215/064

# Background to requirement

## The Contracting Authority (the “Authority”) is the Home Office acting through Border Force. Border Force is a professional law enforcement command within the Home Office. It is responsible for securing the UK Border and controlling immigration at ports and airports across the UK and Northern France.

## 1.2	The Border Force Detection Technology Management Unit (DTMU) is a National team based in Border Force South East & Europe and is charged with the procurement and maintenance of clandestine detection technology and ancillary equipment used by Border Force, authorities and contractors within designated control zones.

## 1.3	 To augment the screening process motion detection systems are deployed in purpose-built accommodation to screen Roll on Roll off (Ro-Ro) freight (wheeled cargo, i.e. HGV trailers) and containers. The technology is designed to quickly and efficiently check for the presence of illegal migrants by using seismic sensors and bespoke algorithms. To operate effectively the motion detection systems must be operated within a wind proof environment. Generic accommodation comprises of a steel frame building clad with aluminium panelling.

## 1.4	Vehicle entrance and exit to the accommodation is controlled by high speed doors that compliment the wind proof environment. Personnel doors at either end of the shelter provide entrance and exit points for the operators and provide an alternative means of escape from the building if required. Traffic management systems and door safety systems help to prevent strikes and door damage.

# description

## The Authority requires the supply and installation of two (2) rigid high speed industrial doors (the “Goods”) at Border Force control points to Plymouth Brittany Ferry Port, Plymouth, PL1 3EW. All Goods supplied must be suitable for use in a Sea Port environment. ## The maximum delivery & installation lead-in time be 8 weeks from receipt of Home Office Purchase Order by the successful bidder.

# Technical specifications for the goods

## The Goods must meet safety and performance requirements set out in BS EN 13241

## The Goods must be of rigid construction. Flexible high-speed doors are specifically excluded from the scope of the requirement.

## The Goods must fit in with the existing shelter construction and door aperture. A site visit day will be arranged for bidders to view existing arrangements Current door dimensions are 5000 mm (h) x 4000 mm (w).

## The Goods must be compatible with UK & European power supply.

## All door motors are to be housed on the internal face of the door.

## The Goods must be power-operated with push button remote control method of operation. Manually operated doors are specifically excluded from the scope of the requirement.

## The Goods must have an Emergency off switch.

## In the event of an emergency or breakdown, the Goods must be able to be opened manually.

## The Goods must have integrated safety systems to prevent accidental door collisions by HGV’s & PLG’s. They will also conform to BS EN 12453 for use in a Type 2 environment. The Goods must be limited to ensure that the forces generated by the door when meeting a person or obstacle do not exceed the values specified in Annex A of BS EN 12453:2001.

## The Goods should have the option to include vision panels if required by the Authority.

## The Goods do not need to be acoustically insulated. Any acoustic properties will be considered as added value and not score any more marks at evaluation.

## Bidders are to indicate what material is used for the door leaf and to demonstrate that it conforms to the appropriate BS or equivalent. E.g. Steel to BS EN 10326 ≥0.4mm thick all galvanised to Z275g/m2 minimum & Aluminium to BS EN 485 ≥ 06mm thick.

## The Bidder will demonstrate that door production will be environmentally sourced as per BS EN 14040/14044.

# performance specifications for the goods

## The Goods must have a minimum opening speed of 1.5m/s and a maximum closing speed of 1.0m/s.

## The Goods must be suitable to the environment. This will be evaluated against conformity to BS or equivalent in regards to:

## Wind load performance (BS EN 12424) – the Goods must be a minimum of Class 3;

## Resistance to water (BS EN 12425) – the Goods must be a minimum of Class 3

## Air permeability (BS EN 12426) – the Goods must be a minimum of Class 2.

## The Goods design, specification & construction must comply with BS EN 13421-1 or equivalent.

## The Goods must be mechanically durable by conforming to BS EN 12604 or equivalent. Doors will be expected to withstand approximately 60 cycles per day, 365 days per year.

## The Goods must be professionally installed by appropriately certified Staff and installation must adhere to standards set out in BS EN 12635 or equivalent.

## The Goods must be capable of operation in temperature conditions ranging from -10°C to +40°C.

## The Goods must be thermally insulated and evaluated in line with standards set out in BS EN 13241 or equivalent. The Goods must achieve a maximum U value of 1.0W/m2K.

# Information for bidders

Any Tenders which do not fully comply with the Statement of Requirements will be deemed non-compliant and, at the Authority’s absolute discretion, will be excluded from further participation in this Tender.

All Tenders which are deemed to be fully compliant with the Authority’s Statement of Requirements shall be financially evaluated in the following manner;

The total evaluated cost shall be calculated on the sum of the;

- Supply, delivery, installation and commissioning of two (2) High Speed Roller Doors at Plymouth excluding VAT.

The award of contract shall be made on the basis of the lowest total evaluated cost of technically compliant Tenders.

Any questions, queries or clarifications regarding this tender should be submitted to Paul.Tooke@homeoffice.gov.uk by 12 noon on Wednesday 2nd January 2019 at the latest.

All bids must be submitted by e-mail to Paul.Tooke@homeoffice.gov.uk by 12 noon on Monday 7th January 2019 at the latest.

TERMS AND CONDITONS OF CONTRACT

The Government Legal Services short form Contract for the Supply of Goods (copy attached) shall apply to any resulting contract and/or Purchase Order.