Lindisfarne in Beal – Natural England Depot

Scoping Document PV Upgrade – February 2025

Generally

The works:  Involve the upgrading of the existing single-phase inverter and battery installation to a 3-phase inverter with additional batteries.

As Existing:

There is already a single-phase system, with PV strings connected to the inverters via a total of 4 strings from 3 roof / building mounted arrays, which is a 13kW system.

The current PV system is dual set up, with 4 strings to DC isolators, and connected to two Solax X3 G4 7.5kW hybrid inverters, see Schematic No1. These are wired back to the electrical network via individual 32A

CPD’s, A 63A RCBO and AC isolator to a 63A CPD in the main distribution board. See Schematic 1 for the configuration.

Existing system details and photos:

Photo 1: Shows the system, as currently installed on the first-floor landing area.

Photo 2: Shows the new 3 phase distribution board.

Photo 3: Shows the incoming mains and breakers located to the right of the 3-phase distribution board, all of which is located on the ground floor, and is directly below the Solax battery / inverter system.

Photo 4 and Site Plan: The Solax system is behind the middle roller shutter door, on the back wall.

Existing As Installed Information: Certification and details of the system. See attachment below.

- Scope of the works: Is to price and provide clarification / confirmation of all of the following within a quotation for the works:

  - The contractor is to provide a schematic: of the intended installation, in relation to the existing system.

  - Replacement of the inverters: Remove the 2 existing inverters and replace with a X3-Ultra 15 kW inverter. This to have a 2-port connection for the batteries and 4 string connectivity for the PV strings.

  - Batteries: Retain the two master 5.8kW batteries and add two 5.8kW slave batteries, and to be set up in ‘master + slave’ configuration. The contractor ‘must’ check that the new batteries are either a version 1 or version 2 to align with the existing master batteries already installed. These will sit in front of the existing batteries.

  - DC isolators and Connections: Adapt and include for the existing for the new set up, using the existing DC and AC isolators and re-connect the entire system, so that it conforms to manufacturers specifications, standards, and IEE 18th edition regulations. Utilise existing equipment as necessary.

  - Power and cabling: The system is currently isolated and needs to be set up to a 3-phase configuration to the new distribution unit (directly below the system). Each phase should be connected to allow the inverter to balance the loads across the site.

  - Containment: Include for all containment and new cabling, or utilise the existing, all to conform to IEE regulations 18th edition.

  - Existing equipment and cabling: strip out and remove from site redundant systems, and isolate /tidy up all cabling.

  - Connectivity to the Solax Cloud: Upon completion the contractor is to ensure the system is fully set up and re-configured to allow for remote monitoring both themselves and for the customer. Login details will be provided when on site.

  - Builders Works: Allow for all works that are non-electrical, associated with the installation.

  - Testing and Certification: Check and test all systems are working and provide an electrical certificate upon completion of the works.

2.0 Accreditation and Insurances: The contractor shall provide confirmation of registration of the NICEIC and be accredited to the MCS standards and also provide confirmation of Public liability insurance to a minimum of £1milllion.

3.0 Welfare: The site will provide access to toilets and a kitchen.

4.0 Access, location and Parking: The site is open from 8am until 4.30pm and is controlled via a CCTV system with card access. Parking is available within the ‘yard’ and you can unload directly adjacent building. All visits to be agreed with the Operational Manager, Andrew Craggs.

- The site is located: - Natural England, National Nature Reserve, Beal Station, Beal, Berwick-on-Tweed, Northumberland TD15 2SP.

5.0 Health and Safety: The contractor is expected to provide a set of RAMS prior to works commencing on site, and proof of qualifications for any installer, on the day.

6.0 Equipment and materials: The battery system should have a minimum of a 10-year warranty, a Certificate of Conformity and a manufacturers data sheet. All proof to be provided within the tender return.

7.0 Site Inspection: The contractor has the opportunity to visit site or utilise the information provided, in order to provide a fixed priced for the supply and installation of the Scope of Works.

8.0 Tender Return: The contractor is to provide the following documents with the tender return, on the due date, as set out within ‘Contract Finder’.

- Priced Scope of Works items 1.1 to 1.10 + 2.0 inclusive.

- Quotation with Specification / Material list

- Warranty confirmation for the battery and Inverter, plus a data sheet.

9.0 Procurement: Natural England will set up the successful contractor on their supplier list, and then raise an order for the works, with payment upon completion. Payment is usually within 14 days.

Schematic 1: System as installed.

Photo 1: Existing system, as is. Situated directly above the dist board, see photos 2 & 3

Photo 2: New 3 phase distribution board (directly below the solar system.

Photo 3: New incoming 3 phase cable to isolator and meter.

Site Location:  The Address: Beal Station, Beal, Berwick-on-Tweed, Northumberland TD15 2SP

Photo 4: The existing building with the Solax system, showing some of the PV panels.

Site Plan: Showing location within the existing building