## Compartmentation
CLIENT: Consillium Group Address: Armthrope Academy Details: Science Block GF & FF DOCUMENTATION: Survey of Observations & Costing
ID | Category | Location | Issue | Recommendation | Size/Quantity
430 | Compartmentation | Performing Arts | Unsealed void in brick wall between main hall and rooms | Install a fire resistant partition with a FR60 1200x600mm access hatch to allow access to main roof | 1200x1500mm partition 1200x600mm FR60 access hatch
433 | Compartmentation | S17 | The existing windows around the science lab S17 are not of fire resistant construction which are required around science labs due to the use of chemicals and gasses. | It is recommended that the windows are boarded using a shaft wall detail to provide a minimum of 30 minutes fire resistance between the classroom and the corridor | 1500x2000mm x 3no windows
439 | Compartmentation | S16 Store | Compartment wall in roof space has unsealed void which allows access through between compartments | Recommend installing a fire rated door and closer within the opening including closer and signage | FR30 Door
440 | Compartmentation | S16 Store | Head of roofspace compartment wall Is unsealed to underside of the roof covering | Install appropriate fire stopping materials along the head of wall to provide 30 minutes fire resistance installed in line with manufacturers installation specifications | Approx 20lm x 50mm batt mastic
441 | Compartmentation | S16 Store | Unsealed cable penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 250x250mm batt patress
442 | Compartmentation | S16 Store | Unsealed cable penetrations in metal trunken passing through plasterboard ceiling | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification | 100x100mm
443 | Compartmentation | S16 | Unsealed service penetrations passing through plaster ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 5no 40mm dia mastic
444 | Compartmentation | S16 Class | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 5x25mm 2x40mm2x15mm
446 | Compartmentation | S17 | The existing windows around the science lab S15 are not of fire resistant construction which are required around science labs due to the use of chemicals and gasses. | It is recommended that the windows are boarded using a shaft wall detail to provide a minimum of 30 minutes fire resistance between the classroom and the corridor | 1500x2000mm opening x 3no
448 | Compartmentation | S15 | Unsealed pvc pipe passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 300mm dia
450 | Compartmentation | S15 | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 7x30mm
452 | Compartmentation | S14 To Store | Compartment wall in roof space has unsealed void which allows access through between compartments | Recommend installing a fire rated door and closer within the opening including closer and signage | 2000x1200mm approx opening
453 | Compartmentation | S15 To Store | Ceiling to s15 store requires overboarding roof trusses to British gypsum standards to achieve 30minuites fire resistants | Ceiling to s15 store requires overboarding roof trusses to British gypsum standards to achieve 30minuites fire resistants | 8mx5m
454 | Compartmentation | S14 | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 10no 40mm mastic seals
456 | Compartmentation | Roof Void Above S10 | Unsealed cable penetrations passing through compartment brick wall | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification | 700x400mm
460 | Compartmentation | Exam Office | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 5x15mm 1x40mm
462 | Compartmentation | Corridor Outside Exam Office | Unsealed service penetrations passing through plasterboard ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 2no 40mm dia mastic seals
463 | Compartmentation | Exam Store | Unsealed cable penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 2x20mm 1x40mm
465 | Compartmentation | Main Hall | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 2no 80mm dia pipes
466 | Compartmentation | Main Hall | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 30MM
467 | Compartmentation | Main Hall | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 60mm pipe 40mm cables 100mm dia trunking
468 | Compartmentation | Main Hall | Section of lath and plaster ceiling is coming away from lath and is a health and safety risk | Recommend removing the section of plaster and reinstate with appropriate fireline plasterboard and sealed using appropriate fire resistant sealant | 600x600mm
472 | Compartmentation | South Hall | The existing windows in the wall from South Hall to corridor are not fire resistant glazing | It is recommended that the windows are boarded using a shaft wall detail to provide a minimum of 30 minutes fire resistance between the classroom and the corridor | 4no 1800x2000mm openings approx size
473 | Compartmentation | South Block Library | Unsealed service penetrations passing through plasterboard compartment wall | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 2no 300x300mm patress with graphite mastic
481 | Compartmentation | Chemical Store | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 6no 40mm dia mastic cables
484 | Compartmentation | South Block Corridor | Radiator pipes passing up through floor slab from basement unsealed | Seal all pipes using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | Allow for 40no 60mm dia mastic
485 | Compartmentation | South Block Basement | Unsealed cable penetrations passing through compartment plasterboard wall | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 1x400x150mm 1x200x100mm
486 | Compartmentation | South Block Basement | Unsealed service penetrations passing through compartment brick wall | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification | 600x600mm
487 | Compartmentation | South Block Basement | Unsealed pipe penetrations passing through concrete floor slab | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 200mm
488 | Compartmentation | English Store | Unsealed service penetrations passing through blockwork compartment wall | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 10no 40mm dia mastic
490 | Compartmentation | South block archive | Unsealed void in plasterboard ceiling | Seal using appropriate fire stopping materials such as fire batt in patress detail to underside of ceiling | 400x300mm batt mastic
492 | Compartmentation | Junior Block Crosscorridoor | Unsealed head of wall above crosscorridoor fire door | requires sealing with fire stopping materials installed in line with manufacturer installation specification to the underside of the roof | 1400x300mm
493 | Compartmentation | Electrical Switch Room Junior Block | The head of the plasterboard compartment wall lacks any form of fire stopping materials | Remove existing ceiling tiles and instal an appropriate fire stopping material such as Rockwool flexislab | 8lm x 400mm linear seal
494 | Compartmentation | Junior Block Crosscorridoor | Unsealed cable penetrations in pvc trunken passing through compartment plasterboard wall | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification to both sides of compartment wall | 40mmx2
496 | Compartmentation | S1 | Head of compartment wall which is required to be sealed to a 30 minute fire resistant standard | Lift ceiling tiles along head of dividing wall and install an appropriate fire stopping materials such as Rockwool flexislab to achieve the required fire resistance | 15lm x 400mm head of wall