## Compartmentation
CLIENT: Consillium Group Address: Armthrope Academy Details: Science Block GF & FF DOCUMENTATION: Survey of Observations & Costing
ID | Category | Location | Issue | Recommendation | Size/Quantity
430 | Compartmentation | Performing Arts | Unsealed void in brick wall between main hall and rooms | Install a fire resistant partition with a FR60 1200x600mm access hatch to allow access to main roof | 1200x1500mm partition 1200x600mm FR60 access hatch
441 | Compartmentation | S16 Store | Unsealed cable penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 250x250mm batt patress
442 | Compartmentation | S16 Store | Unsealed cable penetrations in metal trunken passing through plasterboard ceiling | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification | 100x100mm
443 | Compartmentation | S16 | Unsealed service penetrations passing through plaster ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 5no 40mm dia mastic
444 | Compartmentation | S16 Class | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 5x25mm 2x40mm2x15mm
448 | Compartmentation | S15 | Unsealed pvc pipe passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 300mm dia
450 | Compartmentation | S15 | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 7x30mm
454 | Compartmentation | S14 | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 10no 40mm mastic seals
456 | Compartmentation | Roof Void Above S10 | Unsealed cable penetrations passing through compartment brick wall | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification | 700x400mm
460 | Compartmentation | Exam Office | Unsealed service penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 5x15mm 1x40mm
462 | Compartmentation | Corridor Outside Exam Office | Unsealed service penetrations passing through plasterboard ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 2no 40mm dia mastic seals
463 | Compartmentation | Exam Store | Unsealed cable penetrations passing through plasterboard ceiling | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 2x20mm 1x40mm
465 | Compartmentation | Main Hall | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 2no 80mm dia pipes
466 | Compartmentation | Main Hall | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 30MM
467 | Compartmentation | Main Hall | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 60mm pipe 40mm cables 100mm dia trunking
473 | Compartmentation | South Block Library | Unsealed service penetrations passing through plasterboard compartment wall | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 2no 300x300mm patress with graphite mastic
481 | Compartmentation | Chemical Store | Unsealed service penetrations passing through plasterboard compartment ceiling | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 6no 40mm dia mastic cables
485 | Compartmentation | South Block Basement | Unsealed cable penetrations passing through compartment plasterboard wall | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 1x400x150mm 1x200x100mm
486 | Compartmentation | South Block Basement | Unsealed service penetrations passing through compartment brick wall | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification | 600x600mm
487 | Compartmentation | South Block Basement | Unsealed pipe penetrations passing through concrete floor slab | requires sealing with fire stopping materials installed in line with manufacturer installation specification | 200mm
488 | Compartmentation | English Store | Unsealed service penetrations passing through blockwork compartment wall | Seal using appropriate fire stopping materials such as fire batt and mastic installed in line with manufacturers installation specifications | 10no 40mm dia mastic
490 | Compartmentation | South block archive | Unsealed void in plasterboard ceiling | Seal using appropriate fire stopping materials such as fire batt in patress detail to underside of ceiling | 400x300mm batt mastic
492 | Compartmentation | Junior Block Crosscorridoor | Unsealed head of wall above crosscorridoor fire door | requires sealing with fire stopping materials installed in line with manufacturer installation specification to the underside of the roof | 1400x300mm
494 | Compartmentation | Junior Block Crosscorridoor | Unsealed cable penetrations in pvc trunken passing through compartment plasterboard wall | requires sealing with fire batt and intumescent mastic installed in line with manufacturer installation specification to both sides of compartment wall | 40mmx2