COMMUNITY HOUSING WATER HYGIENE RISK MITIGATION ACTIVITIES CONTRACT

Contract Scope

The scope of the contract is to carry-out the following water hygiene maintenance tasks, on behalf of Community Housing:

-Monthly hot & cold-water temperature checks

-Quarterly Showerhead clean and disinfection

-Six-monthly fail-safe service to Thermostatic Mixing Valves

-Six-monthly Legionella sampling

-Six-monthly Tvc/E.coli/Coliform sampling

-Annual Inspection of CWST/Integrated Water Heaters

-Annual tap descales

Monthly visits to be carried out on site to carry out above tasks, carried out by trained water hygiene technicians. Monthly contract review meetings between Community Housing and the successful Contractor take place.  Any issues may require a site visit with Community Housing and the Contractor.

- Programme of Works:

- Year 1 - 2023/24

- Year 2 - 2024/25

- Please see attached component service schedule.

- Delivery and Geographical Areas:

- Supported and General Needs Blocks across the Wye Forest Area (Kidderminster, Stourport-on-Seven and Bewdley).

- CONTRACT DURATION 2+2 Years

- ESTIMATED VALUE IS IN THE RANGE OF £180,000

Overview of Community Housing Portfolio

The portfolio of sites consists of properties offering community housing initiatives across the Wyre Forest District, consisting of 31 properties in total (see below table)

| Adams House, Woodfield Street, Kidderminster, DY11 6YA | Foley Grove, Kidderminster, DY11 7PT | Ruth Chamberlain Court, Paternoster Row, Kidderminster, DY11 6RU | Wribbenhall Community Centre, BEWDLEY, DY12 1EX |
| --- | --- | --- | --- |
| Arch Hill Court, Orchard Street, Kidderminster, DY10 2JA | Fred Bennett Community Centre, KIDDERMINSTER, DY10 1PX | 94 Shakespeare Drive, Offmore,, Kidderminster, DY10 3QY |  |
| Broomy Close, Lickhill, Stourport-On-Severn, DY13 8RX | Gamson Close, Hoobrook, Kidderminster, DY101LD, | 154 Sion Avenue, broadwaters, Kidderminster, DY10 2YL |  |
| Berrington Court 1, Felix Baxter Drive, Kidderminster, DY11 7FH | Hampton Mews, Felix Baxter Drive, Kidderminster, DY11 7FG | Sion Gardens, New Street, Stourport-On-Severn, DY13 8BH |  |
| Berrington Court 2, Felix Baxter Drive, Kidderminster, DY11 7FH | Hornbeam House, Hales Park, Bewdley, DY12 2JR | The Woodlands, Rifle Range, Kidderminster, DY11 7NN |  |
| 13 Truro Drive, Habberley,, Kidderminster, DY11 6DN | Lister Road Community Centre, KIDDERMINSTER, DY11 6NN | Walshes Community Centre |  |
| Carter Court, Sutton Farm, Kidderminster, DY11 6PT | Neville Court, Neville Avenue, Foley Park, Kidderminster, DY11 7AL | William Bullock Close, New Street, Stourport-On-Severn, DY13 8UG |  |
| Coniston House, Hurcott Road, Hurcott, Kidderminster, DY10 2PA | Oakleaf House, Finepoint Way, Kidderminster, DY117FE | Willow Court Community Room, KIDDERMINSTER, DY11 5AU |  |
| Derwent House, Hurcott Road, Hurcott, Kidderminster, DY10 2PA | Purcell House, Kidderminster Town, Kidderminster, DY10 2JA | Windermere House, Hurcott Road, Hurcott, Kidderminster, DY10 2PA |  |
| Drumart House, Austcliffe Road, Cookley, Kidderminster, DY10 3UP | 116 Queen Elizabeth Road, (adj to 114, Comberton, Kidderminster, DY10 3BG | 56 Worcester Road, 56 Worcester Road,Hoobrook,, Kidderminster,, DY10 1LB, |  |

Reporting

The successful contractor will need to provide all maintenance reports, sample results and significant findings with exceptions and record them electronically with a compatible system.

Reports should be made available within 24 hours of works being completed at site to allow Community Housing to react quickly to hazardous or costly situations.

Exception reports should show the “out of spec “results that require attention. These exceptions should be recorded as High, Medium or Low risk.  These actions must be recorded to enable Community Housing to evidence completion and demonstrate compliance.

Contract Period

The recognised contract period starts at 1st April each year. Monthly purchase order numbers will be issued by Community Housing to cover contract work.

All additional tasks not included within contract scope should be quoted separately. A separate Purchase Order number will be issued for completion of the tasks.

Contact Details Community Housing

| Natalie Baxter | Head of Building Safety and Compliance |  | natalie.baxter@communityhousing.co.uk |
| --- | --- | --- | --- |
| Karen Conde | Safety Compliance Manager (Fire, Asbestos, Water and Estates) |  | Karen.Conde@communityhousing.co.uk |
| Lauren Wheeler | Safety Compliance Officer |  | Lauren.wheeler@communityhousing.co.uk |

Service Level Agreement

| Action | Target |
| --- | --- |
| Booking of service visits | At least 48 hours before visit |
| Notification of TVC results | Within 6 days total from sample date: N.B Samples to be taken to the lab within 24 hrs. |
| Notification of Legionella results | Within 14 days of sample date: Presumptive counts to be notified and reported on 3 & 7 day readings. |
| Positive LP results | Contractor to notify Community Housing of any positive result within 24hrs via email or phone. Quotations, if required, to be sent with certificates. Where complex quotations are required, successful contractor will discuss with Community Housing once certificates are issued. |
| Request for quotations | Acknowledgement by successful contractor within 48 hrs. Complexity of situation will depend upon time taken to provide, as survey may be required. SLA of 7 days for works under £5K |
| Carrying out works following issued orders | Within 1 week for resamples. Complex quotations may require parts to be ordered. Successful contractor to provide approximate time frame for these works within 72 hours. |
| Closure of outstanding quotations | Successful Contractor must notify Community Housing of any quotations that have not been accepted during monthly review meetings. |
| Actions identified from Legionella Risk Assessments | Action to be completed within the timescales below: High Risk – within 21 days from date of order Medium Risk – within 2 months from date of order Low Risk – within 5 months from date of order |
| Invoicing | Valuations to be submitted no later than 25th of each month All Invoices to be accurately submitted following approval of the valuation on a monthly basis |
| Contract Review Meetings | Monthly via Microsoft Teams |