DIO SD TRG (KENYA)

BOOKLET 3 SPECIFICATION LUMP SUM FIRM PRICE CONTRACT FOR THE LIQUID PETROLEUM GAS works AT KIFARU CAMP AND LAIKIPIA AIR BASE EASE (LABE)

References:

A.	BS 7671 + A3:2015: Requirement for electrical installations. IET wiring regulations 17th Edition Amendment 3

B.	JSP 375 MOD Health and Safety Handbook.

C.	Water Supply (Water Fittings) Regulations 1999 (England and Wales).

D.	BS 8558:2011: Guide to design, installation, testing and maintenance of services supplying water for domestic use.

E.	BS EN 60529:1992+A2:2013: Degrees of protection provided by enclosures (IP Code).

F.	Approved code of practice (ACOP) L138 & L135.

G.	BS 8000-0:2014 –Workmanship on construction sites introduction and general principles.

H.	BS EN 60079-10-1:2015 - Electrical apparatus for explosive gas atmospheres. Classification of hazardous areas.

I.	The Pressure Equipment Regulations 1999.

J.	Health and Safety at Work (etc.) Act 1974.

K.	Building Regulations 2010 BS EN 12056-3 Gravity drainage systems inside buildings. Roof drainage, layout and calculation.

L. 	LPG Association Code of Practice (LPGA COP No.5).

M.	Provision and Use of Work Equipment Regulations 1998.

N.	Construction (Design & Management) Regulations 2015 (CDM2015).

O. 	BS 669:1997 ‘Flexible hoses, end fittings and sockets for gas burning appliances’.

Q.	BS 3212:1991 ‘Specification for flexible rubber tubing, rubber hose and rubber hose assemblies for use in LPG.

R.	BS EN 1763-1:2001 ‘Rubber and plastics tubing, hoses and assemblies for use with commercial propane, commercial butane and their mixtures in the vapour phase’

S.	BS EN ISO 7840:2004 ‘Small craft. Fire-resistant fuel hoses’

T.	BS EN 1452-2: Plastic piping for water supply..

U.	BS EN ISO 10239:2000 ‘Small craft. Liquefied petroleum gas (LPG) systems’

Introduction

- The following specification is for the Liquid Petroleum Gas (LPG) works in the following locations:

  - Building 10 main kitchen, Kifaru camp in Nairobi.  Replacement of emergency shut off valve.

  - Building No. 54 cook house, Laikipia Air Base East (LAB E) in Nanyuki.  Construction of LPG cylinder storage shelter adjacent to the building.

Key Project Details:

| Contract title: Site location: | 1609 Kifaru camp, Nairobi and LAB East, Nanyuki |
| --- | --- |
| Proposed start date: | Mar 17 |
| Proposed completion date: | Apr 17 |
| Retention: | 5% (reduced to 2.5% if completion achieved on planned date) |
| Defects liability period: | 12 Months – Note that an inspection must take place 3 – 4 weeks prior to the end of the defects liability period. The retention payment will not be paid until this, and any works arising from that inspection, have been completed. |
| Design life: | 25 years |

Scope of works

- The Specification for this project is Concept and the contractor is to provide detailed designs and detailed specifications for the Authority.

  - Replacement of emergency shut off valve, LPG hose and quick release hose couplings in Kifaru camp, Nairobi.  The existing LPG system in main kitchen is built to the current regulations with all the safety aspects necessary and it is regularly maintained by the qualified local contractors when required.  The system has a separate LPG cylinder storage located outside the building in a safe location.  The cylinder storage is adequately sized to store required number of LPG cylinders and consists of a LPG manifold which can connect up to 6 No. LPG cylinders as shown in the figure 1 below.  The system comprises of pressure regulating valve, isolation valves, non-return valves and emergency shut off valves etc.

Figure 1.  Manifold connecting 6 No. LPG cylinders in Kifaru camp, Nairobi

Scope of works

    - Due to normal wear and tear, the following components need replacing:

      - Emergency shut off valve.

      - 6 No. quick release LPG hose couplings.

      - 6 No. approx 2 m long each LPG hoses with gas regulator to connect LPG cylinders from manifold.

    - Design and installation of an additional manifold to connect additional LPG cylinders to make primary and secondary supply banks.

Requirements

    - Obtain Permit to Work (PTW) from the Authority.

    - Carry out necessary risk assessment and method statement for the work and submit to Authority for approval.

    - Isolation of electrical power supply to the LPG safety components will be carried out by Authority skilled person electrical.  Safety locks and warning signs to be fitted at the point of isolation.

    - Isolation of LPG supply to the main kitchen will be carried out by the authority skilled person petroleum. Safety locks and caution signs to be fitted at the point of isolation.

    - An emergency gas control valve shall be installed close to the point of service entry into the premises in an accessible location. The location and labelling of the valve shall be in accordance with Regulation 8 of the Gas Safety (Installation and Use) Regulations. The emergency shut off valve is to be electrically linked (hard wired) with the gas leak detection system.  In the event of gas leak is detected, the emergency shut off valve must be operated and remain close until manually reset.

    - Quick release coupling and LPG hose.  Currently the existing LPG hoses from the cylinders are connected to manifold without quick release coupling as shown in the figure 2 below.  Quick release couplings are to be fitted in manifold to attached LPG hoses from the cylinders in accordance with BS 3212 type 2.

Figure 2.  Existing LPG hose connected to manifold.

    - LPG hoses with gas regulator.  All existing worn off LPG hoses with regulator are to be replaced with new as per BS 669 part 2.  New hoses are to be adequately sized in length to connect with the cylinders.  Any joints used in the hoses are to be leak proof.  Flexible hoses should have factory fitted swaged or crimped connections (not hose clips) and be manufactured to BS 3212 type 2.

    - Labelling and signage.  After the completion of the project, the contractor must label all components (i.e. valve numbers) and mount necessary safety warning signs in and outside of the LPG storage room as required.  The entire LPG pipelines and manifold are to be painted with yellow paint as per JSP 375 Part 2 Vol 3 Ch 5.

    - Disposing of unwanted materials.  Any unwanted and worn off components / materials removed are to be disposed of appropriately away from the Kifaru camp.  The contractor will be liable for inappropriately disposing of waste material in contravention of NEMA.

    - Risks of fire and explosion.  Due to the nature of work carried out, there is risk of fire and explosion.  Contractor is to carry out detailed generic, specific and dynamic risk assessments and produce appropriate method statement and submit to authority for approval before commencing task.

Inspection and testing

    - Using correct gas testing kit, ensure there are no LPG leakages in the task area.

    - Carry out testing and commissioning of newly installed system.  The authority must be invited to witness the testing and commissioning of the installation.

    - After the completion of the project, the contractor is to hand over the Health and Safety folder which should include; health and safety file, test certificates, as built drawings, operating manuals etc. to the authority.

    - The installation, adjustment, commissioning, or adjustment of gas installation pipework, appliances or associated fittings is to be carried out in accordance to the Gas Safety (Installation and Use) Regulations 1998 (GSIUR).

  - Construction of LPG cylinder storage shelter in Laikipia Air Base East (LAB E), Nanyuki.  The cook house in LAB East often uses 45 kg LPG cylinders for cooking however; the cook house lacks the storage facility to store LPG cylinders.  There is a requirement to build LPG cylinder storage to accommodate maximum of 22 Nos. 45 kg standard size domestic use LPG cylinders adjacent to the cook house with enough space for moving and transporting cylinders with sufficient natural ventilation.  The average dimensions of 45 kg LPG cylinder are 1250 mm high and 375 mm diameter.  With the LPG storage area, there is also a requirement to store used or empty LPG cylinders for maximum of 20 Nos. cylinders.  Used or empty LPG cylinders storage area must have adequate space for moving cylinders, transporting and with enough space to have a natural air circulation for ventilation.

Scope of works

    - Carry out necessary risk assessment and method statement prior commencing task.

    - Prepare ground works to have at least 6m x 4m x 0.15m thick (Minimum thickness) of reinforce concrete foundation pad to accommodate maximum of 22 No. 45 kg full LPG cylinders and 20 No. 45 kg used or empty LPG cylinders within the same storage separated by approximately 1.5 m high concrete built partition wall.

    - Build firm LPG cylinders storage shelter with minimum of 7 m x 5 m, there must be a minimum of 200 mm internal space clearance to accommodate full and emptied cylinders.  The storage space must have a minimum of 2000 mm internal space clearance for moving cylinders, transporting LPG cylinders using trolley and good clearance above and around the storage shelter.  The main entrance door for the storage shelter is to have a double door facility capable of opening outside; the minimum size of the door opening must be 1000 mm with a concrete ramp at front of the door for ease of trolley movement.

    - Provide CGI roof to protect cylinders from the external elements.

    - Divide newly built LPG storage shelter in the middle with approx. 1.5 m high concrete partition wall to store full and empty LPG cylinders.

    - Installation of supplementary bonding to the structure and a lightening protection system (LPS) to BS 6651:1999.

    - Install ATEX rated electric light/s and switch to light up adequately nearby distribution board.

    - Make good and put suitable signs and label the shelter.

    - Site clearance and ground works.  After the completion of the project, the entire site is to be cleared and all unwanted materials from the site are to be disposed of away from LAB (E), this is to be determined by the successful contractor.

    - Storm water drainage system.  The newly built shelter is to be fitted with gutters and down pipes if required to appropriately channel water away from the shelter.

Requirements

    - The store shall not be located above, or in the immediate vicinity of drains.

    - The store shall not be located within the designated route of escape from the building.

    - The store shall not interfere with any fire separation structure within a building.

    - The store shall be located at least 2 metres away from the fixed source of naked flame.

    - The store shall be constructed of concrete, or any material having at least two hour fire resistance (BS 476) and sufficient mechanical strength to protect stored cartridges.

    - Door(s) shall be provided to the store being a material having at least one hour fire resistance (BS 476). The door(s) shall normally be locked.

    - The store shall be vented (wherever possible directly to open air) by natural and/or mechanical ventilation, this shall be provided at low and high level. In the case of mechanical ventilation, the extract opening shall be at low level and the fresh air intake opening shall be at high level.

    - A permanent notice shall be prominently displayed on the door(s) of the store in Kiswahili and English language:

      - "LPG CYLINDER STORE";

      - "NO SMOKING OR NAKED FLAMES".

Inspection and testing

    - Test and commission all electrical installations as per BS 7671+A3:2015.

    - Hand over the project.

General points

- The following general points have been identified as potential issues:

  - Communication will be key in planning and conducting concrete works, excavation works, design works, final connection, new connections to existing systems, electrical installation and during commissioning.

  - All personnel employed to work on the above tasks should be suitably qualified and must have their CV submitted to the authority.  They may also be interviewed by the authority to confirm their competency.

  - Before any work is performed, pertinent risk assessments and method statements should be issued to the authority.  The authority will then issue the appropriate permits to work if required. The contractor must request Statement of known hazards from the authority prior starting and excavation on site.

  - All work to be carried out in accordance with the relevant Safety Rules and Procedures.

  - All detailed design drawings, cable sizing calculations, pipes sizing calculations, drainage sizing, concrete mixing ratios, materials data safety sheets and samples for materials are to be submitted to the authority for approval beforehand.

  - All removed spare or unused parts are to be returned to the authority for disposal.

  - Authority will issue the necessary paperwork’s for transportation of goods in the camp i.e. gate pass.

  - All working at height works should be carried-out as per JSP375 Vol3 CH3 safe system works.

  - Any Scaffolding ladders to be used in the tasks are to be serviceable and where required presented to the Authority for inspection and permission to use.

  - Any electrical works (final connection of the cables to the existing system) work will be carried out as per JSP375 Vol 3 Ch 3 (Permit to work).

  - Under no circumstances trench digging works will be carried-out without a statement of known hazards.

Restrictions / Constraints

- Access to the site.   This is to be agreed in detail with the PM prior to start on site.  Passes may be required and the contractor should submit the details and ID of any technicians that will be working on the contract within the tender return.

- Notice.  The contractor is to provide notice to the authority in writing (or through email), minimum of 3 working days prior to the work on site.  The notice must include the date and expected time of arrival, name and ID No of the workforce, and contact telephone no for both the contract manager and the workforce.

- Working hours.   The contractor may choose to work in his/her suitable hours; however assistance from the authority will only be available 0800-1600 hrs Mon – Fri.  For any assistance from the authority, the contractor must submit request with a minimum of 24hrs notice.

- Permits to Work.  Permits to work applicable for this task are as follows:

  - Statement of Known Services.

  - Electrical work.

  - Working at Height.

  - Confined Spaces.

Annexes:

A.	Generic Points - Pre-contract

B.	Generic Points - Pre-construction.

C.	Generic Points - During construction.

D.	Generic Points - Post construction.

Generic Points - Pre-Contract

Designers

- This project is a Design and Build contract, meaning the contractor must fulfil the role of both the designer, and the Principle contractor.  The design work must be carried out by a qualified and competent person.  The contractor shall ensure all designs are in accordance with, and includes the applicable requirements contained within references and all other design documents specified within this Performance Specification.  If the contractor is not competent to carry out some aspects of the design work, a qualified person or consultancy firm should be sub-contracted to carry out that portion of the work.  The Contractor is to inform the PM of all design consultants/sub-contractors who will be employed in this project and the areas of their responsibility.

- Where design work is required to be carried out by a professionally qualified person, details of their qualifications and experience, registration with the Engineers Board of Kenya and copy of their professional liability insurance needs to be submitted to the authority.

- Pre-Construction Information Pack (PCIP).  Prior to design the contractor will be issued a PCIP with key design and H&S data.  The PCIP will contain the following information:

  - Description of the project.

  - Clients considerations and management requirements such as; Security, PPE, hoarding, signage, gate passes, permits to work etc.

  - Environmental restrictions and existing site hazards such as; services, vehicle routes, ground conditions, existing structures etc.

  - Significant design and Construction hazards.

  - Existing health and safety file if applicable.

Contractor’s initial design

- The contractor is to ensure that their design meets the parameters outlined within this Specification.

- Site visit.  The Contractor shall acquaint himself completely with the exact conditions relating to access and site environment, along with the layout, conditions and positions of the existing services, the full extent of the works required, and the supply and conditions affecting labour, carriage, carting, unloading, storage, tools, scaffolding etc. as well as any security and access constraints.

- Existing ground levels.  The Contractor shall confirm or identify all existing site levels required prior to any construction works.

- Ground water level.  The ground water level has not been established but it is not expected to impact on any of the works.  It is the Contractors responsibility to take into account the ground water levels when submitting technical and commercial proposals.

- Existing record drawings.  The Contractor will upon request, be supplied with copies of all available and relevant as built drawings.  The Contractor during tender stages shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

- The responsibility remains with the Contractor to ensure that all design and construction works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the works, geography, climate, and environment.  Where there are conflicts between the design drawings and Detailed Specification the Detailed Specification will take precedence in all cases.  Any queries should always be addressed to the Authority in the first instance.

Use of design codes and specifications

- In addition to the Conditions of Contract, all designs must conform to the most current editions of British Standards (BS) or Euro Norms (EN).  Other Design Codes may, on occasion, be used provided that they meet the minimum requirements and the Contractor shall submit proof of equivalency to the Authority for approval of use.  The Authority can be approached for clarification of the relevant BS if required.  On no account is the contractor to use any design information other than that stated or approved by the Authority.

- All Contractors will be required to certify their designs for conformity to the specification and to the relevant BS/EN.  Only appropriately qualified and experienced engineers are to certify the designs.

  - Design conformity.  The design engineer is to produce a letter to state that the design conforms with all applicable legislation, most current editions of BS or EN, and best practice.  The letter is to have the company header (of the design agency if sub-contracted) and to be signed by the lead designer with his name, contact details and qualifications detailed in the signature block.

  - Construction inspections.  Prior to the start of construction, the contractor, designer and authority shall agree key stages at which the works are to be inspected by the designer for compliance with the design.

  - Build conformity.  At the end of the project, the lead designer is to confirm in writing that the works have been built correctly, in accordance with his design.

- Design life.  The design life of all new works to first major overhaul, repair or replacement shall be as stated in para 1 of this main document.  The Contractor shall supply and install all components, elements and systems/structures to satisfy this requirement and provide documentary evidence.

- Initial design information.  As part of the bidding process a concept design must be submitted to the Authority.  The level of detail at this stage must be sufficient to clearly demonstrate what the contractor is proposing to deliver, and to accurately price the job.  No allowance for additional funding will be made after the contract is awarded.  The minimum design information to be provided in the tender bid shall include the followings:

  - General layout plans for the site and the structures.

  - Services layouts and schematics.

  - Details of all materials and components to be incorporated.

  - Project Programme, to be regularly updated or upon request by the Authority and provided electronically on Microsoft Project or equivalent.

Generic Points - Pre Construction

Detailed design and planning

- Additional design information.   Particular reference is made to Clause 11 of the Conditions of Contract.  The Contractor is to submit any additional design information to the Authority prior to commencement of the construction phase.  The PM will examine design documentation and shall be entitled to reject a design as unsatisfactory where it is not in accordance with the specification, statutory regulations or if it would be unfit for purpose.

- A copy of all construction drawings are to be provided by the Contractor to the PM prior to commencing Works.  Amended or updated drawings are to be provided as necessary.  The minimum design information to be provided by the Contractor shall include the following:

  - Any additional design calculations for the works.

  - Any additional general layout plans for the site and the structures.

  - Any additional detailed structural design, calculations and drawings.

  - Any additional foundation plans shall (as a minimum) indicate: all footing locations and dimensions, screeds and / or ground slabs or plinths, as applicable.

  - Any additional services layouts and calculations.

  - Any additional detailed Electrical, Mechanical drawings and calculations.

  - Manufacturer product details including safety data sheets.

  - Designers risk register.

  - Project Programme to be regularly updated or upon request by the Authority and provided electronically on Microsoft Project or equivalent in a regularly basis or on request.

Design responsibilities (under CDM)

- The designer has the following responsibilities under CDM Regs:

  - Eliminate hazards and risks during design.  Designers are to analyse the risks posed during the construction, daily use, maintenance and ultimate demolition of the facility.  Once identified, these risks should, where practicable, be designed out.

  - Provide information on remaining risks.  Remaining risks after the design process are to be compiled onto a designers risk register and submitted with the final design.

Provision of information

- Unless otherwise specified the following is to be provided:

  - Three copies of all information, including valid certification, in respect to work, goods and materials proposed by the Contractor, shall be supplied to the Authority.  Where the original document is written in a language other than English, it shall be accompanied by an English translation.

  - Information and certificates shall be supplied at least two days prior to the use of the work, goods or materials in the Works.

  - Three copies of detailed working and fabrication drawings and calculations shall be submitted to the Authority for reference purposes.  Such submittal shall in no way relieve the Contractor of his responsibilities for the work under the contract.

- The Authority reserves the right to request copies of all calculations and drawings for analysis prior to the commencement of any construction on site.  The contractor will provide copies of all calculations and ‘As Built Drawings’ for the Health and Safety File.

- The signed and approved drawings shall be used as the construction drawings on site for all work purposes and to satisfy the requirements as specified by the Construction, (Design and Management) Regulations 2015 (CDM 2015) & appropriate ACOP.

Construction phase plan

- Under the requirements of CDM, the contractor is to prepare a construction phase plan detailing how they will safely conduct the works.  Risk assessments are to be included for all elements of work and method statements are required for any works that are out of the ordinary or high risk.  The Construction Phase Plan must cover the following area’s (where applicable):

  - Safety risks:

    - Protecting the public.  The public is any persons not involved in the works.  Particular attention should be paid to area’s where children are likely to have access to the site outside of working hours.

    - Traffic routes.  Traffic routes for delivery of stores and equipment should be clearly highlighted and controlled.  Movement of plant and machinery on site should be organised in a way that minimises risk to the workforce and any visitors to site.  Care must also be taken to minimise risk from existing traffic routes.

    - Existing buried and overhead services.  Some of these may be identified in the permit to dig process, however care must be taken to identify and avoid any damages on existing services.

    - Adjacent land use.  The use of adjacent land and properties will affect the level of protection for things such as noise and dust suppression etc.

    - Stability of nearby structures.  Care must be taken that works do not affect the stability of nearby structures.

    - Demolition works.  Demolition work is a particularly dangerous task and careful planning must be conducted.  Method statements for all aspects of demolition will be required by the authority.

    - Work equipment.  Work equipment must be inspected and in a suitable condition not to cause a hazard on site.

    - Electrical safety.  Electrical works will be conducted in accordance with the JSP and CDM recommendations.

    - Preventing falls.   Falling from height is one of the biggest killers in the construction industry.  Even when not working under a permit, it is expected that the correct equipment and management methods are utilised to prevent falls.

    - Working with or near fragile materials.  Fragile materials should be identified prior to work commencing and appropriate action must be taken.

    - Control of lifting operations.  Lifting operations are to be carefully planned and controlled on site.

    - Excavations / confined spaces.  All excavations inside buildings where work is to be conducted are to have the appropriate level of shoring / protection.  Where an area is deemed a confined space, a permit may need to be issued to control the works.  If permit is not issued, the contractor is to have a suitable system in place with appropriate paperwork i.e. risk assessment and method statements associated to the work being carried out.

    - Working on or near water.  If working on or near water the contractor is to plan the works to minimise the risk drowning.

  - Health risks:

    - Temperature / weather protection.  Protection from the elements for the workforce.

    - Substance misuse.  The misuse of drugs or alcohol by the workforce.

    - Manual handling.  Correct lifting techniques, lifting equipment etc.

    - Dust.  Dust suppression and removal.

    - Noise.  Reduction and suppression of noise.  Management of timings for noisy activities etc.

    - COSHH.  The correct storage and use of hazardous substances.  Appropriate protective equipment must be worn when handling COSHH materials.  Safety data sheets must be available on site at all time.

    - Asbestos.  Identification and appropriate management of Asbestos.

  - Provision of:

    - Welfare facilities.  Water, food, shade, toilet facilities etc.

    - First aid.  There should be at least one qualified first aider with appropriate medical equipment on site at all times.

    - Emergency procedures.  Procedures for response to incidents such as Fire, major and minor injuries, security incident etc.

    - Reporting of accidents, incidents or near misses.  Procedure for reporting and follow-on actions to prevent re-occurrence.

    - Waste management.  Management, storage and disposal of waste and arising from the site.

    - Fire prevention, detection and firefighting.  Methods to prevent the start and spread of fire, and to identify any fire that does start. There must also be appropriate firefighting equipment available and access to the site for firefighting services.

Pre-Start meeting.

- Prior to the commencement of any works, a Pre-Start meeting is to be held with the contractor, lead designer and chaired by a representative from the authority.  The following topics are to be discussed as a minimum:

  - Mobilisation plan

  - Site setup

  - Health and safety

  - Required permits

  - Access and security

  - Programme

Generic Points - During Construction

Facilities/temporary works/services

- Locations.  The Contractor is to agree with the PM of the intended siting of all spoil heaps, temporary works and services in advance.  The Authority shall verify with the Contractor which site features are to be removed and protected during construction works.

- Survey and setting out.  The Contractor will be responsible for all setting out and levelling during construction.  The Contractor shall keep updated schedules and drawings of all bench marks used in setting out of the site; these must be made available to the Authority when required.  A minimum of 2 survey control stations are to be constructed, one visible from the site at a distance of 50 m and the other 200 m away from the first but in line of site.

- Record drawings.  The Contractor shall record details of all grid lines, setting out stations, bench-marks and profiles on the site setting out drawing.  Retain on site throughout the contract and hand to PM on Completion.

- Signage.  The Contractor shall supply and erect all applicable and appropriate signage to the site.  This shall include as a minimum all H&S signage, directions and location of site office and emergency contact details of the Contractor’s representative on site.  Temporary warning signs and careful demarcation of works areas must be undertaken with care to ensure compliance with any and all requirements.

- Lighting and power.  The Contractor shall provide all lighting and power for his works.  No facility will exist on site from the general base infrastructure.

- Communications.  The Contractor shall provide his workforce with adequate means of communications throughout the duration of the Contract period in order to carry out the work specified.

- Temporary services.  The Contractor shall provide temporary service connections to both mechanical and electrical systems.  All temporary service connections are to be in accordance with current UK regulations.

- Use of the site.  The Site shall not be used for any purpose other than undertaking the specified works.  The Contractor may erect the site office and storage compound in a location agreed with the Authority.  No storage of materials, parking of vehicles, temporary accommodation or any other use of areas beyond the boundaries shall be permitted.  Under no circumstances shall it be permissible for the Contractor to cause an obstruction to normal pedestrian or vehicular movements within the vicinity of the site.

- Restrictions to the works.  The Works are to be undertaken without interfering with everyday running of the Authority’s operations within the area.  The demarcation of the Site boundary is to be obvious and clearly marked to restrict access to the Site whilst the Works are being undertaken.

Project management

- The authority.  The Project Support Officer (PSO) has overall authority on this project.  For the purpose of this specification, the PM is the only person from within the authority acting on behalf of the PSO, or Superintending Officer (SO) in most cases.

- The Contractor shall not commence any work in accordance with any Design Document until the PM has agreed the relevant Design Document.

- Programme of works.   Prior to the commencement of the works, the Contractor shall liaise with the Authority, in order to produce a detailed programme of works.  This programme shall be agreed and approved and shall form the baseline programme for the project.  Any deviations from the agreed programme shall be communicated to the Authority, with programme updates being produced if required and approved by the Supervising Officer.  The programme must be daily resolution and show when stores equipment and plant deliveries will occur.

- Programme status.   The Contractor shall also show on this programme the state of construction of the various elements of the works so as to illustrate the latest dates by which instructions requiring changes can be accommodated in each part of the Works without effecting the completion thereof.  Thereafter, the Contractor shall amend and revise the programme as required by the Conditions of Contract and as required by the PM or his representative.  The submission of a programme will not relieve the Contractor of his responsibility to apply in writing for instructions, drawings etc. in accordance with the Conditions of Contract.

- Commencement of work.  The Contractor is to inform the PM of any delays before the proposed date for commencement of work on site.

- Buried services.   Prior to carrying out any excavation work, the Contractor must:

  - Obtain a Permit to Dig (Statement of Known Services) and all drawings relating to existing services that may interfere with the proposed works.  A copy of the Permit to Dig must be given to the Authority prior to any works commencing.

  - Identify all local services and take adequate precautions to protect such services from damage for the duration of the works.

  - Inform the Authority immediately if any unknown services are discovered that will impact on the works.

- Supervision.  The Contractor shall accept responsibility for delivery, co-ordination, supervision and administration of the Works, including all subcontracts.  They shall arrange and monitor a programme with each subcontractor, supplier, local Employer and any statutory undertaker, and obtain and supply information as necessary for co-ordination of the work.

- Site diary.  The Contractor shall keep an up to date daily site diary.  This document is to be used to record all decisions made on site both verbally and written.  The document is also to be used to record visits to site and note anything, which has a direct effect on the project in terms of cost and extensions to time, or any other occurrence that affects the project programme.  This document will be used as the audit trail in light of any disputes, concerning the project.

- Contractor’s site meetings.  The Contractor is to hold meetings with appropriate subcontractors and suppliers shortly before site meetings with the Authority to facilitate accurate reporting of progress.

- Site meetings.  The PM, or his representative will hold regular site meetings to review progress and other matters arising from the administration of the Contract.  It will be the Contractors responsibility to ensure the availability of accommodation and attend all such meetings.

- Liaison with the authority.  The Contractor shall designate a site manager from within his organisation who will be responsible for liaising with the PM, PSO or his representative (SO) on a day to day basis and as the need arises.  At all times the Contractor shall ensure that the Site Manager presents on site that has the capability of reading, writing, speaking and receiving instructions in the English Language, including being able to understand and interpret technical drawings and specifications.  The Site Manager must be able to explain the work operations to person performing the work in a language that those performing the work are capable of understanding.  The PM shall have the right to determine, whether the proposed representative has sufficient technical and linguistic capabilities.

- Approvals.  Where products or work are specified to be approved or the PM instructs or requires that they are to be approved, the same must be supplied and executed to comply with all requirements.

- Access.  The Contractor shall provide at all reasonable times, access to the Works.  The Contractor shall supply the PM or his representative with copies of any documentation and drawings, which may reasonably be required for the purposes of monitoring the work performed under this or any sub-contract.

- Regulations.  It is the Contractor’s responsibility to be fully conversant with all local/MOD regulations and requirements in respect of fire, safety, security and occupational health, etc.  These are to be fully complied with throughout the contract period.

- Site instructions.  Where there is a change in design or specification, which does not have a cost or time implication a Site Instruction shall be issued by the SO to authorise the proposed change at nil cost to the Authority.  The site instruction shall also be used to authorise a change in a specified material/item/equipment as long as the replacement meets the standards required by the original specification and is authorised by the SO.

- Variation order.  Where there is a change in design or specification, which does have a cost or time implication a Variation Order shall be raised by the Supervising Officer to describe the proposed change, this may have a cost implication to the Authority.  The Works Contract Officer will issue the Variation Order to the Contractor for pricing; the Contractor will price the variation and return it to the Works Contract Officer.  All Variation Orders must be authorised by the Project Manager, Financial Officer and issued via the Works Contract Officer prior to the commencement of any works on site.

- Rejection of work.  The Authority reserves the right to reject or condemn any area of the works that he considers to be below an acceptable standard and the Contractor shall replace or repair the said works within 7 days of being notified in writing of the rejection by means of a Non Conformance Report.

- Extension of time.  When it is necessary to report a cause of a delay or likely delay in the progress of the Works this shall be given in the form of a written notice that must also be given of all other causes, which apply concurrently.  The notice shall state the following details.

  - Relevant particulars of the expected effects if appropriate related to the concurrent causes.

  - An estimate of the extent, if any, of the expected delay in the completion of the works beyond the Date of Completion.

  - Any other relevant information required by the PM.

Health and Safety

- Health and Safety (H&S).  All works shall be carried out in accordance with the Health & Safety at Work Act 1974 (HASWA).

- JSP 375.  The contractor shall comply with the Client’s permit to work system and the JSP 375, Volume 3, (details of which are obtainable from the Authority SO), including the provision of method statements, risk assessments, switching/isolating safety programmes, permit to dig, etc.

Permits to work

- Permit to dig.  If any excavation or breaking of ground is to be carried out, the contractor must request a permit to dig at the Pre-Start meeting.  Should any excavation be conducted without a permit, the contractor may be removed from site.

- Hot works permit.  The contractor is to establish at the Pre-Start meeting if hot work permits will be required for his location of work.

- AP’s.  The following table shows details of Authorise Person (AP) in their respective discipline.

| Discipline | CAP | Contact No |
| --- | --- | --- |
| Electrical | Mr Ezekiel | 0719197643 |
| Mechanical | SSgt Ambohang | 0702659971 |
| Petroleum | Mr Ezekiel/SSgt Ambohang | 0719197643 / 0702659971 |
| Confined Spaces | Mr Mbilo | 0720015852 |
| Working at Height | Mr Mbilo | 0720015852 |

- Skilled Persons & Persons in Charge (PIC).  Any works required to be completed under a JSP 375 permit must have a dedicated PIC and the work carried out by registered skilled persons.  At the Pre-Start meeting the contractor must establish if any of his works require a permit, and if so arrange for currently registered personnel to conduct the works, or registration of the contractors personnel.

- CDM Regs.  The Contractor shall submit a pre-construction H&S file to the Authority for approval, including all risk assessments, method statements, hazardous material procedures etc to comply fully with Construction, Design Management Regulations 2015 (CDM 2015) & appropriate ACOP.

Quality of work

- Quality standards/control.  The contractor will provide evidence to the PM of his quality standards and controls, and will produce a plan detailing Quality Control (QC) activities in order for the PM to plan for witnessing of critical activities.

  - General quality of products.  All products shall conform to the following subparagraphs:

    - Products to be new unless otherwise specified by the Authority.

    - For products specified to a BS or EN obtain certificates of compliance from manufacturers when requested.

    - Where a choice of manufacturer or source is allowed for any particular product, the whole quantity required must be of the same type, manufacture and/or source unless otherwise approved.  Produce written evidence of sources of supply when requested by PM.

    - Ensure that the whole quantity of each product required to complete the work is of consistent kind, size, quality and overall appearance.

    - Where consistency of appearance is desirable ensure consistency of supply from the same source.  Do not use different colour batches where they can be seen together.

    - If products are prone to deterioration or have a limited shelf life, order in suitable quantities to a programme and use in appropriate sequence.  Do not use if there are any signs of deterioration, setting or other unsatisfactory condition.

  - Proprietary products.   All products shall conform to the followings:

    - Handle, store, prepare and use or fix each product in accordance with its manufacturer’s current printed or written recommendations/instructions.  Inform PM if these recommendations/instructions conflict with any other specified requirement. Submit copies to PM when requested.

    - The tender will be deemed to be based on the products specified and recommendations on their use given in the manufacturer’s literature current at the date of tender.

  - Obtain confirmation from manufacturers that the products specified and recommendations on their use have not been changed since that time.  Where such change has occurred inform PM and do not place orders for or use the affected products without further instructions.

  - Checking compliance of products.  The Contractor shall check all delivery tickets, labels, identification marks and where appropriate the products themselves to ensure that all products comply with the project documents. In particular, check that the products comply with the following sub-paragraphs.

    - The sources, types, qualities, finishes and colours are correct, and match any approved samples.

    - All accessories and fixings that should be supplied with the products have been supplied.

    - Sizes are correct.  Where tolerances are critical, measure a sufficient quantity to ensure compliance.

    - The delivered quantities are correct, to ensure that shortages do not cause delays in the work.

    - The products are clean, undamaged and otherwise in good condition.

    - Any products with a limited shelf life are not out of date.

  - Protection of products.  All products shall be protected to ensure that they remain in the condition they are required to be in.  In particular the contractor is to ensure that products are to be prevented from overstressing, kept clean, protected from the elements and kept in original wrappings until required for the project.

- Prohibited products.  The Contractor shall not employ on or incorporate in the Works any of the following products and shall impose a like obligation upon all Sub-Contractors.

  - Asbestos materials as described in the Asbestos Prohibitions Regulations 1985 and the Asbestos Products (Safety) Regulations 1985.

  - Lead or any products containing lead for use in connection with drinking water.

  - Materials that are generally composed of mineral fibres either manmade or naturally occurring which have a diameter of 3 microns or less and a length of 200 microns or less or which contain any fibres not scaled or otherwise stabilised to ensure that fibre migration is prevented.

  - Other products or substances generally known to be deleterious to health and safety at the time of use or to the durability of the property in the particular circumstances in which they are being used.

- Hazardous, aggressive or unstable materials.  The Contractor is not to import or use fill materials which would either in themselves or in combination with other material or ground water, give rise to health hazards, damage buildings or structures.  The construction materials should not include any finishes that may lead to shedding of particles.

- Defects in existing construction/services.  This shall be reported to the PM without delay. Obtain instructions before proceeding with work which may be covered up or otherwise hinder access to the defective construction, or be rendered abortive by the carrying out of remedial work.  This is particular relevant in relation to the expansion of the existing service runs.

- Proposals for rectification of defective work/products.  As soon as possible after any part(s) of the work or any products are known to be not in accordance with the Contract, or appear that they may not be in accordance, the Contractor is to submit proposals to the PM for opening up, inspection, testing, making good, or removal and re-execution. Such proposals may be unacceptable to the PM and he may issue contrary instructions.

- Quality control.  The Contractor is to establish and maintain procedures to ensure that the works, including the work of all Subcontractors, comply with specified requirements.  This is to include all testing of materials that are to be incorporated into the project (e.g. concrete).  The Contractor is to maintain full records, keep copies on site for inspection by the PM, and submit copies of particular parts of the records on request.  The records must include the following:

  - Identification of the element, item, batch or lot including location in the works.

  - The nature and dates of inspections by the Contractor or PM, tests and approvals.

  - The nature and extent of any non-conforming work found.

  - Details of any corrective action.

- Workmanship.  Notwithstanding any clauses in the Conditions of Contract or elsewhere in the Specifications or Scope of Works, the Contractor shall be responsible for ensuring that all work-related activities shall be carried out in a neat and workmanlike manner, in accordance with accepted good practice.  The Contractor shall pay full attention to quality control and adherence to the specifications.  Particular care shall be taken in respect to Health and Safety matters, which shall include the provision of any relevant temporary warning signs and safety barriers.  All working areas are to be kept clean and tidy on a daily basis.  All redundant materials must be cleared to the requirements laid down in the Authorities Environmental Regulations.

- Materials testing.  It is the Contractor’s responsibility to carry out all materials testing and present all test results to the Authority on request and within the H&S file.  The Authority will carry out concurrence quality control material tests at regular intervals.

- Notification.  The Authority requires to be informed in writing at least 10 days in advance of any tests and commissioning being carried out.  Access must be available to the Authority to carry out testing as deemed necessary by the Authority.

Generic Points - Post Construction

Completion / handover

- Commissioning period.  Within the tender submission the Contractor shall submit a Works Commissioning Plan, setting out his commissioning proposals including the preparation of handover documentation.

- Notice of completion.  The Contractor is to provide the PM at least five days notice of the anticipated dates of Practical Completion of the whole or parts of the Works.

- Mechanical and electrical services.  Mechanical and Electrical Services must have final tests and commissioning carried out by the Contractor so that they are in full working order at Practical Completion.  This includes buried but not connected cables and pipelines.

- Timing of tests and inspections.  The Contractor is to agree dates and times of tests and inspections with PM four days in advance, to enable the PM and other affected parties to be present.  On the previous working day to each such test or inspection the Contractor is to confirm to the PM that the work or sample in question will be ready or, if not ready, agree a new date and time.

- Test certificates.  The Contractor is to submit a copy of each certificate to PM as soon as practicable and keep copies of all certificates on site.  Copies should be included in the Health and Safety File on handover of the works.

- Work at or after completion.  The Contractor is required to undertake the following works prior to handover.

  - Make good all damage consequent upon the work.

  - Remove all temporary markings, coverings and protective wrappings unless otherwise instructed.

  - Clean the works thoroughly inside and out including all accessible ducts and voids; remove all splashes, deposits, efflorescence, rubbish and surplus materials consequent upon the execution of the work.

  - Cleaning materials and methods to be as recommended by manufacturers of products being cleaned, and to be such that there is no damage or disfigurement to other materials.

- Security at completion.  The Contractor is to leave the Works secure with all accesses locked.  Account for and adequately label all keys and hand over to PM with itemised schedule, retaining duplicate schedule signed by PM as a receipt.

- Making good defects.  The Contractor is to make arrangements with the PM and give reasonable notice of the precise dates for access to the various parts of the Works for purposes of making good defects.  The PM is to be informed by the Contractor when remedial works to the various parts of the Works are completed and ready for approval.

- Inspection, testing and commissioning.  The installations shall be tested and inspected in accordance with but not limited to the current CIBSE Codes, BS7671:2008+A3:2015 Requirements for Electrical Installations, IEE Wiring Regulations 17th Edition, 3rd amendment where appropriate, etc.  Advance notice of tests shall be given (minimum of 7 days prior to notification).

- Test and inspection certificates are to be approved by the Authority, preferred document templates will be provided by the Authority on request.  Test certificates shall serve as a record that the item referred to has been shown under test to meet the requirements of the specifications and of British Standards as applicable and shall be dated, numbered and clearly referenced to the item tested by means of serial, chassis or other manufactures reference number permanently marked in a conspicuous position.

- The calibration certificates for the testing of the equipment are to be available on request to be shown to the Authority for scrutiny.  The Contractor shall ensure all calibrations are in date.  The Authority reserves the right to have an independent electrician available during the test and inspection phase.

- Any defects of workmanship, materials or non-compliance with the specifications or other irregularities which become apparent during the tests shall be rectified by the Contractor, at his own expense, until the whole work is free from defects and in full working order to the complete satisfaction of the Supervising Officer.

- All materials used for construction of permanent works shall have suppliers’ specifications and/or testing certificates available.  Where materials are used as part of a whole or in conjunction with other materials, and in any case where site testing is required by best practice, verification of quality and specifications should be allowed for the parts / items / products (suppliers’ specification) as well as the whole (site testing).

- Defects liability period.  A defects liability period shall apply for the works as detailed above.  The Contractor will be responsible for making good at his own expense any defects in the works arising within that period.  The contractor is to ensure that a defects inspection is conducted 2-4 weeks prior to the end of the liability period in order to release the contract retention.

- Operations and maintenance documentation.  Upon completion of the works the Contractor shall forward all manufacturers’ details relating to equipment/materials used to the Authority for inclusion into the O&M Manual/H&S File.  Refer also to Construction, (Design and Management) Regulations 2015 (CDM 2015) & appropriate ACOP, this documentation less ‘As Built Drawings’ is to be made available at the Pre Board of Officers not less than 10 days before the due project handover date.  A full list of snagging items shall be produced and presented to the Authority with a rectification programme at this very same board.

Health and safety file

- Upon project completion the H&S file shall be presented to the Authority before the Board of Officers is convened and in compliance with (CDM 2015) & appropriate ACOP.

- Presentation of health and safety file.  The Contractor is to provide the PM with three copies of the H&S File.  The Manual is to be contained in a series of A4 size, plastic covered, loose leaf, four ring binders with hard covers, each indexed, divided and appropriately cover titled.  Selected drawings needed to illustrate or locate items mentioned in the Manual, where larger than A4, are to be folded and accommodated in the binders so that they may be unfolded without being detached from the rings.  The main set(s) of as-built drawings will form Annex(es) to the Manual.

- The health and safety file.  The Contractor shall be required to complete the Project Health and Safety File on completion of the works, three copies of which will be provided to the Authority at handover. Advice can be sought from the Authority if required.  The H&S File provides information required for future construction work, which includes cleaning, maintenance, alterations, refurbishment and demolition.  The Manual is to consist of the following parts, sub-sectioned as appropriate.

  - Section 1: H&S.  The Contractor is to provide a description of the site and the buildings thereon. This is to include details of construction methods and materials, which may present significant residual hazards in the future.

  - Section 2: Certificates.  The Contractor is to provide a copy of all Test Certificates (including but not limited to electrical circuit tests, start and commissioning tests) for the installations and plant, equipment, valves, etc, used in the installations. Warranty Certificates and guarantees are also to be included in this section.

  - Section 3: As-built drawings.  The Contractor is to provide as-built drawings recording details of all construction, electrical and mechanical work. A fire strategy for the site should also be included with drawings showing emergency escape routes, location of emergency and firefighting systems, services shut-off valves, switches, etc.

  - Section 4: Operation & Maintenance (O&M) schedules.  The Contractor is to provide recommendations as to the preventative maintenance, frequency and procedures to be adopted to ensure the most efficient operation of the systems. Manufacturer’s O&M schedules are to be included. Diagrammatic drawings of each system indicating principal items of plant, equipment, and valves are also to be included.

  - Section 5: O&M manuals.  The Contractor is to provide copies of manufacturers’ current literature for all products for which the particular proprietary brand has been chosen by the Contractor, including COSHH data sheets, catalogue list numbers and manufacturers recommendations for cleaning and maintenance.  The mechanical and electrical systems section shall contain a full description of each of the systems installed, written to ensure that the client fully understands the scope and facilities provided.  All manufacturers technical literature for items of plant and equipment, assembled specifically for the project, including detailed drawings, electrical circuit details and operating and maintenance instructions are to be included.

- Draft health and safety file.  A complete draft of the Manual must be submitted by the Contractor, not less than 4 weeks before the date for submission of the final copies of the Manual.  This is to be amended in the light of any comments and resubmitted to the PM.  Do not proceed with production of the final copies of the Manual until authorised to do so by the PM.