NYATI BARRACKS BUILDING 230 GE’S DEPARTMENT OFFICE EXTENSION WORKS

BRITISH ARMY TRAINING SUPPORT UNIT KENYA (BATUK)

BOOKLET 3 SPECIFICATION FOR CONTRACT No. KEN/GE/2303 BUILDING 230 GE’S DEPARTMENT OFFICE EXTENSION WORKS NYATI BARRACKS BRITISH ARMY TRAINING UNIT KENYA (BATUK)

# Contractor’s Design

- The contractor is to advise the authority of all design consultants / Sub-contractors who will be employed on this contract and the areas of their design responsibility. Any works undertaken without prior issue of full information for the necessary approvals will be entirely at the contractor’s own risk.

- The contractor shall not commence any work in accordance with any Design Document until the Authority1 has agreed the relevant Design Document. The contractor shall keep one copy of each Design Document on site, to which the Authority or his representatives may have access at all reasonable times.

Design Responsibilities

- Contractor’s Design Responsibilities. The contractor is responsible for the design of all elements except authority issued designs contained within the Schedule of Works.  Where required, all designs are to be submitted to the Authority for concurrence and authorisation prior to implementation of Works.  Where the nature of Works does not warrant full design, a descriptive proposal complete with proposal sketch must be submitted for concurrence.

- The contractor shall ensure all designs are in accordance with and include the applicable requirements as contained within stated references and all other design documents specified within these specifications.  NOTE: These references are provided as guidance and minimum requirement only; the responsibility remains with the contractor to ensure that all design and construction works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the works, geography, climate, environment, and theatre of operations.

- Where there are conflicts between the contractor’s design drawings and the Specification (Booklet 3) the Performance Specifications (PS) will take precedence in all cases.  Any queries should always be addressed to the Authority in the first instance.  The references and specified British Standards (BS) / Euro Norms (EN), within this PS are to be used (or similar Authority approved standards) as a minimum standard, throughout the Works.

- UK Building Regulations.  All works shall comply with the latest UK Building Regulations.  Should any variation be required, approval from the Authority shall be obtained in writing prior to the commencement of any Works.

- Health and Safety (H&S).  All works shall be carried out in accordance with the Health And Safety At Work Act 1974 (HASAWA 74).  The contractor shall submit a Construction Phase Plan (CPP) to the Authority for approval, including but not limited to all risk assessments, method statements and hazardous material procedures.

- Construction Drawings.  All works shall be constructed in accordance with the final approved contractor construction drawings and written proposals. Where a conflict in design is found, authorisation shall be obtained in writing prior to any changes in design.  No construction shall commence prior to obtaining written approval of the final construction drawings / proposal by the Authority.

- Design Life.  The design life of all new fuel and structural components shall be a minimum of 25 years.  The contractor shall supply and install all components, elements and systems / structures to satisfy this requirement, and any additional Contractual requirements that may apply.

- Existing Services.  The contractor is responsible for ensuring all services on or adjacent to the site that will be affected by the works are identified, located and appropriate action taken to prevent damage before work commences.  The contractor shall ensure that any existing services and concrete slabs are reinstated to a condition similar to the existing, with minimum disruption to existing facilities and services during construction.  All Works that could possibly influence existing services may only commence with written approval from the Authority. The Authority must be informed immediately if any unknown services are discovered that will have an impact on the works.

- The contractor shall ensure that any existing services and affecting works – including all connections and services tied into – are of an acceptable standard to ensure the required performance over the life of the facility.  Should it be found that one or more of the services (including but not limited to existing water, sewerage, drainage, and electrical services) is not considered acceptable to the requirements, the contractor shall inform the Authority and obtain written approval / instruction prior to taking any actions to rectify or make good the pertinent unacceptable situation.

Construction Preliminaries

- Existing Ground Conditions.  The contractor is responsible for confirming the existing ground conditions, which are to be considered whilst designing and compiling the CPP.

- Obstructions.  As the proposed Works are to be carried out around existing infrastructure and surrounding areas, there are obstructions in the form of fences, roads, and buildings etc. The contractor is to review the site before commencing works.

- H&S Restrictions, Precautions and Monitoring.  The contractor shall implement the requirements described in the HASAWA 74 to protect members of the public and persons visiting the site from risks arising from the use of equipment, materials or substances defined therein.

- Control of Noise and Vibration.  The contractor shall comply with the recommendations for practical measures to reduce noise set out in BS 5228-1:2009+A1:20142.

- It is expected that the contractor will not require a forward resources area other than the site. Should one be required a location shall be made available, as agreed by the Authority.  Packaging shall be to a good standard capable of withstanding transportation and handling loads.  The contractor shall be solely responsible for storage and movement of all equipment to site.  The contractor shall always remain responsible for the security of equipment including prevention of theft.

# Proposed Works

- Key Project Details:  The key project details are shown below:

| Contract title: Site location: | KEN/GE/2303 - Building 230 GE’s Department Office Extension Works Nyati Barracks |
| --- | --- |
| Proposed start date: | 7 February 2024 |
| Proposed completion date: | 7 October 2024 |
| Design life: | 25 years |

- Background: Currently Building 230 within Nyati Barracks is an industrial building used by Garrison Engineer Department as an office, store, and workshop area for the technical tradesmen. The building is one block single storey internally partitioned into different sections workshops, general store, office spaces, restroom, archive room etc as per attached drawing number DIO/KEN/NYA/GE/EXT/C/001. The building is a steel structure constructed and filled with masonry walls using concrete blocks and all the partitions have been done using accredited fireproof and soundproof gypsum boards.

- Contract Deliverables: There is a requirement to extend the current building as per the attached concept drawing number DIO/KEN/NYA/GE/EXT/C/001 to include more office spaces, storage cage and rest areas.

Requirements

- To carry out the building extension and partition works as per the scope of work below.

Scope of Works

- The scope of work shall be carried out in conjunction with the specification:

  - Demolish works.

  - Extension works of steel framed structure.

  - Partition works to allow for corridor and internal offices.

  - Structure infill and cladding.

  - Finishes.

  - Electrical services.

  - Testing and commissioning of the installation.

Performance Specifications

Civil Works

- Demolition

  - The proposed building to be extended has masonry walls which shall be demolished to be compatible with the new space layout. These walls are built with 200mm thick masonry blocks with plaster finish. Other walls are built with 100 mm thick wall with steel studs and gypsum cladding on either side.

  - Demolition for these walls will not include the foundations, and the superstructure will go up to where it is required, for example, opening for a door will be expected to end at the lintel/tie beam.

  - Part demolition will also be required to create space to tie in the existing structure with new structure, this is where the portal frames used as the main structure is boxed in with other elements. This however will only be demolished as reasonably required to create enough space for working.

  - Existing concrete will be required to be demolished to create space for foundation pad excavation. The existing concrete is strong enough to be retained as ground slab, however modifications will be required to achieve levels, this may necessitate to demolish the whole concrete slab depending on the contractor assessment.

  - Elements to be demolished may contain encased services and therefore the contractor will need to seek authority approval before demolishing and be careful while demolishing to avoid damage of services.

  - Relocation of existing underground drainage manhole that is not in use.

  - Areas to be demolished are shown on drawing No. DIO/KEN/NYA/GE/EXT/C/001.

- Excavation

  - There is a requirement to excavate ground for foundations. The existing ground is currently backfilled and compacted therefore excavation will be on compacted material. Excavations will be required as deep as to where there is firm ground formation.

- Backfilling

  - Backfilling will be from selected excavated material or imported material as per authority approval.

  - Backfilling of the excavation should be compacted in layers of minimum 100mm depending on the equipment used and the number of passes.

- Structural steel

  - The contractor is to match all structural steel elements as the existing on site, in all aspects, size, position, material, workmanship etc. however this does not exonerate the contractor from being the designer.

  - Existing members. All the members sizes of the new installation should match the existing members, new member positioning should be in line with the existing member positions.

  - Welds. All welds should be arc-welding as per BS EN 1011General welding guidelines and BS 4449. Material to be welded should be free from rust, dust and oils. Welds should be continuous without gaps and should be of uniform thickness.

  - Finish. Finish to the steel members should be galvanised, and weld painted with primer paint. All paint should match existing paints.

  - Bolting. Where the requirement is to join by bolting, the bolts should be fitted tight with a washer on both sides, the bolt should extend at least two threads after the nuts. Drilled holes for bolting should be at the centre of the member and should not exceed half of the member cross section.

  - Griding. All gridded parts should be smooth, and sand papered and left flush with the other parts of the member. Gaps should be filled with appropriate steel fillers and painted to match other parts of the steel members.

  - Workmanship. Workmanship should be maintained at high standards, all members should be parallel, right angles and vertical members should be plumb. Where painting has been done to surfaces it should be done uniformly all over the surfaces and should match the existing handrail.

- Reinforcement

  - The contractor is supposed to come up with specifications, drawings, design calculations and assumptions for all reinforced concrete required. A guide for the existing designs is attached as drawing no. K19000-DIO-4000-LT.

  - All Reinforcement should be Hot-Rolled High-Yield (HRHY) deformed steel bars to BS4449 Grade 460.

- Concrete

  - All concrete should be reinforced minimum C35/20 with supporting design calculations. Concrete design should be as per BS 8110-1: 1997.

  - Formwork to concrete should be made from rigid material with smooth surface so as to ensure the concrete finish is smooth and has no deformities.

- Walls

  - All external walls should be masonry to match existing in thickness minimum 200mm thick after finishes. Masonry walls should be bonded to the structure with tie strips welded to the portal frame after every alternative course. Vertical joints to be staggered every subsequent course to avoid continuous vertical joints.

  - Building stones should have a minimum of 3.5n/mm2 strength and should be of uniform material with no foreign particles.

  - Internal walls should be 100mm thick built with steel studs and gypsum cladding on either side to match the existing.

- Roof

  - The contractor is to match the roof structure elements as the existing on site, in all aspects, size, position, material, workmanship etc. However, this does not exonerate the contractor from being the designer.

  - Roof cladding shall be pre-painted box profiled sheet gauge 28 and should match existing sheets in all aspects, colour, gauge, overlaps, fixing, workmanship etc.

  - The existing rainwater goods should be extended to the end of the new extension, existing down pipe should be left in place. New down pipe to be installed and the end of extension and water channelled to the nearby existing underground storm water drain.

- Floor

  - The floor slab should be supported by a strip fill foundation constructed of reinforced C35 concrete strength with a nominal aggregate size of 20mm. The strip foundation should be RC 250mm thick minimum on a C15 mass concrete 50mm thick blinding.

- Doors:

  - Internal doors to be solid pressed MDF 45mm thickness with a view panel on the top part, this should match existing doors on site. Surfaces to have a painted finish. Locks to be dead lock with a thumb turn internally and key operated externally. Door handles and kick plates to be fitted on both sides.

  - External doors to be engineered steel door double leaf with push bar from inside and key operated from outside.

  - All ironmongery to be silver made.

  - Doors to include architrave on both sides of the frame, frames to be full width of the wall being fitted to.

- Windows

  - All windows to be UPVC sliding double leave windows, with a single leaf sliding from the outside. The design and mechanism to match existing.

  - All windows to be fixed with UPVC sliding insect meshes.

- Finishes

  - Floor finish to be linoleum PVC sheet to match existing in colour, skirting to be 100mm tile.

  - Wall finish to be plaster and paint from outside, skimming and paint to the inside. All paint used are to be vinyl matt emulsion water-based paints, colour matching existing.

  - Ceiling finish is to be suspended acoustic panels, 600mm2 with colour and texture matching existing.

- External works

  - The extension shall be built on an existing hard stand. The external ground works required will be tying the new into the existing ground and making good the affected areas.

  - Some services are to be fixed underground, this will need cutting into the concrete fixing the services and making good the affected areas.

General civil points

- Groundworks

  - Preparatory works. Site investigation is to be conducted by the contractor. The contractor must ensure a safe system of work is in place prior to the commencement of construction. This is to include Risk Assessments and Method Statements (RAMS) of works (as required). The area is to be clear from rubbish, rubble or debris prior to any works being carried out. All local services are to be identified and adequate precautions taken to protect such services from damage for the duration of the works. Ground preparation and earthworks to include removal of loose material to a suitable subgrade.

  - Unrecorded features. If any unrecorded legacy construction is unearthed, it is to be left undisturbed while further Authority instruction is obtained.

  - Unstable ground. The contractor is to inform the Authority without delay if any newly excavated faces do not remain supported sufficiently long enough to allow the necessary earthwork support to be inserted.

  - Hazardous, aggressive or unstable materials. The contractor shall not import or use fill materials which would, either by themselves or in combination with other materials or ground water, give rise to a health hazard, damage to the facility structures or instability in the filling. Construction materials should not include any finishes that may lead to shedding of particles.

  - Groundwater level. The groundwater level has not been established but it is not expected to impact on the works. It is the contractor’s responsibility to take into account the groundwater levels when submitting technical and commercial proposals.

  - Ground level. The contractor is to prepare the ground to enable construction. All materials arising from the works that are not suitable for general filling, are to be removed from site and disposed in a location approved by the local authority.

  - Sinkholes. Any sinkholes or soft spots are to be excavated and filled with a suitable fill material. The imported fill material is to be thoroughly compacted in layers not exceeding the capability of the compaction equipment. Any areas requiring extra or unforeseen works are to be reported to the Authority for concurrence on the remedial works prior to any rectification action.

  - Placing fill. The contractor shall ensure that excavations and areas to be filled are free from loose soil, organics, rubbish and standing water. All fill is to be placed and compacted against structures, membranes or buried services in a sequence and manner which will ensure stability and avoid damage. The plant employed for transporting, laying and compacting must be suited to the type of fill material being used and the size of the site. All compaction works are to be carried out correctly.

  - Compacted fill. Compacted general fill includes any materials that have been excavated or imported. Suitable and unsuitable materials that have been excavated, are to be kept separate to prevent cross contamination. If there is insufficient suitable material, the contractor is to provide the Authority with details (and quantities) of proposed imported material. The contractor is to spread and level all materials in layers and as soon as possible thereafter compact each layer using plant and methods suitable for the type of material. This should be laid in the below layers.

  - Disposal of materials. All materials requiring disposal is to be kept to a minimum on site and the following rules are to be applied:

    - Spoil heaps are not to be not more than 2.5m high.

    - Do not place any other material on top of spoil heaps.

    - Do not allow construction plant to pass over spoil heaps.

    - Prevent compaction and contamination.

    - Surplus subsoil is to be removed from site.

    - Separate different materials so as not to cross contaminate.

  - Grading. The crushed aggregate to be used as Type 1 is to conform to the grading requirement illustrated in Table 1. The optimum Moisture content of the Type 1 aggregate is to be maintained within a range of 8 - 12%, to aid the compaction process:

| BS EN Sieve Size | Percentage by Mass Passing |  |
| --- | --- | --- |
|  | Minimum | Maximum |
| 63mm | 100 | 100 |
| 31.5mm | 75 | 100 |
| 16mm | 43 | 81 |
| 8mm | 23 | 66 |
| 4mm | 12 | 53 |
| 2mm | 6 | 42 |
| 1mm | 3 | 32 |
| 63micron | 0 | 9 |
| The particle size shall be determined by washing and sieving method as stated in BS 933. |  |  |

- Formwork

  - Design and construction. Formwork is the responsibility of the contractor but must comply with series 1700.

  - Formwork should be timber or steel and should be set to provide the whole thickness of the concrete slab or height of the concrete member. They are set to line and level and must be firmly secured at intervals to avoid bulging. Form sections should be tightly set together to avoid play. Care must be taken to provide accurate and continuous to edge for the tamper to run on.

- Concrete

  - Concrete materials and mix designs. The contractor shall submit to the Authority the proposed concrete mix designs for all concrete works, including in-situ and pre-cast concrete. The contractor is to notify the Authority 48 hours prior to pouring of concrete. Cubes are to be taken from the structural concrete with 7 and 28day crushing results passed to the Authority by the contractor QC representative. The authority will request cube samples also that will be tested by the authority.

  - Joints. The contractor is to make suitable provision for construction, contraction, and expansion joints. All joints are to be in accordance with, series 1000. All joints are also required to be impervious to oils and fuels. The contractor is to provide joint details to the Authority prior to commencement of work.

  - Water. Any water used in the mixing of the concrete shall be clean and non-saline. The contractor is required to check any water sources used for salinity. The Authority reserves the right to check water salinity on site. Concrete made using saline water will be rejected and replaced by the contractor at their expense.

  - Concrete practice. The contractor shall ensure that suitable consideration is given to the placing of concrete in inclement weather and that appropriate precautionary / avoidance measures are taken to minimise shrinkage and cracking.

  - Reinforcement. Reinforcement steel may be either prefabricated sheet (BRC) or hot rolled steel or cold worked steel bars cut bend and fixed to form mesh. Reinforcement steel must be free oil, dirt loose dust and scales. when fabricated sheets are used individual sheets must overlap by more than one complete mesh and tied together but joining should be welded together. reinforcement should be placed on spacers to provide the recommended concrete covers. Reinforcement shall be cut and bent in accordance with BS 8666.

    - Concrete surface finishes. It’s the contractor’s responsibility to carry out all finishing operations at optimum times in relation to the setting and hardening of the concrete. Any exposed concrete edges are to have a 25 x 25 mm chamfered finish applied to prevent damage when striking formwork. e

    - Traffic on finished concrete. With the exception of plant and equipment required for any cutting of any sawn contraction joints, the fresh concrete shall not be subjected to the final expected external or superimposed loads, lateral or vertical for a minimum period of at least 28 days. A fence clearly demarcating this area will be required.

- Storm Water

  - A drainage system is required for rainwater goods which will connect to existing gutters and downpipe.

Electrical Works

- The building electrical installation shall comply with the requirement of the current edition of BS7671 latest edition based on the following system requirements:

- Purpose, Design and Structure.

  - The nominal system frequency shall be 50 Hz.

  - The nominal system voltage shall be 230V.

  - Number and type of conductors shall be single phase 3 wire ac.

  - Protection for safety shall be based on Automatic Disconnection of Supply (ADS).

  - Earthing arrangements shall be based on a TN-S system.

General lighting installation

- Design parameters: To meet the requirements of CIBSE Code for Interior Lighting, CIBSE Lighting Guide 3 and Lighting Guide 7, Building Regulations Part L2 and Guidance notes GIL20: 2002 and BS EN 12464.

- Lighting controls

  - Office areas lighting control shall be provided via the use of manual push on/off wall mounted light switches with movement detectors providing automatic ‘off’ should the office be vacated for a predetermined period.

  - Circulation spaces shall be provided with presence automatic ‘on’ and automatic ‘off’ control via the use of ceiling mounted movement detectors.

- Luminaires. The contractor is to ensure that all luminaires are suitable for their intended location and environment and their mounting and wiring configuration can be integrated into the ceiling system/background to which they are to be installed.

- Passive Infrared (PIR) sensor

  - PIR sensor shall detect occupancy in the controlled area by sensing the difference between heat emission from human body in motion and the background space.

  - The PIR sensor shall be provided with built-in heat sensing detector resided behind an optical lens.

  - The PIR sensor shall have 360o field of view with provision of mounting external covering mask for fine adjustment of the detection zone to meet the various applications.

  - When the sensor is mounted under the ceiling at 2.4 m above the finished floor level, the minimum detection coverage area shall not be less than 5 m in diameter.

  - A built-in LED lamp shall be provided and illuminated once the sensor detects movement within the control area.

  - Sensing sensitivity and extent of detection area shall be adjustable in field.

  - The sensor shall be provided with its own delay timer for adjusting the delay of switching off the lights between 5 seconds to 20 minutes when no occupancy being sensed.

- Emergency lighting installation

  - Design parameters to meet the requirements of BS 5266 Part 1:2005 Building Control/Fire Authority requirements. Maintained emergency illumination levels through escape routes shall be not less than 1 lux average, with anti-panic areas illuminated to 0.5 lux minimum.

  - The emergency lighting system shall be provided throughout consisting of self-contained standalone units serving LED luminaires in the positions identified on the drawings. The systems shall include an automatic self-test facility.

  - Luminaires shall be a combination of open area/anti-panic, escape route, illuminated exit and overdoor external emergency LED fittings in accordance with BS 5266.

  - Emergency luminaires shall provide a combination of 3 hour maintained or non-maintained coverage as appropriate.

  - The contractor shall include for the testing, programming, commissioning, and demonstration of the system prior to handover.

  - Handover will not be permitted until full certification has been provided, including certification to conform satisfactory design, installation, and commissioning of the system in accordance with BS 5266.

  - The building shall be provided with a standard electrical distribution arrangement comprising of the following basic elements:

    - All internal wiring and cables shall comply with the requirement of BS7671 Amendment 2: 2022 and be BASEC certified. All cables shall be concealed in a suitable trunking/conduit system.

    - The building shall be provided with a cable management system that shall be suitably sized for the intended purpose. The cable management system shall be facilitated using a trunking and conduit system which will be correctly terminated at switches, light fittings, and components. All trunking, conduits and fittings shall be effectively secured to the internal building fabric.

    - Cables entering the building structure shall be correctly terminated through a cable box and IP65 rated gland to prevent ingress of water, dust, and other foreign matter.

- Final Circuits

  - Final circuits shall be controlled by switches that ensure complete isolation of all conductors from the supply (i.e., all phases/line and neutral). Switches may be within the building if they conform to the category appropriate to the building.

  - Cables with a single solid core conductor or single layer of insulation are prohibited other than where they are used for alarm circuits or emergency lighting. Such cables shall be either Mineral Insulated Metal Covered (MIMC) or a thermosetting insulated fire-resistant type.

- Cables Used in Conduit and Trunking Systems

  - Power cables shall be synthetic rubber, PVC, LSF or XLPE insulated of 450/750- volt grade complying with BS 6007, BS 6004, BS 7211, or BS 7889. The cross- Sectional area of a conductor shall be appropriate for the current loading and not less than 1.5mm2. Cables for communication and alarm systems may be insulated flexible cords complying with BS 6500. The cross-Sectional area of a conductor shall not be less than 0.35mm2.

- Conduit

  - Conduits shall comply with BS 4568, BS 4607 or BS EN 61386-1. The following requirements also apply:

    - Conduits may be heavy gauge solid drawn, continuously seam welded and galvanised, Black enamel or Non-metallic.

    - Metal conduit shall be screwed tightly into all fittings and equipment with the minimum of exposed thread.

    - Running couplers are permitted.

    - Conduit shall be fixed with a minimum of 12mm clearance from walls and be supported by appropriately robust saddles.

    - The use of flexible conduit shall be kept to a minimum.

    - Rigid PVC conduit system shall comply with BS 4607 Part 1 and BS 4607 Part 2.

    - Additional protection against mechanical damage shall be provided as necessary.

    - Where slip joints or sliding couplers are used, joints should be made using a suitable adhesive.

    - A separate and adequately rated protective earth (PE) continuity conductor shall be installed throughout the systems.

- Trunking and Cable Tray Systems

  - Metallic or non-metallic trunking may only be used.

  - Cable tray or hanger support systems may be employed where armoured and metal-sheathed cables are used. Additional protection against mechanical damage shall be provided as necessary.

- Mineral Insulated Metal Covered (MIMC) Cables

  - Mineral Insulated Metal Covered cables shall comply with BS EN 60702-1 and shall be of a grade suitable for voltages up to 750V. The outer covering shall be of Low Smoke and Low Acid Gas Emission material. Cables shall be fitted with terminations, which comply with BS EN 60702-2.

  - NOTE: cable, glands and terminations shall be from the same manufacturer.

- Armoured and Metal Sheathed Cables

  - PVC and XLPE insulated wire armoured and sheathed cables shall comply with BS 6346 and BS 7655/BSI BS EN 50363. The outer metal sheaths shall be compatible with any explosives or chemicals used in the vicinity of the installation. Additional protection against mechanical damage shall be provided where necessary.

  - The armour shall be of galvanised steel wire for multi-core cables. Single core armoured cables shall be provided with non-ferrous armour. Use of steel armour for single core cable is not accepted.

- Cable Terminations

  - Cables shall be terminated in approved non-ferrous mechanical glands which comply with BS EN 62444 complete with compression devices for securing the cable sheath.

  - An armour clamp shall be required for bonding to metal sheaths.

  - Where the cables are installed in entirely dry situations, the gland shall be designed with a compressible gasket or packing for securing the inner sheath and means of anchoring the armour.

  - For cables installed wholly or partly in outdoor or damp conditions compressible sealing and clamping features shall be provided for securing the inner and outer sheaths and armour. Barriers shall be incorporated to prevent the ingress of moisture.

- Thermosetting Insulating Cables Low Fume Hazard (LFH)

  - Thermosetting insulated cables (non-armoured) shall comply with BS 7211 for lighting and power.

  - Thermosetting insulated cables (armoured) shall comply with BS 6724 for lighting and power.

- Communications and Instrumentation Cables.

  - Communications and instrumentation cables which are armoured, sheathed, or screened shall comply with BS EN 50290 and BS EN 50288.

- Identification of Core

  - Each core of a PVC or XLPE power cable shall be identified continuously throughout its entire length.

  - For a mineral-insulated cable each core shall be identifiable at its termination by the application of sleeves or discs of appropriate colours. Identification sleeves shall comply with BS 3858, where appropriate and shall have temperature rating similar to that of the sealant.

  - The identification shall take the form of appropriate colour or number codes in accordance with Table below, or the relevant Specifications.

| Function of core | Colour code | Number code |
| --- | --- | --- |
| Phase conductor of a single-phase circuit Phase conductor of a three-phase circuit Neutral conductor | Brown Brown, Black, Grey according to phase concerned Blue | L L1, L2, L3 according to phase concerned N |
| Core used as protective conductors shall have an exclusive colour identification of green-and-yellow. |  |  |

Table 1.0 – Core Identification of Power Cable

- Plastic or PVC Trunking and Accessories

  - PVC trunking and fittings shall comply with IEC 61084-1:2017

  - Cover for trunking shall be secured either by purpose-made rivets or clip-on mechanism to manufacturer’s standard.

- Socket Outlets

  - All socket outlets shall be of 3-pin shuttered type.

  - Socket outlet and plug rated at 13 A shall comply with BS 1363.

  - Socket outlet and plug rated at 5 A or 15 A for general application shall comply with BS 546.

  - Weatherproof socket outlets shall have cover with ingress protection of at least IP55 to IEC 60529.

  - For socket outlet installed outdoor and exposed to sunlight, the cover of the socket shall be UV stabilised, chemically and impact resistant with ingress protection of at least IP66.

- Residual Current-Operated Circuit-Breakers (RCBO)

  - RCBO’s shall comply with BS EN 61008 (RCCB’s) or BS EN 61009 (RCBO’s) as appropriate. The rated voltage, rated current, rated tripping current and rated breaking capacity shall be as indicated.

- Marking and Notices

  - All diagrams, charts, tables and the wording for labels and notices shall be submitted for the approval of the Authority before they are installed.

  - Identification labels shall be fixed to the outside of equipment enclosures. Label format and materials shall be appropriate to the installation and shall be fixed by non-corrosive materials appropriate to the intended application and location.

  - Characters for labels fixed on the means of isolation at the origin of each installation shall be at least 10mm high and 1.5mm thick. On all other labels characters shall be at least 4mm high and 0.5mm thick.

- Selection of cable supports - The type and sizes of cable support systems shall be selected by the contractor to suit the circumstances of the installation, unless otherwise indicated.

- Installation of perforated cable trays.

  - Perforated metal cable trays shall be formed from plain steel sheet complying with BS EN 10149-1 and shall be hot-dipped galvanised to ISO 1460: 2020 and ISO 1461:2022 after perforation.

  - Connection between adjacent lengths of tray

    - Connections between adjacent lengths of tray, tee, or bend pieces, shall be made by butt joints and fixed by mushroom-head steel roofing bolts and nuts complying with BS 1494.

    - The connection shall be mechanically strong so that no relative movement between the two lengths can occur.

  - Bend pieces shall be of the same material, thickness and finish as the main body of the cable tray and shall have an inner radius of 50 mm and a straight length of 100 mm at each end.

  - Tee pieces shall be of the same material, thickness, and finish as the main body of the cable tray. The distance measured between the point of inter-section and the end of the tee piece shall not be less than 100 mm.

  - Cutting of tray

    - Cable trays shall be cut along a line of plain metal only, i.e. they shall not be cut through the perforation.

    - All cut edges of the galvanised cable tray shall be prepared and treated with a cold galvanised paint.

  - Fixing of tray

    - The cable tray except those of short run less than 300 mm long where at least 1 set of hanger or bracket is required, shall be supported by at least 2 sets of hangers or brackets of adequate mechanical strength securely fixed to the walls, ceiling, or other structure. Unless otherwise specified the hangers or brackets shall be hot dip galvanised, painted with anti-rust epoxy coating or use anti-rusting material to prevent corrosion.

    - Fixings for cable trays shall be disposed at regular intervals not exceeding 1.2 m for straight run and at a distance not exceeding 225 mm on both sides from a bend or intersection.

    - A minimum clear space of 20 mm shall be left behind all cable trays.

- Wire mesh cable tray (cable basket)

  - The wire mesh cable tray system shall be provided for the support and accommodation of data and/or telecommunication cables where specified in the contract or on the drawings. The wire mesh cable tray system shall be of proprietary product complying with IEC 61537:2023.

  - All fittings and accessories associated with the installation of the wire mesh cable tray system shall be supplied by the same manufacturer with the same finish. All the accessories and tools for the connection of straight run pieces, formation of bends, risers, reducers, T-branch, etc. shall be provided by the manufacturer.

  - The steel wires of wire mesh cable trays shall be welded together and bent into rigid basket shape. The up-stand edges shall have a minimum height 50 mm to contain the cables. The surface of all system components, which come into contact with cables, shall not cause damage to the cables when installed according to the manufacturer’s recommendation.

Fire detection and alarm system

- Points to consider when carrying out the fire detection and alarm system installation:

  - The completed installation shall comply fully with BS EN 54 Parts 2 and 4, BS 5839-1 providing L2 category protection.

  - The Contractor shall supply and install a system to cover all areas of the building as detailed on the drawings.

  - The system shall include:

    - All manual and automatic detection devices,

    - Sounders

    - Control and indicating equipment

    - Cabling

    - Interfaces

    - Power supplies

    - Containment

  - The system shall all the above components as required forming a fully operational system.

Lightning Protection Systems (LPS)

- Points to consider when carrying out the LPS installation:

  - The LPS and the means of fixing it should be effective, simple, rugged, and permanent, and as far as possible, accessible for testing and maintenance; this is particularly applicable to earth termination networks which are hidden from view.

  - The use of unnecessary clamp connectors, which are liable to be disconnected, shall be avoided. Such connectors shall only be used where it is necessary to disconnect for test purposes.

  - The main danger posed by unbonded structural metal or metal cladding is damage from side flashing where the unbonded metalwork relative to roof or down conductors may offer an alternative current path to earth. This can be avoided by isolation or by bonding.

  - Bare conductors may lie on the surface of the roof provided that the roofing materials are either not of dissimilar metals to the air terminal conductors (which may cause corrosion) or if not metallic, are non-combustible and do not cover them.

  - If the roof surface is made from dissimilar metals or combustible material standoff fittings or fire-resistant layers shall be fitted between the conductor and the roof material.

  - The edges and apexes are the most vulnerable parts of a roof. Conductors shall therefore be placed as close as practicable to the edges (within 100mm) and shall be above the highest level of the roof. Where this is not achieved finials shall be installed to protect the vulnerable points of the roof-

  - Air Termination Network (ATN).

    - Air Termination Network conductors shall be of bare copper or aluminium only (i.e., not covered with insulation).

  - Down Conductors.

    - A surface mounted air termination network shall be provided with the required number of down conductors to meet the requirements of BN EN 62305 with a minimum of 4 around the perimeter of the facility. They should be equally spaced as far as possible but not more than 10m apart and shall be installed at exposed corners as a priority. Down conductor material may be bare copper or aluminium but shall be covered by insulating material or installed on spacers if it is required to prevent corrosion from contact with dissimilar metals. Each down conductor shall have an associated earth rod as specified in BS EN 62305 Part 3.

    - All down conductors shall be installed as straight and vertical as possible. They shall form the most direct path from the air termination to earth without sharp bends. Any unavoidable loops shall have a radius which conforms to the requirements of BS EN 62305 Part 3.

  - Earth termination networks.

    - Earth termination networks are to be a minimum of 600mm from the wall footings. An earth termination shall consist of earth electrodes made up of rods, tapes, or other means of providing a connection to the general mass of earth.

    - Where rod electrodes are used, they shall be driven to the depths necessary to give the desired earth resistance; the minimum depth being that at which the rod penetrates soil of permanent dampness. Where more than one rod is necessary to obtain the desired resistance, the spacing between the rods shall be at least equal to the driven depth. Earth rods have a finite life of approximately 30 years; increasing resistivity is caused by failure of the copper plating and consequent rusting of the steel rod beneath. Failing rods must be replaced.

    - When increasing earth rod resistance forces the driving of additional rods, the facility drawings shall be amended to reflect the change and future testing shall test the two (or more) rods as one electrode.

    - To allow for the isolation of and access to the electrodes during testing, the upper ends of the electrodes are to be terminated in a small, covered service pit, which shall be made easily accessible for inspection and testing.

  - Test Joints.

    - A multi-way, clamp type, test joint shall be constructed in each service pit. Only the earth termination networks shall be permitted below a test joint.

    - Earth electrodes shall be capable of being isolated and a reference earth electrode shall be provided for testing purposes (particularly when the surrounding soil is covered with concrete or tarmac).

  - Bonding

    - All major items of metal external to, and forming part of a facility, are to be bonded to the LPS. Bonding material for explosives buildings shall be of annealed copper for both internal and external bonds.

    - The metal sheath or armour of incoming electrical supply cables shall be bonded to the LPS and to the enclosure of the main switch at the cable entry point only. The metal sheath or conduit of each circuit leaving the main switch shall be bonded to the switch enclosure. All other metal service pipes or conduits shall be bonded to the LPS at their point of entry to the facility only. All straight runs of metallic conduit, pipe work or metallic cable sheathing shall be bonded to the LPS at each entry and exit point outside the building. It shall be possible to isolate the LPS connection for test purposes.

    - The LPS shall be connected to the facility Main Earthing Terminal (MET) “earth bus bar” at one point only. The means of connection shall be such that it can easily be disconnected to enable tests to be made.

- Inspection & Testing of LPS. Test Requirements: Establish the electrical integrity of bonds and earth impedance of the LPS as follows: The maximum allowed resistance to earth for the LPS shall be as follows:

  - Inaccessible Joints and Bonds – All joints and bonds which cannot be accessed for inspection purposes shall be tested to ensure adequate continuity. A maximum resistance of 0.2Ω shall be allowed across each bond or joint. For earth covered buildings where the LPS is covered, test between the air termination conductor and the earth electrode bonds.

  - Rebar - For structures utilizing steel-reinforced concrete (including pre-cast, prestressed reinforced units), the electrical continuity of the reinforcing bars shall be determined by electrical testing between the uppermost part and ground level. The overall electrical resistance shall not be greater than 0.2Ω, measured in accordance with BS EN 62305-3 Section E.4.3.

  - System Testing - This is a test of the LPS with all equipotential bonding in place between the LPS and other facility earthing systems, and with all earth electrodes connected. Measure the impedance to earth of the system at random points. The measured impedance is not to exceed 10Ω. If the impedance to earth of the whole LPS exceeds 10Ω, in the first instance, a check should be made to confirm that the earth electrodes conform to BS EN 62305-3.

  - Earth Electrode Testing – All earth electrodes shall be disconnected from the LPS and their impedances to earth measured. The impedance to earth of each earth electrode, when disconnected from the LPS, shall not be greater than 10Ω multiplied by the number of electrodes in the whole LPS earth termination network, and not differ by greater than a factor of 2 between each neighbouring earth electrode. If the impedance to earth exceeds the maximum determined value, in the first instance a check should be made to confirm that the earth electrode conforms to BS EN 62305-3.

  - Testing of the LPS earthing shall be carried out using the fall of potential method (i.e., 3 or 4 terminal) as described in BS7430 and IET Guidance Note 3.

  - Produce a detailed drawing of the LPS clearly showing the following.

    - Air Termination.

    - Down Conductors.

    - Earth Termination (i.e., Rods, Mats, Ring).

    - Bonding.

Public Address System (PAS)

- Points to consider when carrying out the PAS installation.

# The completed installation shall comply fully with BS 6259:2015.

  - The Contractor shall supply and install a system to cover all areas of the building as detailed on the drawings. The system shall include speakers, cabling, interfaces, power supplies etc. as required forming a fully operational system.

  - Box Speakers.

    - The speaker shall be contained in a rigid enclosure designed for surface mounting to match the existing installation. Its inner rear section shall be fitted with sound absorption lining.

    - On-axis frequency response not to vary by more than ± 10 dB over a frequency range 200 to 10 000 Hz.

    - Sensitivity should not be less than 90 dB/W.

  - Cable shall be laid in the same trays and routes as the fire alarm system cables.

Ventilation system

- Points to consider when carrying out the PAS installation:

  - The ventilation should be provided by oscillating ceiling mounted fan to match the existing.

  - The fan will be controlled using a fan speed controller linked with a fused spur switch unit to match the existing.

  - The ventilation is to be done as per BS EN 13141

General Points for the Entire Task

- Electromagnetic Interference: To minimise the electromagnetic interference generated from single core cables, the following arrangements shall be adopted:

  - All the single core cables of a circuit shall be of the same conductor, same cross-sectional areas, same type, same construction and from the same manufacturer.

  - All the single core cables of a circuit shall be of equal length and shall follow the same route of installation.

  - The single core cables shall not be able to operate individually.

- Fire Barrier: Where a cable duct passes through fire resistant structural elements, such as floor or wall designated as fire barriers, the opening thus formed shall be sealed with fire resistant materials having the same degree of fire resistance as the structural element. Penetration seals for openings where ducts, cables and the like passing through the fire barrier shall be provided in compliance with Code of Practice for Fire Safety in Building.

- Inspection and Test Procedure.  The inspection and testing of the new installation shall include the following:

  - Visual inspection.

  - Test in accordance with the standard test procedure as per BS and EN for each serial on the performance specification.

- Trenching.  No work shall commence until the Authority has taken all reasonable steps to ensure that the area is free of all cables, drains and other services.  Cable Avoidance Tool (Cat) and Signal Generator (Genny) or any other equivalent cable detector tools shall be used to detect services.  Unless otherwise indicated the following is required.

  - Excavations within 600 mm of existing services shall be by hand digging.  Any damage to services shall be reported immediately to the Authority.  No repairs or replacement shall be done unless the Authority gives approval.  All works will be at the Contractors expense.

- 'As installed/built' drawings, maintenance manuals and training.

  - During the progress of the contract, the Contractor shall record on drawings (in an approved manner) the information necessary for preparing the ‘As Installed’ record drawings.

  - These record drawings shall be included within the operation and maintenance manuals, which shall also include test certificates, manufacturer’s literature, system description, etc.

- Commissioning.  The Contractor shall be responsible for carrying out all inspection and testing. The Contractor is to complete their required sections of the commissioning forms and present them to the Authority.

- All Works shall be carried out maintaining Safe System of Work (SSOW) practices as per JSP 375 Part 2 Vol 3.

- Existing Services and Facilities.  It is the Contractor’s responsibility to conform to the following:

  - The Contractor is responsible for ensuring all services or facilities on or adjacent to the site including public roads approaching the site, that may be affected by the works are identified and that appropriate action is taken to prevent damage occurring before work commences.  Liaison between adjacent sites is essential where any activity on the site or on adjacent sites are identified which may have an impact on the project or which may be impacted upon by the project. The Authority is to be informed in writing at the earliest opportunity (e.g., services requiring redirection).  If damage is incurred, it will be the sole responsibility of the Contractor to rectify to the Authorities given standard.

  - All works that could possibly influence existing services may only commence upon receipt of appropriate written documentation (e.g., Statement of known services), a copy of which must be provided to the Authority.  The Contractor must discuss in advance with the Authority which specific agencies it will need to obtain approvals and documentation from (e.g., NEMA etc.).  Obtaining any such approvals and documentation is the Contractor’s responsibility.

  - Upon request, and subject to security caveats, the Contractor may have access to all relevant existing drawings relating to the contracted works on the site, held by the Authority.  During the tender stage, the Contractor shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

  - The Contractor shall conduct a detailed site investigation and ensure that any existing services which are to be tied in to are of an acceptable standard to ensure the required performance over the life of the new facility.  Where it is found that an existing service (including, but not limited to water, sewerage, drainage and electrical power) is not adequate for the project requirements, the Contractor shall inform the Authority and obtain written instruction prior to taking any remedial action.

  - Where the proposed works interact with any existing facilities and defects are found in said facilities this shall be reported to the Authority without delay.  Instructions must be obtained from the Authority before proceeding with work which may cover up, or otherwise hinder access to, the defective construction, or be rendered abortive by carrying out of subsequent remedial work.

- Setting Out.  The Contractor is responsible for all setting out and for all on-going monitoring of line, level and accuracy as works progress.

- Communication will be the key in planning and conducting concrete works, excavation works, design works, final connection, and new connections to the existing systems, and during commissioning.  Therefore, contractor must communicate with the authority in timely manner.

- All personnel employed to work on the above tasks should be suitably qualified and must have their CV submitted to the authority.  They may also be interviewed by the authority to confirm their competency.

- Before any work is performed, pertinent risk assessments and method statements should be issued to the authority.  The authority will then issue the appropriate permits to work if required. The contractor must seek Statement of known hazards from the authority prior starting and excavation on site.

- All detailed design drawings, pipes sizing calculations, cable sizing calculations, structural calculations, electrical calculations and mechanical calculations, concrete mixing ratios, materials safety data sheets and samples for materials are to be submitted to the authority for approval beforehand.

- Authority will issue the necessary paperwork for transportation of goods in the camp e.g., gate pass.

- Any Scaffolding, ladders to be used in the tasks are to be serviceable and where required presented to the Authority for inspection and permission to use.

- Any electrical works will be carried out as per BS 7671-18.

- Under no circumstances will trench digging works be carried-out without gaining statement of known hazards from the authority.

Restrictions / Constraints

- Access to the Site.   This is to be agreed in detail with the PM prior to start on site.  Passes may be required, and the contractor should submit the details and ID of any technicians that will be working on the contract within the tender return.

- Notice.  The contractor is to provide notice to the authority in writing (or through email), before a minimum of 3 working days prior to the work on site.  The notice must include the date and expected time of arrival, name, and ID No of the workforce, and contact telephone no for both the contract manager and the workforce.

- Working Hours.   The contractor may choose to work in their suitable hours; however, assistance from the authority will only be available 0800-1600 hrs Mon – Fri.  For any assistance from the authority, the contractor must submit request with a minimum of 24hrs notice.

- Permits to Work.  Permits to work applicable for this task are as follows:

  - Statement of Known Services.

  - Working at Height.

  - Confined Spaces.

  - Electrical connection permit

Annexes:

A.	Generic Points - Pre-Contract

B.	Generic Points - Pre-Construction.

C.	Generic Points - During construction.

D.	Generic Points - Post construction.

E.	Drawings.

Annex A to

CONTRACT/KEN/GE/2303/BK/3/Spec

Dated 8 Mar 24

Generic Points - Pre-Contract

Designers

- This project is a Design and Build contract, meaning the contractor must fulfil the role of both the designer, and the principal contractor.  The design work must be carried out by a qualified and competent person.  The contractor shall ensure all designs are in accordance with, and includes the applicable requirements contained within references and all other design documents specified within this PSpec.  If the contractor is not competent to carry out some aspects of the design work, a qualified person or consultancy firm should be sub-contracted to carry out that portion of the work.  The contractor is to inform the authority of all design consultants/sub-contractors who will be employed in this project and the areas of their responsibility.

- Where design work is required to be carried out by a professionally qualified person, details of their qualifications and experience, registration with the Engineers Board of Kenya and copy of their professional indemnity insurance needs to be submitted to the authority.

- Pre-Construction Information (PCI).  All the pre-construction information is contained within this Booklet 3. If any additional information is required, the contractor is to request a copy in enough time to affect any changes prior to tender submission.

Contractor’s Design

- The contractor is to ensure that their design meets the parameters outlined within this Specification.

- Site Visit.  The contractor shall acquaint himself completely with the exact conditions relating to access and site environment, along with the layout, conditions and positions of the existing services, the full extent of the works required, and the supply and conditions affecting labour, carriage, carting, unloading, storage, tools, scaffolding etc. as well as any security and access constraints.

- Existing Ground Levels.  The contractor shall confirm or identify all existing site levels required prior to any construction works.

- Ground Water Level.  The ground water level has not been established but it is not expected to impact on any of the works.  It is the contractor’s responsibility to consider the ground water levels when submitting technical and commercial proposals.

- Existing record drawings.  The contractor will upon request, be supplied with copies of all available and relevant as built drawings.  The contractor during tender stages shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

- The responsibility remains with the contractor to ensure that all design and construction works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the works, geography, climate, and environment.  Where there are conflicts between the design drawings and detailed specification the detailed specification will take precedence in all cases.  Any queries should always be addressed to the Authority in the first instance.

Use of Design Codes and Specifications

- All designs must conform to the most current editions of BS or EN.  Other Design Codes may, on occasion, be used if they meet the minimum requirements and the contractor shall submit proof of equivalency to the Authority for approval of use.  The Authority can be approached for clarification of the relevant BS if required.  On no account is the contractor to use any design information other than that stated or approved by the Authority.

- All contractors will be required to certify their designs for conformity to the specification and to the relevant BS/EN.  Only appropriately qualified and experienced engineers are to certify the designs.

  - Design Conformity.  The design engineer is to produce a letter to state that the design conforms with all applicable legislation, most current editions of BS or EN, and best practice.  The letter is to have the company header (of the design agency if sub-contracted) and to be signed by the lead designer with his name, contact details and qualifications detailed in the signature block.

  - Construction Inspections.  Prior to the start of construction, the contractor, designer, and authority shall agree key stages at which the works are to be inspected by the designer for compliance with the design.

  - Build Conformity.  At the end of the project, the lead designer is to confirm in writing that the works have been built correctly, in accordance with his design.

- Design Life.  The design life of all new works to first major overhaul, repair or replacement is 25 years.  The contractor shall supply and install all components, elements, and systems/structures to satisfy this requirement and provide documentary evidence.

Annex B to

CONTRACT/KEN/GE/2303/BK/3/Spec

Dated 8 Mar 24

Generic Points - Pre-Construction

Detailed Design and Planning

- Additional Design Information.   The contractor is to submit any additional design information to the Authority prior to commencement of the construction phase.  The authority will examine design documentation and shall be entitled to reject a design as unsatisfactory where it is not in accordance with the specification, statutory regulations or if it would not be fit for purpose.

- A copy of all construction drawings is to be provided by the contractor to the PM prior to commencing Works.  Amended or updated drawings are to be provided as necessary.  The minimum design information to be provided by the contractor shall include the following:

  - Any additional design calculations for the works.

  - Any additional general layout plans for the site and the structures.

  - Any additional detailed structural design, calculations and drawings.

  - Any additional foundation plans shall (as a minimum) indicate: all footing locations and dimensions, screeds and / or ground slabs or plinths, as applicable.

  - Any additional services layouts and calculations.

  - Any additional detailed Electrical, Mechanical drawings and calculations.

  - Manufacturer product details including safety data sheets.

  - Designers risk register.

  - Project Programme to be regularly updated or upon request by the Authority and provided electronically on Microsoft Project or equivalent in a regularly basis or on request.

Design Responsibilities (under CDM)

- The designer has the following responsibilities under CDM 2015:

  - Eliminate Hazards and Risks During Design.  Designers are to analyse the risks posed during the construction, daily use, maintenance, and ultimate demolition of the facility.  Once identified, these risks should, where practicable, be designed out.

  - Provide Information on Remaining Risks.  Remaining risks after the design process are to be compiled onto a designer’s risk register and submitted with the final design.

Provision of Information

- Unless otherwise specified the following is to be provided:

  - Three copies of all information, including valid certification, in respect to work, goods and materials proposed by the contractor, shall be supplied to the Authority.  Where the original document is written in a language other than English, it shall be accompanied by an English translation.

  - Information and certificates shall be supplied at least two days prior to the use of the work, goods, or materials in the Works.

  - Three copies of detailed working and fabrication drawings and calculations shall be submitted to the Authority for reference purposes.  Such submittal shall in no way relieve the contractor of his responsibilities for the work under the contract.

- The Authority reserves the right to request copies of all calculations and drawings for analysis prior to the commencement of any construction on site.  The contractor will provide copies of all calculations and ‘As Built Drawings’ for the Health and Safety File.

- The signed and approved drawings shall be used as the construction drawings on site for all work purposes and to satisfy the requirements as specified by the Construction, (Design and Management) Regulations 2015 (CDM 2015) & appropriate ACOP.

Construction Phase Plan

- Under the requirements of CDM, the contractor is to prepare a construction phase plan detailing how they will safely conduct the works.  Risk assessments are to be included for all elements of work and method statements are required for any works that are out of the ordinary or high risk.  The Construction Phase Plan must cover the following area’s (where applicable):

  - Safety Risks:

    - Protecting the public.  The public is any persons not involved in the works.  Particular attention should be paid to area’s where children are likely to have access to the site outside of working hours.

    - Traffic routes.  Traffic routes for delivery of stores and equipment should be clearly highlighted and controlled.  Movement of plant and machinery on site should be organised in a way that minimises risk to the workforce and any visitors to site.  Care must also be taken to minimise risk from existing traffic routes.

    - Existing buried and overhead services.  Some of these may be identified in the permit to dig process, however care must be taken to identify and avoid any damages on existing services.

    - Adjacent land use.  The use of adjacent land and properties will affect the level of protection for things such as noise and dust suppression etc.

    - Stability of nearby structures.  Care must be taken that works do not affect the stability of nearby structures.

    - Demolition works.  Demolition work is a particularly dangerous task and careful planning must be conducted.  Method statements for all aspects of demolition will be required by the authority.

    - Work equipment.  Work equipment must be calibrated where necessary, inspected and is to be in a suitable condition not to cause a hazard on site.

    - Electrical safety.  Electrical works will be conducted in accordance with the JSP and CDM recommendations.

    - Preventing falls.   Falling from height is one of the biggest killers in the construction industry.  Even when not working under a permit, it is expected that the correct equipment and management methods are utilised to prevent falls.

    - Working with or near fragile materials.  Fragile materials should be identified prior to work commencing and appropriate action must be taken.

    - Control of lifting operations.  Lifting operations are to be carefully planned and controlled on site.

    - Excavations / confined spaces.  All excavations inside buildings where work is to be conducted are to have the appropriate level of shoring / protection.  Where an area is deemed a confined space, a permit may need to be issued to control the works.  If permit is not issued, the contractor is to have a suitable system in place with appropriate paperwork i.e., risk assessment and method statements associated to the work being carried out.

    - Working on or near water.  If working on or near water the contractor is to plan the works to minimise the risk drowning.

  - Health Risks:

    - Temperature / weather protection.  Protection from the elements for the workforce.

    - Substance misuse.  The misuse of drugs or alcohol by the workforce.

    - Manual handling.  Correct lifting techniques, lifting equipment etc.

    - Dust.  Dust suppression and removal.

    - Noise.  Reduction and suppression of noise.  Management of timings for noisy activities etc.

    - COSHH.  The correct storage and use of hazardous substances.  Appropriate protective equipment must be worn when handling COSHH materials.  Safety data sheets must be always available on site.

    - Asbestos.  Identification and appropriate management of Asbestos.

  - Provision of:

    - Welfare facilities.  Water, food, shade, toilet facilities etc.

    - First aid.  There should always be at least one qualified first aider with appropriate medical equipment on site.

    - Emergency procedures.  Procedures for response to incidents such as Fire, major and minor injuries, security incident etc.

    - Reporting of accidents, incidents or near misses.  Procedure for reporting and follow-on actions to prevent re-occurrence.

    - Waste management.  Management, storage, and disposal of waste and arising from the site.

    - Fire prevention, detection, and firefighting.  Methods to prevent the start and spread of fire, and to identify any fire that does start. There must also be appropriate firefighting equipment available and access to the site for firefighting services.

Pre-Start Meeting.

- Prior to the commencement of any works, a Pre-Start meeting is to be held with the contractor, lead designer and chaired by a representative from the authority.  The following topics are to be discussed as a minimum:

  - Mobilisation plan

  - Site setup

  - Health and safety

  - Required permits

  - Access and security

  - Programme

Annex C to

CONTRACT/KEN/GE/2303/BK/3/Spec

Dated 8 Mar 24

Generic Points - During Construction

Facilities/Temporary Works/Services

- Locations.  The contractor is to agree with the PM of the intended siting of all spoil heaps, temporary works and services in advance.  The Authority shall verify with the contractor which site features are to be removed and protected during construction works.

- Survey and setting out.  The contractor will be responsible for all setting out and levelling during construction.  The contractor shall keep updated schedules and drawings of all benchmarks used in setting out of the site; these must be made available to the Authority when required.  A minimum of 2 survey control stations are to be constructed, one visible from the site at 50 m and the other 200 m away from the first but in line of site.

- Record Drawings.  The contractor shall record details of all grid lines, setting out stations, benchmarks and profiles on the site setting out drawing.  Retain on site throughout the contract and hand to PM on completion.

- Signage.  The contractor shall supply and erect all applicable and appropriate signage to the site.  This shall include as a minimum all H&S signage, directions and location of site office and emergency contact details of the contractor’s representative on site.  Temporary warning signs and careful demarcation of works areas must be undertaken with care to ensure compliance with all requirements.

- Lighting and Power.  The contractor shall provide all lighting and power for his works.  No facility will exist on site from the general base infrastructure.

- Communications.  The contractor shall provide his workforce with adequate means of communications throughout the duration of the contract period to carry out the work specified.

- Temporary Services.  The contractor shall provide temporary service connections to both mechanical and electrical systems.  All temporary service connections are to be in accordance with current UK regulations.

- Use of the Site.  The Site shall not be used for any purpose other than undertaking the specified works.  The contractor may erect the site office and storage compound in a location agreed with the Authority.  No storage of materials, parking of vehicles, temporary accommodation or any other use of areas beyond the boundaries shall be permitted.  Under no circumstances shall it be permissible for the contractor to cause an obstruction to normal pedestrian or vehicular movements within the vicinity of the site.

- Restrictions to the Works.  The Works are to be undertaken without interfering with every day running of the Authority’s operations within the area.  The demarcation of the Site boundary is to be obvious and clearly marked to restrict access to the Site whilst the Works are being undertaken.

Project Management

- The authority.  The Superintending Officer (SO) has overall authority on this project.  For this specification, the SO is the only person acting on behalf of the authority, in most cases.

- The contractor shall not commence any work in accordance with any Design Document until the authority has agreed to the relevant Design Document.

- Buried Services.   Prior to carrying out any excavation work, the contractor must:

  - Obtain a Permit to Dig (Statement of Known Services) and all drawings relating to existing services that may interfere with the proposed works.  A copy of the Permit to Dig must be given to the Authority prior to any works commencing.

  - Identify all local services and take adequate precautions to protect such services from damage for the duration of the works.

  - Inform the Authority immediately if any unknown services are discovered that will impact on the works.

- Supervision.  The contractor shall accept responsibility for delivery, co-ordination, supervision, and administration of the Works, including all subcontracts.  They shall arrange and monitor a programme with each subcontractor, supplier, local Employer, and any statutory undertaker, and obtain and supply information as necessary for co-ordination of the work.

- Site Diary.  The contractor shall keep an up-to-date site diary.  This document is to be used to record all decisions made on site both verbally and written.  The document is also to be used to record visits to site and note anything, which has a direct effect on the project in terms of cost and extensions to time, or any other occurrence that affects the project programme.  This document will be used as the audit trail considering any disputes, concerning the project.

- Contractor’s Site Meetings.  The contractor is to hold meetings with appropriate subcontractors and suppliers shortly before site meetings with the Authority to facilitate accurate reporting of progress.

- Site Meetings.  The authority, or his representative will hold regular progress meetings to review progress and other matters arising from the administration of the Contract.  It will be the contractor’s responsibility to ensure the availability of accommodation and attend all such meetings.

- Liaison with the Authority.  The contractor shall designate a site manager from within his organisation who will be responsible for liaising with the SO on a day-to-day basis and as the need arises.  At all times the contractor shall ensure that the Site Manager present on site has the capability of reading, writing, speaking and receiving instructions in the English Language, including being able to understand and interpret technical drawings and specifications.  The Site Manager must be able to explain the work operations to person performing the work in a language that those performing the work are capable of understanding.  The authority shall have the right to determine, whether the proposed representative has enough technical and linguistic capabilities.

- Approvals.  Where products or work are specified to be approved or the authority instructs or requires that they are to be approved, the same must be supplied and executed to comply with all requirements.

- Access.  The contractor shall provide at all reasonable times, access to the Works.  The contractor shall supply the authority with copies of any documentation and drawings, which may be required for the purposes of monitoring the work performed under this or any sub-contract.

- Regulations.  It is the contractor’s responsibility to be fully conversant with all local/MOD regulations and requirements in respect of fire, safety, security, and occupational health, etc.  These are to be fully complied with throughout the contract period.

Health and Safety

- Health and Safety (H&S).  All works shall be carried out in accordance with the HASAWA 74.

- JSP 375.  The contractor shall comply with the Client’s permit to work system and the JSP 375, Volume 3, (details of which are obtainable from the Authority), including the provision of method statements, risk assessments, switching/isolating safety programmes, permit to dig, etc.

Permits to Work

- Permit to Dig. If any excavation or breaking of ground is to be carried out, the contractor must request a permit to dig at the Pre-Start meeting.  Should any excavation be conducted without a permit, the contractor may be removed from site.

- Hot Works Permit. The contractor is to establish at the Pre-Start meeting if hot work permits will be required for his location of work.

- Authorised Persons (APs). The Authority has (APs) in their respective discipline to facilitate Safe Systems of Work (SSoW).

- Skilled Persons & Persons in Charge (PIC).  Any works required to be completed under a JSP 375 permit must have a dedicated PIC and the work carried out by registered skilled persons. At the Pre-Start meeting the contractor must establish if any of his works require a permit, and if so, arrange for currently registered personnel to conduct the works, or registration of the contractor’s personnel.

- CDM 2015. The contractor shall submit a CPP file to the Authority for approval, including all risk assessments, method statements, hazardous material procedures etc to comply fully with Construction, Design Management Regulations 2015 (CDM 2015) & appropriate ACOP.

Quality of Work

- Quality Standards/Control.  The contractor will provide evidence to the authority of his quality standards and controls and will produce a plan detailing Quality Control (QC) activity for the authority to plan for witnessing of critical activities.

  - General Quality of Products.  All products shall conform to the following subparagraphs:

    - Products to be new unless otherwise specified by the Authority.

    - For products specified to a BS or EN obtain certificates of compliance from manufacturers when requested.

    - Where a choice of manufacturer or source is allowed for any product, the whole quantity required must be of the same type, manufacture and/or source unless otherwise approved.  Produce written evidence of sources of supply when requested by authority.

    - Ensure that the whole quantity of each product required to complete the work is of consistent kind, size, quality, and overall appearance.

    - Where consistency of appearance is desirable ensure consistency of supply from the same source.  Do not use different colour batches where they can be seen together.

    - If products are prone to deterioration or have a limited shelf life, order in suitable quantities to a programme and use in appropriate sequence.  Do not use if there are any signs of deterioration, setting or other unsatisfactory condition.

  - Proprietary Products.   All products shall conform to the followings:

    - Handle, store, prepare and use or fix each product in accordance with its manufacturer’s current printed or written recommendations/instructions.  Inform authority if these recommendations/instructions conflict with any other specified requirement. Submit copies to authority when requested.

    - The tender will be deemed to be based on the products specified and recommendations on their use given in the manufacturer’s literature current at the date of tender.

  - Obtain confirmation from manufacturers that the products specified and recommendations on their use have not been changed since that time.  Where such change has occurred inform authority and do not place orders for or use the affected products without further instructions.

  - Checking Compliance of Products.  The contractor shall check all delivery tickets, labels, identification marks and where appropriate the products themselves to ensure that all products comply with the project documents. Check that the products comply with the following sub-paragraphs.

    - The sources, types, qualities, finishes, and colours are correct, and match any approved samples.

    - All accessories and fixings that should be supplied with the products have been supplied.

    - Sizes are correct.  Where tolerances are critical, measure enough to ensure compliance.

    - The delivered quantities are correct, to ensure that shortages do not cause delays in the work.

    - The products are clean, undamaged, and otherwise in good condition.

    - Any products with a limited shelf life are not out of date.

  - Protection of Products.  All products shall be protected to ensure that they remain in the condition they are required to be in.  The contractor is to ensure that products are to be prevented from overstressing, kept clean, protected from the elements, and kept in original wrappings until required for the project.

- Prohibited Products.  The contractor shall not employ on or incorporate in the Works any of the following products and shall impose a like obligation upon all Sub-contractors.

  - Asbestos materials as described in the Asbestos Prohibitions Regulations 1985 and the Asbestos Products (Safety) Regulations 1985.

  - Lead or any products containing lead for use in connection with drinking water.

  - Materials that are generally composed of mineral fibres either manufactured or naturally occurring which have a diameter of 3 microns or less and a length of 200 microns or less or which contain any fibres not scaled or otherwise stabilised to ensure that fibre migration is prevented.

  - Other products or substances generally known to be deleterious to health and safety at the time of use or to the durability of the property in the circumstances in which they are being used.

- Hazardous, Aggressive or Unstable Materials.  The contractor is not to import or use fill materials which would either in themselves or in combination with other material or ground water, give rise to health hazards, damage buildings or structures.  The construction materials should not include any finishes that may lead to shedding of particles.

- Defects in Existing Construction/Services.  This shall be reported to the authority without delay. Obtain instructions before proceeding with work which may be covered up or otherwise hinder access to the defective construction or be rendered abortive by the carrying out of remedial work.  This is particularly relevant in relation to the expansion of the existing service runs.

- Proposals for Rectification of Defective Work/Products.  As soon as possible after any part(s) of the work or any products are known to be not in accordance with the Contract, or appear that they may not be in accordance, the contractor is to submit proposals to the authority for opening, inspection, testing, making good, or removal and re-execution. Such proposals may be unacceptable to the authority, and he may issue contrary instructions.

- Quality Control.  The contractor is to establish and maintain procedures to ensure that the works, including the work of all Subcontractors, comply with specified requirements.  This is to include all testing of materials that are to be incorporated into the project (e.g., concrete).  The contractor is to maintain full records, keep copies on site for inspection by the authority, and submit copies of parts of the records on request.  The records must include the following:

  - Identification of the element, item, batch, or lot including location in the works.

  - The nature and dates of inspections by the contractor or authority, tests, and approvals.

  - The nature and extent of any non-conforming work found.

  - Details of any corrective action.

- Materials Testing.  It is the contractor’s responsibility to carry out all materials testing and present all test results to the Authority on request and within the H&S file.  The Authority will carry out concurrence quality control material tests at regular intervals.

- Notification.  The Authority requires to be informed in writing at least 10 days in advance of any tests and commissioning being carried out.  Access must be available to the Authority to carry out testing as deemed necessary by the Authority.

Annex D to

CONTRACT/KEN/GE/2303/BK/3/Spec

Dated 8 Mar 24

Generic Points - Post Construction

Completion / Handover

- Commissioning Period.  Within the tender submission the contractor shall submit a Works Commissioning Plan, setting out his commissioning proposals including the preparation of handover documentation.

- Notice of Completion.  The contractor is to provide the authority at least five days’ notice of the anticipated dates of practical completion of the whole or parts of the Works.

- Mechanical and Electrical Services.  Mechanical and Electrical Services must have final tests and commissioning carried out by the contractor so that they are in full working order at practical completion.  This includes buried but not connected cables and pipelines.

- Timing of Tests and Inspections.  The contractor is to agree dates and times of tests and inspections with authority four days in advance, to enable the authority and other affected parties to be present.  On the previous working day to each such test or inspection the contractor is to confirm to the authority that the work or sample in question will be ready or, if not ready, agree a new date and time.

- Test Certificates.  The contractor is to submit a copy of each certificate to the authority as soon as practicable and keep copies of all certificates on site.  Copies should be included in the Health and Safety File on handover of the works.

- Work at or After Completion.  The contractor is required to undertake the following works prior to handover.

  - Make good all damage consequent upon the work.

  - Remove all temporary markings, coverings and protective wrappings unless otherwise instructed.

  - Clean the works thoroughly inside and out including all accessible ducts and voids; remove all splashes, deposits, efflorescence, rubbish and surplus materials consequent upon the execution of the work.

  - Cleaning materials and methods to be as recommended by manufacturers of products being cleaned, and to be such that there is no damage or disfigurement to other materials.

- Security at Completion.  The contractor is to leave the Works secure with all accesses locked.  Account for and adequately label all keys and hand over to the authority with itemised schedule, retaining duplicate schedule signed by the authority as a receipt.

- Making Good Defects.  The contractor is to decide with the authority and give reasonable notice of the precise dates for access to the various parts of the Works for purposes of making good defects.  The authority is to be informed by the contractor when remedial works to the various parts of the Works are completed and ready for approval.

- Inspection, Testing and Commissioning.  The installations shall be tested and inspected in accordance with but not limited to the current CIBSE Codes, BS, EN where appropriate, etc.  Advance notice of tests shall be given (minimum of 7 days prior to notification).

- Test and inspection certificates are to be approved by the Authority; preferred document templates will be provided by the Authority on request.  Test certificates shall serve as a record that the item referred to has been shown under test to meet the requirements of the specifications and of BS as applicable and shall be dated, numbered and clearly referenced to the item tested by means of serial, chassis or other manufactures reference number permanently marked in a conspicuous position.

- The calibration certificates for the testing of the equipment are to be available on request to be shown to the Authority for scrutiny.  The contractor shall ensure all calibrations are in date.  The Authority reserves the right to have an independent electrician available during the test and inspection phase.

- Any defects of workmanship, materials or non-compliance with the specifications or other irregularities which become apparent during the tests shall be rectified by the contractor, at his own expense, until the whole work is free from defects and in full working order to the complete satisfaction of the SO.

- All materials used for construction of permanent works shall have suppliers’ specifications and/or testing certificates available.  Where materials are used as part of a whole or in conjunction with other materials, and in any case where site testing is required by best practice, verification of quality and specifications should be allowed for the parts / items / products (suppliers’ specification) as well as the whole (site testing).

- Defects Liability Period.  A defects liability period shall apply for the works as detailed above.  The contractor will be responsible for making good at his own expense any defects in the works arising within that period.  The contractor is to ensure that a defects inspection is conducted 2-4 weeks prior to the end of the liability period to release the contract retention.

- Operations and Maintenance Documentation.  Upon completion of the works the contractor shall forward all manufacturers’ details relating to equipment/materials used to the Authority for inclusion into the O&M Manual/H&S File.  Refer also to CDM 2015 & appropriate ACOP, this documentation less ‘As Built Drawings’ is to be made available at the Pre-Board of Officers not less than 10 days before the due project handover date.  A full list of snagging items shall be produced and presented to the Authority with a rectification programme at this very same board.

Health and Safety File

- Upon project completion the H&S file shall be presented to the Authority before the Board of Officers is convened and in compliance with (CDM 2015) & appropriate ACOP.

- Presentation of Health and Safety File.  The contractor is to provide the authority with three copies of the H&S File.  The Manual is to be contained in a series of A4 size, plastic covered, loose leaf, four ring binders with hard covers, each indexed, divided and appropriately cover titled.  Selected drawings needed to illustrate or locate items mentioned in the Manual, where larger than A4, are to be folded and accommodated in the binders so that they may be unfolded without being detached from the rings.  The main set(s) of as-built drawings will form Annex(es) to the Manual.

- The Health and Safety File.  The contractor shall be required to complete the Project Health and Safety File on completion of the works, three copies of which will be provided to the Authority at handover. Advice can be sought from the Authority if required.  The H&S File provides information required for future construction work, which includes cleaning, maintenance, alterations, refurbishment, and demolition.  The Manual is to consist of the following parts, sub-sectioned as appropriate.

  - Section 1: H&S.  The contractor is to provide a description of the site and the buildings thereon. This is to include details of construction methods and materials, which may present significant residual hazards in the future.

  - Section 2: Certificates.  The contractor is to provide a copy of all Test Certificates (including but not limited to electrical circuit tests, start and commissioning tests) for the installations and plant, equipment, valves, etc, used in the installations. Warranty Certificates and guarantees are also to be included in this section.

  - Section 3: As-built Drawings.  The contractor is to provide as-built drawings recording details of all construction, electrical and mechanical work. A fire strategy for the site should also be included with drawings showing emergency escape routes, location of emergency and firefighting systems, services shut-off valves, switches, etc.

  - Section 4: Operation & Maintenance (O&M) Schedules.  The contractor is to provide recommendations as to the preventative maintenance, frequency, and procedures to be adopted to ensure the most efficient operation of the systems. Manufacturer’s O&M schedules are to be included. Diagrammatic drawings of each system indicating principal items of plant, equipment, and valves are also to be included.

  - Section 5: O&M Manuals.  The contractor is to provide copies of manufacturers’ current literature for all products for which the proprietary brand has been chosen by the contractor, including COSHH data sheets, catalogue list numbers and manufacturers recommendations for cleaning and maintenance.  The mechanical and electrical systems section shall contain a full description of each of the systems installed, written to ensure that the client fully understands the scope and facilities provided.  All manufacturers technical literature for items of plant and equipment, assembled specifically for the project, including detailed drawings, electrical circuit details and operating and maintenance instructions are to be included.

- Draft Health and Safety File.  A complete H&S file in draft must be submitted by the contractor, not less than 4 weeks before the date for submission of the final copies of the Manual.  This is to be amended in the light of any comments and resubmitted to the authority.  Do not proceed with production of the final copies of the Manual until authorised to do so by the authority.

Annex E to

CONTRACT/KEN/GE/2303/BK/3/SpecDated 8 Mar 24

Drawings

            - DIO/KEN/NYA/GE/EXT/C/001-GE Department extension floor plan.

            - DIO/KEN/NYA/GE/EXT/E/001-GE Department extension electrical layout.

            - DIO/KEN/NYA/GE/EXT/E/002-GE Department extension fire alarm layout.

            - DIO/KEN/NYA/GE/EXT/E/003-GE Department extension PA layout, dado trunking, socket outlets & external lights.

            - DIO/KEN/NYA/GE/EXT/E/004-GE Department extension ventilation layout.

            - DIO/KEN/NYA/GE/EXT/E/005-GE Department extension

            - K19000-DIO-4000-LT-AsBuilt-Foundation ground floor extension

            - K19000-DIO-4003-LT-AsBuilt-Cross-section and Details

British material standard for Carbon Steel Bars for Concrete Reinforcement for strengthening application.

Manual of Contract Documents for Highway Works, Volume 1

Manual of Contract Documents for Highway Works, Volume 1

Requirements for Electrical Installations (IEE Wiring Regulations)

Specification for Steel Conduit and Fittings with Metric Thread of ISO Form for Electrical Installations - Part 1: Steel Conduit, Bends and Couplers

Non-Metallic Conduit Fittings for Electrical Installations - Part 1: Specification for Fittings and Components of Insulating Material

Conduit systems for cable management. General requirements (+A1:2019)

Cable glands for electrical installations

Specification for Binding and identification sleeves for use on electric cables and wires.

Cable trunking systems and cable ducting systems for electrical installations - Part 1: General requirements

Metallic coatings — Hot dip galvanized coatings on ferrous materials — Gravimetric determination of the mass per unit area

Hot dip galvanized coatings on fabricated iron and steel articles — Specifications and test methods.

Specifies requirements and tests for cable tray systems and cable ladder systems intended for the support and accommodation of cables and possibly other electrical equipment in electrical and/or communication systems installations

Electrical wiring regulation 2018

Construction (Design & Management) Regulations 2015 (CDM2015).

ACOP-Approved Code of Practice

British Standard

Euro Norm

Control Of Substance Hazardous to Health.