## Sheet1
Number | Received From | Received Date | Question | Reply Date | Answer
The Authority has taken the decision to extend the tendering period. The revised Tender Return Date is now 10:00 12 January 2021.
Site Visit - Presentation
l |  | 2020-12-16 | Do you expect the board shown in Annex A of the Invitation to Tender to be reconfigured? | 2020-12-16 | No. This is used to replicate what you would find onboard a ship for training purposes. The layout/configuration is to remain the same, but the pipework is to be replaced.
2 |  | 2020-12-16 | Do you need the guages shown in Annex A of the Invitation to Tender to be recalibrated following the works? | 2020-12-16 | Yes as all work must conform to relevant regulations.
3 |  | 2020-12-16 | Does the HP air bottle need testing/calibrating? | 2020-12-16 | Yes. It is out-of-date for all certification and will need to be re-certified.
4 |  | 2020-12-16 | Do you need to maintain the same configuation shown in Annex D of the Invitation to Tender? | 2020-12-16 | There is no requirement for a particular configuration as this is not representative of anything onboard a ship.
5 |  | 2020-12-16 | Do you absolutely require the double block and bleed as shown in Annex F of the Invitation to Tender? | 2020-12-16 | Yes. Double block and bleed valve arrangements must be fitted in positions indicated in Annex F to allow the training units to isolate the system in accordance with the safe systems of work on site.
Site Visit - Room J8
6 |  | 2020-12-16 | Has this room been checked for asbestos? | 2020-12-16 | There is no asbestos in the rooms in which pipework will be replaced in support of this project.
7 |  | 2020-12-16 | Do you know the distances required for the pipework? | 2020-12-16 | No.
8 |  | 2020-12-16 | Would there be an option to use flaring? | 2020-12-16 | Yes
9 |  | 2020-12-16 | Does the pipework need to be fire-stopped between classrooms? | 2020-12-16 | The contractor must ensure that any existing fire protection is maintained and that newly installed pipework is fire rated accordingly.
Site Visit - Room H8
10 |  | 2020-12-16 | Do you need the redundant pipes removed as well? | 2020-12-16 | The pipework can be capped off at the point it enters the room. The remaining piepwork that passes through the wall to H4 may remain in place and does not need to be removed as part of this project.
15 |  | 2020-12-16 | Will the HP air bottle in here be moved? | 2020-12-16 | Yes, and its bracket and associated control valves. It will re-purposed to room K5C lab 2. The bottle in K5C lab 1 will remain where it is.
17 |  | 2020-12-16 | Will the written scheme for this need to be modified after completion? | 2020-12-16 | The contractor will need to pass the details of any changes to Maxura who maintain the WSE. The Project Manager should be included in any correspondance with Maxura.
18 |  | 2020-12-16 | Can you clarify who is responsible for the written scheme? | 2020-12-16 | Maxura is responsible for the WSE. Warrant Officer Peake in the Weapon Engineering Training Unit is the custodian and must be informed of any changes. Mr Peake should be informed via the Project Manager.
Site Visit - Room K5B
19 |  | 2020-12-16 | Where are the failures in the system currently? | 2020-12-16 | They are throughout and frequent.
20 |  | 2020-12-16 | Does the pipework go directly to K1? | 2020-12-16 | The pipework passes from room K5C directly to K1.
21 |  | 2020-12-16 | Is the job here to connect the HP air bottle? | 2020-12-16 | The HP air bottle from room H8 should be transferred to this compartment and fitted into the system. The bracket and control panel should also be re-purposed to here. The bottle should be connected to the HP air supply, and be fitted with a drain valve that discharges into the adjacent floor trench.
22 |  | 2020-12-16 | Do you want to use the same panel configuration in this room also? Can the panel be replaced? | 2020-12-16 | The panel could be replaced, however the exact configuration needs to be maintained.
23 |  | 2020-12-16 | Do you envisage the panels being taken offsite? | 2020-12-16 | They could be, but disruption to training must be limited. Any disruption to training must be approved in advance by the PM.
24 |  | 2020-12-16 | Would weekend/out-of-hours working be possible to minimise disruption? | 2020-12-16 | This may be possible, but would need authorisation. It is unknown whether this would be granted.
Other
25 |  | 2020-12-17 | In the provisioned budget, shall the pressure gauges be calibrated/certified, as they normally need to be checked annually? | 2020-12-18 | The pressure gauges should be calibrated/certified within the cost of the advertised budget.
26 |  | 2020-12-17 | In the specifications it was mentioned to use "Swagelok, eg.", therefore my question is it required to use compression fittings, or would a flaring system be acceptable as well? The reason for asking is that if you currently face problems with leakages, the safest way would be to use a flared connection as it removes the possibility of a leaking/damaged compression ring. | 2020-12-18 | Compression fittings are not necessarily required. A flared connection is suitable. The key requirement is increased reliability of the system within the available funding profile.
27 |  | 2020-12-17 | Also mentioned is "utilise Hale Hamilton supplied component service kits". Will the kits be provided by the MoD or are we (the supplier) requested to purchase them? | 2020-12-18 | The Hale Hamilton service kits must be provided by the contractor and should be included in the overall project cost.
28 |  | 2020-12-17 | Further the requirement to "Recertify HP air storage cylinder" as well as if you would like to calibrate the pressure gauges; in case any of them fail the tests, they would have to be replaced with new ones. Would the procurement of new gauges/cylinder be included in the tender price or would that be an additional cost? | 2020-12-18 | The potential replacement of the air storage cylinder and/or pressure gauges is not in scope for this requirement.