STATEMENT OF REQUIREMENT

SUPPLY INSTALLATION COMMISSION AND MAINTENANCE OF LOAD BANK AND SWITCH GEAR FOR DIESEL GENERATOR AT HMS SULTAN

Introduction

- This Statement of Requirement (SOR) stipulates Defence School of Marine Engineering’s (DSMarE’s) requirements for a load bank.

- This SOR addresses the requirement to replace the existing load bank and switchgear to support Marine Engineer (ME) operator and maintainer training in DSMarE so that military personnel are effectively trained in line with thed Training Requirement Authority (TRA) mandated Training Objectives (TOs) contained in the course specific Formal Training Statement (FTS) as defined in the Role Performance Statement (RPS). The overall purpose of the SOR is to ensure that, in accordance with TRA direction, a load bank is procured to support effective delivery of maintainer/operator training is procured.

Background

- At present DSMarE utilises a custom made load bank of 1960s vintage that supplies load to a Paxman Valenta RPA200 Generator set up similar to that employed on the T23 Frigate. Load is increased in incremental steps by manually closing individual breakers locally at the load bank.  The remaining running Diesel engines located in Watt hanger (Deltic and Paxman Ventura) have their loading supplied via a water brake arrangement that has no requirement for inputting into the load bank.

- Both the DELTIC and Paxman Ventura series of engines are awaiting removal to allow the installation of a MTU 12V 4000M53B and a Wartsila 4L20 engines to satisfy the new training requirements of the T23 PGMU and QEC projects respectively.  The relevant project’s intentions are to supply both these engines to DSMarE in a diesel generator configuration (the Wartsila is already on contract and the MTU is being delivered imminently).

Scope

- The requirement includes the design, construction, delivery, installation and commissioning of a load bank and associated switchgear to support Instructor Led Training (ILT) in Watt Hanger at DSMarE. As well as initial operator training to DSMarE instructors, warranty for the load bank, maintenance and a programme of maintenance for the load bank.

- The load bank and switchgear are required to provide 100% load to 3 diesel generator sets rated at a maximum of 1750kVA and operating at 600V and 440V.

Priorities

- The requirements are listed in priority order at Table 1.

Deliverable Dates

- The solution must be able to be at initial operating capability (IOC) no later than (NLT) the date specified within the Schedule of of Requirement and full operating capability (FOC) within 2 weeks following installation. IOC and FOC are defined as:

  - IOC:	The solution is delivered and installed waiting commissioning.

  - FOC:	The solution is commissioned and ready for instruction to commence.

Safety and Environmental Provisions

- When on site the Contractor shall comply with on-site MOD Safety, Health and Environmental protection regulations.

Outline of Deliverables

- The deliverables shall consist of the following items:

  - Load bank and switchgear installed and commissioned to the standards defined in Paragraph 11.

  - Initial operator training to DSMarE instructors as defined in Paragraph 12.

  - Installation drawing in electronic format detailing connectivity of the load bank & switch gear installation.

  - 2 year maintenance of load bank including a programme of maintenance as defined at Paragraph 12.

Specification

- The load bank is to comply with the specifications as detailed in Table 1 below.

Table 1 – Specification of Load Bank

| Ref | Specification | Additional Information |
| --- | --- | --- |
| 1 | The solution must be able to connect to both 600/440v supplies | 1 genset produces 600V whilst the other 2 have 440V outputs |
| 2 | Be able to handle 1750 KVA at 0.8 Pf load with a 10% fault over load capacity | The 600v genset has a max output of 1750KVa whilst the others are rated at 1250KVA |
| 3 | Switchboard to be rated at 600/ 440V 50/60Hz, 3 phase with a 3 wire, busbar rated at 2000A. | Switchboard can be rated at 440V should a step down transformer be utilised in the final solution |
| 4 | Switchgear must be able to withstand a minimum short circuit of 40kA @ 600V | Actual fault capacity will be dependent on the final solution. |
| 5 | Switchgear must be compatible with the Automatic Voltage Regulators (AVR) fitted to the Wartsila and MTU gensets | The Wartsila genset has the Basler DECS 100 AVR fitted. The MTU has the Basler DECS-250 AVR fitted. |
| 6 | Switchgear must be configured to enable loading in steps of 1kW with a range of metering and monitoring options | The enclosed quotation utilises a Crestchic Eclipse software package |
| 7 | The switchboard is to be of mild steel, modular construction and be free standing | Item to be located internally in Watt Hanger |
| 8 | The load bank itself must be housed in a steel container suitable for outdoor use, complete with keypad and 50 meters of control cable. | A suitable location is located directly outside the facility with suitable underground channelling for the cabling. |
| 9 | Breaker operation can be either local (at the switchgear) or remote | Switchgear will be housed internally in Watt Hanger |
| 10 | Digital display will be required providing indication of current, voltage, power factor, active power and reactive power ,breaker status indication and operation pushbutton | A digital display is preferable but other options may be suitable |
| 11 | Equipment to be compliant with BS EN 610822006, IEC 60617-2:1996, BS EN 60529-1992. EC Council directive 2006/95/EC |  |
| 12 | Contractual standards to be compliant with the following; AQAP 2120 edition 3 (NATO Quality Assurance Requirements for Production) AQAP 2210 edition 1 (NATO Supplementary Software Quality Assurance Requirement) DEFSTAN 05-57 issue 6 (Configuration Management of Defence Materiel) DEFSTAN 05-61 part 1 issue 6 (Concessions) DEFSTAN 05-61 Part 4 Issue 3 and Amendment 1 28/01/11 (Contractor Working Parties) DEFSTAN 05-135 Issue 1 Avoidance of Counterfeit Material. ISO 9001 Accreditation NICEIC (approval and registration/certification) | Following contract award the successful supplier may undertake a visit and survey the location to where the equipment to be installed. |
| 13 | The acceptance criteria will be a demonstration that the installation can provide load in 1% steps to 1750 KVa at 600 V and remain at 100% for 2 hours and reduce in 1% steps to zero The installation must also provide load in 1% steps to 1250 KVa at 440 V and remain at 100% for 2 hours and reduce in 1% steps to zero | A certificate of conformity will be required as a condition of acceptance |

Other Deliverables

- In addition to the load bank the other following outputs are to be delivered as detailed at Table 2 below.

Table 2 - Other Deliverables

| Ref | Requirement | Additional Information |
| --- | --- | --- |
| 1 | Manufacturer to supply significant operator training to DSMarE instructors to facilitate safe and efficient operation of the equipment | 1/2 Day would be considered sufficient |
| 2 | Manufacturer’s warranty for load bank | 1 year warranty |
| 3 | Maintenance of load bank including programme of maintenance | 2 years of maintenance of the load bank |

This is exactly the same fit as found on serving platforms (post-PGMU T23).