|  | ESTATES |
| --- | --- |

# OPERATION & MAINTENANCE MANUAL

| Project: | New Bransfield House Solar Thermal System |
| --- | --- |
| Location: | Rothera |
| Issue Date: | 1 Jul 2020 |
| Revision: | 1 |
| Author(s): | Dave Blaylock, Matt Meaden, Tom Brennan, Matt Ivory |

Contents

OPERATION & MAINTENANCE MANUAL	1

Section 1 – Specification	2

Section 2 – System Description	2

Section 3 – Plant & Equipment Inventory	4

Section 4 – Maintenance & Operational Requirements	4

Volume 1 – Maintenance & Operational Requirements – Structural	4

Volume 2 – Maintenance & Operational Requirements – MEchanical	4

Volume 3 – Maintenance & Operational Requirements – Electrical	4

Section 5 – Manufacturer’s literature	4

Section 6 – As-Built Drawings	4

6.1 – Architectural details	4

6.2 - Structural details	5

6.3 - Mechanical and electrical system details	5

6.4 - Specialist systems (including fire alarm, emergency lighting, access control, intruder alarms, CCTV etc.)	5

6.5 - External works details	5

6.6 - Services details	5

Section 7 – Commissioning Results	5

Section 8 – Other Test Sheets & Certificates	5

Section 9 – Warranties & Spares	5

Section 10 – Health & Safety & Emergency Procedures	5

Section 11 – Environmental Information	5

# Section 1 – Specification

| Solar Collectors | 8 in no. Veissmann Vitosol 300-TM vacuum tube collector (3.03 m2), 24 tubes per collector |
| --- | --- |
| Accumulator pre-charge pressure | 2.65 Bar |
| System operating pressure (Gauge in NBH Plant Room) | 2.85 Bar |
| Max system pressure (Relief valve operating pressure)) | 6 Bar |
| System volume | Approx. 180 litres |
| System flow rate (measured at main flow meter between circulation pumps and solar arrays) | 600 litres/hour |
| Gross solar collector area | 36.96 m2 |
| Solar collector tube angle correction | The North side of NBH is angled approximately 15° off due North, therefore the solar tubes are installed with a 15° angle of correction. In reality this means that the tubes are installed angled towards the West end of NBH by 15° to achieve maximum efficiency. |
| Max stagnation Temperature *The stagnation temperature is the maximum temperature that the collector can reach during insolation (solar energy absorbtion) of 1000 W/m2. If no heat is drawn from the collector, it will heat up until it reaches the stagnation temperature. In this state, the thermal losses are of the same magnitude as the radiation absorbed. | 150°C |

# Section 2 – System Description

Commissioned in 2020, the solar thermal system installed in New Bransfield House consists of 2 separate solar arrays mounted on the North façade of the building. Each array includes 4 in no. Veissmann Vitosol 300-TM headers/manifolds that are plumbed together in series. Each solar array has a dedicated pressure relief valve (6 bar) and temperature sensor for monitoring output temperatures.

The solar arrays utilise vacuum tube collector technology based on the heat pipe principle, with ThermProtect automatic temperature-dependent shutdown for high operational reliability. Each glass collector tube contains a closed circuit heat pipe system, which absorbs solar thermal energy and heats up the solar system glycol via a copper heat exchanger within each Vitosol header/manifold. The connection between the glass collector tubes and manifolds is a dry copper to copper heat transfer contact, therefore tubes can be removed/replaced without isolating/draining the wet glycol system.

Flow/return pipework for the panels is plumbed via the NBH undercroft to the ground floor plant room and rises adjacent to the hot water/BMS equipment skid. Glycol is circulated via 2 in no. pumps (duty/standby) located on the hot water skid.

During normal operation a selected circulation pump will automatically run when the solar array output temperature reaches set point and flow will be regulated between the HWS cylinders and the AHU’s. This control is based on proximity to hot water and air temperature set points. For example, if HWS cylinder 1 is 10 degrees less than set point, HWS cylinder 2 is at set point and both AHU’s are 5 degrees less than set point, cylinder 2 divert valve will be closed, cylinder 1 will be 100% open, and the AHU divert valve will also be 100% open, with the individual AHU coil control valves splitting the duty between AHU1 and AHU2.

If the solar gains are minimal (i.e. low sun penetration etc) the BMS will report a low header temperature, the solar circulation pumps will be stopped and will only run on a routine exercise regime to prevent seizing etc.

Control for the solar thermal system is provided by the common NBH Schneider BMS architecture. The schedule below outlines the various inputs and outputs used to monitor and control the system:

Inputs/Monitoring:

NBH Ground Floor Plant Room Main BMS Panel:

- 24VAC/10VDC Solar panel header temperatures

- 0-10VDC HWS Cylinder 1 Temperature

- 0-10VDC HWS Cylinder 2 Temperature

- 0-10VDC Solar Panel Array 1 Temperature

- 0-10VDC Solar Panel Array 2 Temperature

- 0-10VDC HWS Cylinder 1 Temperature

- 0-10VDC HWS Cylinder 2 Temperature

- 400VAC Circulation Pumps 1 & 2 Run Indication

AHU BMS Panel (Located in NBH Loft Plant Room):

- 0-10VDC AHU 1 Solar Coil Temperature

- 0-10VDC AHU 2 Solar Coil Temperature

Dedicated Solar BMS Panel (Located in NBH Ground Floor Plant Room):

- BACNET Digital (from Kamstrup Meter) Solar Panels Flow Rate signal

- BACNET Digital (from Kamstrup Meter) Solar Panels Flow Temp

- BACNET Digital (from Kamstrup Meter) Solar Panels Return Temp

- BACNET Digital (from Kamstrup Meter) HWS System Flow Rate signal

- BACNET Digital (from Kamstrup Meter) HWS System Flow Temp

- BACNET Digital (from Kamstrup Meter) HWS System Return Temp

- BACNET Digital (from Kamstrup Meter) AHU No1&2 Flow Rate signal

- BACNET Digital (from Kamstrup Meter) AHU No1&2 Flow Temp

- BACNET Digital (from Kamstrup Meter) No1&2 Return Temp

Outputs/Control:

NBH Ground Floor Plant Room Main BMS Panel:

- 400VAC Circulation Pumps 1 & 2 Start/Stop Control

AHU BMS Panel (Located in NBH Loft Plant Room):

- 0-10VDC AHU 1 Solar Coil Flow Control Valve

- 0-10VDC AHU 2 Solar Coil Flow Control Valve

Dedicated Solar BMS Panel (Located in NBH Ground Floor Plant Room):

- 0-10VDC HWS Cylinder No.1 Solar Heating Valve

- 0-10VDC HWS Cylinder No.2 Solar Heating Valve

- 0-10VDC HWS Cylinders/AHU Heating Coils Solar Heating Diverting Valve

The dedicated solar BMS panel is networked by piggybacking from the main NBH ground floor plant room BMS panel panel’s BacNet daisy chain. The new panel also takes a 230v supply from the main BMS panel via a 20A switched spur and supplies the B3920 controller, a 24VAC and a 5VDC power supply.

In addition to the 0-10VDC reference connections listed previously in this section, the Solar System Divert valve and HWS cylinder 1 & 2 divert valves are supplies with 24VAC supplies from the solar BMS panel 24VAC rail. The 3 in no. Kamstrup heat meters are also supplied with 24VAC from the solar BMS panel.

Via contactors, the original BMS system takes control of the two 3 phase circulation pumps in a duty/standby arrangement. Duty pump switchover is pre-programmed to automatically changeover at midnight every Sunday.

One difference to the usual 0-10VDC sensor arrangement is the solar header temp sensors (located inside the end manifold of each array). These are a high range pt1000 sensor, which reports back to a 0-10VDC converter. The converter itself takes a 24VAC supply from the original BMS and ultimately the pt1000 signal is converted to a 0-10VDC range for the BMS to read.

# Section 3 – Plant & Equipment Inventory

# Section 4 – Maintenance & Operational Requirements

## Volume 1 – Maintenance & Operational Requirements – Structural

## Volume 2 – Maintenance & Operational Requirements – MEchanical

Prior to conducting any maintenance to the solar system, refer to Safety and Environmental information within Section 10 & 11 of this document.

| Maintenance Operation | Interval | Notes |
| --- | --- | --- |
| Visual Inspection of pressure relief valves (located in under croft) | 12 months | Visual inspection to ensure valves are in serviceable material state |
| Replacement of all pressure relief valves | 5 years |  |
| Visual Inspection of Expansion Vessel | 12 months | Visual inspection of expansion vessel to check for weaknesses, signs of corrosion. Vessel to be replaced as required |
| Clean system strainer (located in NBH ground floor plant room between hot water skid and expansion vessel) | 6 months |  |
| Check system pressures | 6 months | Ensure pressures remain in accordance with commissioning values outlined in Section 7 of O&M Manual |
| Check Glycol concentration and frost protection values (refractometer test) | 12 months |  |
| Check pressure relief valve blow off line collection vessels. (2 in no. located underneath NBH, in vicinity of each panel) | 3 months | Ensure suitable collection vessel is in place and that sufficient capacity is available to prevent environmental incident in the event of pressure release. Investigate any evidence of recent pressure release valve operation and report to Rothera FE |

## Volume 3 – Maintenance & Operational Requirements – Electrical

# Section 5 – Manufacturer’s literature

| NBH Solar O&M Annex A | Vitosol 300TM Service Instructions |
| --- | --- |
| NBH Solar O&M Annex B | Vitosol Technical Guide |

# Section 6 – As-Built Drawings

## 6.1 – Architectural details

## 6.2 - Structural details

## 6.3 - Mechanical and electrical system details

Mechanical and Electrical system schematics are provided in the following drawings:

| Drawing Number | Description |
| --- | --- |
| BAS ESTATES-PROJ202001-DWG-MS-01 | Mechanical Schematic |
| BAS ESTATES-PROJ202001-DWG-ES-01 | Electrical Schematic |

## 6.4 - Specialist systems (including fire alarm, emergency lighting, access control, intruder alarms, CCTV etc.)

## 6.5 - External works details

## 6.6 - Services details

# Section 7 – Commissioning Results

# Section 8 – Other Test Sheets & Certificates

# Section 9 – Warranties & Spares

# Section 10 – Health & Safety information & Emergency Procedures

Temperatures within the solar system can reach a maximum 150°C.

The typical working pressure of the system is between 2.5 – 3 Bar, however pressures can rise to 6 Bar before the safety pressure relief valves will operate. This combined with high temperatures represents a significant hazard.

Extreme caution should be taken when working on any part of the system and appropriate PPE should be worn, including eye protection and heat/fluid resistant gloves until it has been confirmed that the system has been de-pressurised and cooled back to a safe working temperature.

Particular attention should be paid to how external conditions will affect system pressures and temperatures. Ideally the system should only be worked on when solar gains are at a minimum. If this is unachievable, then the solar panel arrays be suitably covered to prevent solar energy transfer, or the collector tubes should be removed. The system should then be allowed to cool back sufficiently prior to de-pressuring.

The solar panel arrays should never be isolated during periods of high solar gain. This may lead to system over-heating/over pressurization, system damage and potential injury to persons in the vicinity.

The solar system is filled with TYFOCOR© G-L-S ready-mixed propylene glycol. This substance is hazardous to health and appropriate precautions must be taken to ensure safe handling of this substance, including fluid resistant gloves and eye protection. The product safety data sheet should be consulted for further information.

# Section 11 – Environmental Information

The solar system is filled with TYFOCOR© G-L-S ready-mixed propylene glycol. This substance is hazardous to the natural environment and suitable precautions must be taken to prevent accidental release into the environment. Any spillages must be immediately dealt with and waste fluid must be appropriately bottled for proper disposal. Further details can be found within the product safety data sheet.