SPECIFICATION FOR THE ANNUAL SERVICE, REPAIR AND SUPPLY OF THE FIRE FIGHTING EQUIPMENT

January 2020

SPECIFICATION FOR THE ANNUAL SERVICE, REPAIR AND SUPPLY OF THE FIRE FIGHTING EQUIPMENT

GENERAL CONDITIONS AND PRELIMINARIES

1.	DEFINITION		For the purpose of the Contract the "Employer" shall mean:

OF PARTIES

Derbyshire Community Health Services NHSFT

Ash Green

Ashgate Road

Old Brampton

Chesterfield

S42 7JE

and the Supervising Officer shall mean:

Paul Aveston/Simon Fairchild

Fire Officers

Estates Department

Ash Green

Ashgate Road

Old Brampton

Chesterfield

S42 7JE

Telephone No:  01629 817917

and the Contract Administrator shall mean:

Mrs Emma Morten

Senior Procurement Officer

Estates Department

Ash Green

Ashgate Road

Old Brampton

Chesterfield

S42 7JE

Telephone No:  01629 817964

or their designated representative.

The Contract shall be formed on the basis of the NHS Conditions of Contract for the Provision of Services     and the Special Conditions contained within the specification.

2.	ACCESS TO			Shall be via the premise roadway system.

SITE				Following the unloading of materials, etc.  The 							Contractor's vehicle must be parked in the visitor’s car 					park.

Not all sites are permanently staffed, access must 						therefore be pre-arranged.

3.	DESCRIPTION	Carry out the annual inspection and service of fire          fighting equipment as per the attached schedule (Includes the supply of photoluminescent fire safety signs).

4.	CONTRACT			All maintenance and repairs will be carried out in

REQUIREMENTS		accordance with the original equipment manufacturer's

recommendations.  There shall be one service visit 						per annum, each service visit to be strictly carried out 						within the correct service date.  Replacement 							consumables and parts must be supplied and fitted in 						accordance with the original manufacturer 							specifications.

All services, parts and consumables supplied against 						this agreement shall comply with relevant legislation, 						British	Standards and Health & Safety requirements.

Response time shall be within a range of 4 to 12 hours 					depending on criticality and consultation with the 						Supervising Officer.

5. 	VISITS TO SITES		The Contractor may visit the sites to ascertain the full 						extent of the works prior to submitting his tender, as 						no claims in respect of want of knowledge will be 						entertained.

Appointments to visit the sites must be made by prior 						arrangement with the Supervising Officer.

6.	FIXED PRICE		Contractors should quote on a fixed price basis for all

QUOTATION			labour, transport and materials required for the works 						which is to remain fixed for a period of 48 months from 					receipt of official order any additional costs incurred 						through inflation shall be agreed by all parties.

The Contract is for a three year period, with an option to extend a further year, subject to annual review and satisfactory performance on the part of the Contractor.

Payment will be made following submission of invoice and duly completed service sheets on completion of the works at the end of each service week's time period.

The Contractor is also required to submit an itemised 			priced schedule with his quotation detailing estimated 			time allocated for each task.

The Supervising Officer may, without invalidating the 			Contract, order an addition to and omission from, or 			other change in the works or the period in which they 			are carried out, and any such instruction shall be 			valued by the	Supervising Officers on a fair and 			reasonable basis using relevant prices in the priced 			specification or other agreed rate between themselves 		and the Contractor.

7.	WORKMANSHIP,		A high standard of workmanship is required and the

MATERIALS AND		Contractor's staff will be expected to re-attend on any

EQUIPMENT			areas of work that are found to be not satisfactory.

The Contractor is required to immediately report to the 					Supervising Officer any remedial work recognised to 						be urgent.

All Contractors’ staff working on site must wear clean 						overalls used solely for the purpose of this contract.

The Contractor shall provide all his own equipment 						and materials. The use of DCHS materials and 							equipment shall not be permitted.

All equipment and materials are to be sanctioned by 						the Supervising Officer.

Copies of Calibration/Repair/Service Certificates are 						to be passed to the Supervising Officer.

8.	STATUTORY		The Contractor is to ensure compliance with the

REQUIREMENTS		following whilst carrying out the works.

Health & Safety at Work Act 1974

BS 5306 Part 1 – Code of practice for hydrant systems, hose reels and foam inlets.

BS 5306 Part 3 – Fire extinguishing installations and equipment on premises.

BS EN 1869 - Relevant for light duty fire blankets.

BS EN 671 -   Relevant for hose equipment.

BS EN 3 New British and European standard, that all fire extinguishers for use in European countries must have 95 per cent of body painted red.

Quality Assurance System to BS EN ISO 9002.

To undertake all pressure testing of fire extinguishers. At the intervals designated in the British Standard. Montreal protocol and revisions regarding the cessation of use of halon fire extinguishers. Comply with all relevant environmental legislation, regulations and other public body requirements.

The contractor shall be required to produce COSHH data sheets for all materials used prior to commencement of contract.

9.	WORKING 			The Contractor will only be allowed access to carry out

ARRANGEMENTS		the works Monday to Friday between the hours of 						0800 and 1700 excluding Bank Holidays.

The times allocated to the works will be agreed with 						the Supervising Officer.

The Contractors are advised that they may be working 					in an operational area and must therefore allow for 						any inconvenience and disruption to the works, which 						may occur.

10.	WORK CONTENT		As per Technical Specification and Equipment 							Schedule.

11.	PROGRAMME		The successful Contractor in conjunction with the 						Supervising Officer shall produce an expected work 						programme for the contract period, which must be 						strictly adhered to.

The time performance will be of the essence.

Training –

- The Contractor’s staff shall hold certificates of competence in the categories of work detailed in the specification and schedule.

- The Contractor’s staff shall be instructed not to attempt to exceed the scope of their training.

- The Contractor shall provide details of the training programme their operatives undergo.

- Only those staff identified to and audited by the Supervising Officer may carry out the works.

12.	MONITORING 		On completion of the work the service/repair sheets,

OF THE WORKS	plus additional paperwork as may be required for a particular appliance type shall be forwarded to the Supervising Officer without delay preferably electronically

.13.	SECURITY	The Contractor is to ensure that security of the premises and equipment is maintained at all times.  The Contractor is not to leave site until arrangements have been made to lock up the premises.

Contractor's staff when on site must wear, at all times, 					ID badges complete with photograph and company 						name.  All staff shall report to the reception for signing 					in and out of the visitors' book on each visit to site.

The Contractor shall remove any of its staff from the 						premises where the Trust’s Supervising Officer 						requests on grounds of efficiency or public interest.

14.	SCAFFOLDING AND	The Contractor shall allow for the provision of all safe

ACCESS EQUIPMENT	access equipment needed for the works.

15.	USE OF POWER 		Only 110-volt power tools shall be used.  The

TOOLS			transformer shall be sited adjacent to the mains 230-							volt power socket with a cable length of 2 metres 							maximum.  Only 110-volt extension leads shall be 							used.  The Contractor shall make available to the 							Supervising Officer test records for all electrical 							equipment used on site.  The test period shall be

no greater than 6 months for each item including all 							110 volt extension leads.

16.	CLEANLINESS OF		All Contractors’ materials and equipment are to be 		SITE				removed from site at the end of each working day.

17.	FIRE PRECAUTIONS	Before any works are carried out, the Contractor is to 						discuss his proposals with the Supervising Officer, to 						ensure that the extent of any fire hazards in the work 						are known fully to both the Contractor and the Trust.  						The Contractor is to draw the attention of all his 						workmen to the special vulnerability of hospital 							patients in the event of fire, and the dangers involved 						in the careless disposal of matches, cigarettes and 						tobacco ash, must be passed on to them.

Smoking is not permitted on Trust premises and the 						Contractors workmen are required to strictly conform 						to all "NO SMOKING" rules applicable to the site.

The Contractor shall take all reasonable precautions 						to avoid the outbreak of fire on site of the works and 						the adjacent buildings.

The Contractor shall allow facilities for the Trust’s Fire 					Safety Adviser to inspect the site and buildings to 						ensure that the fire precautions are adequate and that 					the Contractor shall comply with any reasonable 						request that the Fire Officer may make in this 							connection.

The Contractor shall allow for all necessary safety 						precautions when using petrol, diesel, acetylene, 						propane or similar gases. In accordance with the 						highly Flammable Liquids and liquefied Petroleum Gas 					Regulations 1972 and any relevant Codes of Practice.

The Contractor shall be responsible for ensuring that 						all his sub-contractors workmen employed on any 						works within 	the premises shall know the means of 						giving alarm in the case of fire which apply to that part 					of the premises in which they are working:

That on discovery of a fire, or suspicion of fire, the 					alarm is to be given immediately, in the manner 						prescribed for those premises.

He will also be responsible for ensuring that the above 					mentioned workmen know the location of the fire 						fighting equipment provided in that part of the 							premises in which they are working.

When work necessitates the use of high temperature 						sources of ignition, a "hot work permit" shall be 							obtained from the Supervising Officer, and the 							Contractor shall provide a suitable portable fire 							extinguisher, which shall be kept readily available.

Welding and similar operations shall not be executed 						until all surrounding inflammable materials have been 						adequately protected and the "hot work permit" has 						been obtained.

The Contractor shall provide a suitable portable fire 						extinguisher, which shall be kept readily available.

All hot work shall cease one hour before the end of the 					day’s work and a final check made by the Contractor 						of his areas of work before leaving site.

NOTES

1.	The occupants of the premises must be notified of any works.

2.	Access shall be agreed with the Supervising Officer.  It shall be the Contractor’s 	responsibility to ensure the boiler house and any ancillary buildings and access 	doors are securely locked before leaving the premise.

3.	Aborted visits i.e. sickness, access problems etc must be reported immediately to 	the supervising officer and a return visit made within seven working days.

4.	On visiting site, any changes or additions to the equipment listed in the 	equipment schedule shall be notified to the Supervising Office without delay.

5.	Work extra to the contract must be authorised by the supervising officer and a 	day work sheet submitted for approval.

6.	Great care must be taken to ensure all equipment is properly reinstated after 	completion of testing.

7.	If an appliance is found to be dangerous or with potentially dangerous faults, the Supervising Officer must be contacted immediately for a decision on repair or removal.

8.	Report all appliance faults to be Supervising Officer at the Derbyshire Community              Health Services NHSFT, Estates Department on (01629) 817917.

TECHNICAL SPECIFICATION

TECHNICAL SPECIFICATION

Fire Blankets

Inspection of a fire blanket must consist of checking that the blanket is in position, and identifying that it complies with BS EN 1869. That it is clean and serviceable also can be easily removed from the container and visually examined for signs of use or damage. Re-fold and replace blanket in container. Replacement fire blankets shall be replaced subject to express agreement from the Supervising Officer.

Hose Reels

Hose reels are to be inspected and tested in accordance with BS 5306 
Part 1, plus adjustment and lubrication where necessary. Examine hose reel to ensure that inlet valve, automatic valve (if any), glands, tubing and shut off nozzle are sound and free from leaks. Check the nozzle is not blocked and is operating as designed (spray jet working correctly). Run out hose reel tubing completely and visually check hose condition. Check all couplings are watertight. Using a flow test meter to ensure a discharge of at least 30 litres a minute is achieved. Replacement hose reels shall be replaced subject to express agreement from the Supervising Officer.

Inspection and Reporting

The contractors’ inspection will identify each item of equipment with an adhesive label that will incorporate the inspectors name, signature and date of inspection. The Supervising Officer will have the opportunity to inspect the work carried out in progress, or on completion, and will have the right to request remedial action, at no extra cost, if the work is not up to standard or incorrect spare parts have been fitted. After each inspection and site visit the contractor will submit a report on the equipment inspected and the action taken, to the Supervising Officer who will certify acceptance.

Definition of Maintenance of Fire Extinguishers – Full Service

Prices offered per fire extinguisher will include service attendance cost, labour, replacement spare parts including clips, caps and labels, extinguisher test discharging and refilling materials, replacement of condemned fire extinguishers and blankets, replacement of powder extinguishers due powder test and CO2 extinguishers due hydraulic pressure test . This cost includes replacement of spare parts that have deteriorated through fair wear and tear excluding any misuse or abuse of equipment. Where a fire extinguisher is found in a discharged condition and requires refilling during a service visit the contractor may charge for refilling materials at discounted prices agreed in this contract.

Refilling

No equipment will be removed from the building for refilling at the contractors premises without prior authorisation from the Supervising Officer. The contractor will make available suitable temporary replacements, which will be returned to him on receipt of the refilled units. Alternative for CO2 the contractor may offer as an option, a service exchange refilled extinguisher provided that it is of the same type and similar age.

Over Haul and Refurbishment

Complete overhaul or refurbishing may only be carried out after the Supervising Officer has received the contractors report and authorised work to commence.

Supply of New Equipment

The contractor will advise the Supervising Officer when items require replacement with reasons reported.

Commissioning costs to be included in the new equipment pricing.

Disposals

At the request of the Supervising Officer the contractor will provide a free disposal service for any extinguishers condemned as unfit for service, however, the contractor reserves the right to charge for disposal of halon fire extinguishers.

SITE & EQUIPMENT SCHEDULE

SITE & EQUIPMENT SCHEDULE

| Address |  |  | Postcode | Water | Foam | CO2 | Powder | H/Reels | Blankets | Hydro | Chemical |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AMBERLEY HOUSE | CEDAR CLOSE | ECKINGTON | S21 4BA | 0 | 2 | 1 | 1 | 0 | 1 | 4 | 0 |
| BRIMINGTON CLINIC | CHURCH STREET, BRIMINGTON | CHESTERFIELD | S43 1JG | 0 | 0 | 4 | 2 | 2 | 2 | 5 | 0 |
| BUXTON HOSPITAL,LONDON ROAD | NORTH DERBYSHIRE N H S TRUST | BUXTON | DE45 1AD | 8 | 0 | 17 | 4 | 0 | 7 | 12 | 0 |
| BUXTON HEALTH CENTRE | BATH ROAD | BUXTON | SK17 9NJ | 6 | 0 | 5 | 2 | 0 | 2 | 0 | 0 |
| CLAY CROSS COMMUNITY HOSPITAL | MARKET STREET, CLAY CROSS | CHESTERFIELD | S45 9NZ | 4 | 4 | 19 | 4 | 0 | 9 | 15 | 1 |
| ORCHARD COTTAGE | DARLEY DALE | NR MATLOCK | DE4 2EU | 0 | 2 | 2 | 1 | 0 | 1 | 2 | 0 |
| ROCKLEY CORE UNIT | 64-66 CARTER LANE | SHIREBROOK, MANSFIELD | NG20 8PL | 0 | 2 | 5 | 2 | 0 | 2 | 5 | 0 |
| SHIREBROOK HEALTH CENTRE | 17 PATCHWORK ROW, | SHIREBROOK MANSFIELD | NG20 8A |  | 0 | 6 | 2 | 0 | 0 | 6 | 0 |
| STAVELEY HEALTH CLINIC | LIME AVENUE, STAVELEY | CHESTERFIELD | S43 3JJ | 0 | 0 | 3 | 1 | 0 | 1 | 3 | 0 |
| WHITWORTH HOSPITAL | 330 BAKEWELL ROAD | MATLOCK | DE4 2JD | 0 | 0 | 17 | 5 | 0 | 5 | 33 | 0 |
| WALTON HOSPITAL | WHITECOTES LANE | CHESTERFIELD | S40 3HW | 22 | 8 | 58 | 28 | 0 | 23 | 44 | 0 |

SITE & EQUIPMENT SCHEDULE

| Address |  |  | Postcode | Water | Foam | CO2 | Powder | H/Reels | Blankets | Hydro | Chemical |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ASH GREEN LEARNING DISABILTIY | ASHGATE ROAD, ASHGATE | OLD BRAMPTON, CHESTERFIELD | S42 7JE | 16 | 2 | 18 | 17 | 0 | 13 | 22 | 0 |
| CHAPEL-EN-LE-FRITH HEALTH CTR | THORNBROOK ROAD,HIGH PEAK | CHAPEL-EN-LE-FRITH | DE45 1AD | 0 | 0 | 5 | 1 | 0 | 1 | 5 | 0 |
| CRESSWELL MEDICAL PRACTICE | WELBECK STREET | CHRESSWELL | S80 4HA | 6 | 3 | 5 | 2 |  | 2 | 2 | 0 |
| DRONFIELD HEALTH CENTRE | HIGH STREET | DRONFIELD | S18 6PY | 0 | 0 | 8 | 2 | 0 | 1 | 8 | 0 |
| ECKINGTON HEALTH CENTRE, | GOSBER ROAD, ECKINGTON | SHEFFIELD | S21 4BZ | 0 | 0 | 3 | 2 | 0 | 1 | 4 | 0 |
| HOPE CLINIC | ECCLES CLOSE, HOPE | HOPE VALLEY | S33 6RG | 0 | 0 | 2 | 1 | 0 | 1 | 2 | 0 |
| KILLAMARSH CLINIC | PARKSIDE SHOPPING CTR | KILLAMARSH SHEFFIELD | S21 1FY | 2 | 0 | 4 | 2 | 0 | 1 | 6 | 0 |
| LANGWITH MEDICAL PRACTICE | 206 MAIN STREET | LANGWITH | NG20 9HD | 4 | 0 | 5 | 1 | 0 | 0 | 0 | 0 |
| NEWHOLME HOSPITAL, RIVERSIDE UNDERCROFT | BASLOW ROAD | BAKEWELL | DE45 1AD | 4 | 0 | 14 | 5 | 0 | 3 | 14 | 0 |
| DR A L NATT SURGERY | 17-19 ST. LAWRENCE ROAD, | NORTH WINGFIELD, CHESTERFIELD | S42 5LH | 0 | 0 | 2 | 1 | 0 | 1 | 3 | 0 |
| NEW MILLS CLINIC | HYDE BANK ROAD, NEW MILLS | HIGH PEAK | DE45 1AD | 0 | 0 | 2 | 2 | 0 | 1 | 3 | 0 |
| CAVENDISH HOSPITAL | MANCHESTER ROAD | BUXTON | DE45 | 13 | 2 | 14 | 8 | 0 | 3 | 21 | 1 |
| WELBECK ROAD HEALTH CENTRE | WELBECK ROAD, BOLSOVER | CHESTERFIELD | S44 6DH | 0 | 0 | 14 | 4 | 0 | 1 | 9 | 0 |
| 30 WHEATBRIDGE ROAD | WHEATBRIDGE | CHESTERFIELD | S40 2AB | 0 | 0 | 5 | 1 | 0 | 0 | 5 | 0 |

SITE & EQUIPMENT SCHEDULE

| Address |  |  | Postcode | Water | Foam | CO2 | Powder | H/Reels | Blankets | Hydro | Chemical |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ASHBOURNE HC | COMPTON ROAD | ASHBOURNE | DE6 1DA | 0 | 0 | 5 | 0 | 0 | 0 | 4 | 0 |
| ASHENFELL SURGERY | CHURCH LANE | BASLOW | DE451SP | 0 | 4 | 1 | 0 | 0 | 1 | 0 | 0 |
| ASHOVER MEDICAL PRACTICE | MILKEN FAR LANE | ASHOVER | S45 0BA | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 0 |
| BELPER CLINIC | DERBY ROAD | BELPER | DE56 1WH | 0 | 0 | 5 | 1 | 0 | 1 | 3 | 0 |
| CASTLE STREET SURGERY | CASTLE STREET | BOLSOVER | S44 6PP | 0 | 1 | 2 | 0 | 0 | 1 | 2 | 0 |
| DOCTORS SURGERY | DIG STREET, | HARTINGTON | DE45 0AQ | 0 | 0 | 4 | 0 | O | 1 | 4 | 0 |
| Drs TURNER & BULL | 4 GORSEY STREET | DRONFIELD | S18 8UE | 0 | 0 | 4 |  | 2 | 1 | 4 | 0 |
| HEANOR MEMORIAL HEALTH CENTRE | WILMOT STREET | HEANOR | DE75 7EF | 0 | 0 | 3 | 0 | 0 | 0 | 3 | 0 |
| HIGHFIELDS MEDICAL CENTRE | 86 COLLEGE STREET | LONG EATON | NG10 4NP | 0 | 0 | 6 | 0 | 0 | 0 | 6 | 0 |
| HOME LOANS | THE MANOR STORE | UTTOXETER ROAD | DE3 3NB | 0 | 5 | 11 | 0 | 0 | 0 | 4 | 0 |
| ILKESTON COMMUNITY HOSPITAL | HEANOR ROAD | ILKESTON | DE7 8LN | 4 | 29 | 63 | 2 | 0 | 11 | 14 | 1 |
| ILKESTON HEALTH CENTRE | WHITE LION SQUARE | ILKESTON | DE7 5TZ | 0 | 1 | 8 | 0 | 0 | 1 | 9 | 0 |
| DR LINGARDS PRACTICE | LIME GOVE WALK | MATLOCK | DE4 3FD | 1 | 1 | 4 | 0 | 0 | 1 | 4 | 0 |
| REPTON HC | ASKEW GROVE | REPTON | DE65 6SH | 0 | 2 | 5 | 0 | 0 | 2 | 3 | 0 |
| RIPLEY HOSPITAL | SANDHAM LANE | RIPLEY | DE5 3EH | 0 | 8 | 35 | 2 | 0 | 3 | 20 | 1 |
| ROBERTSON ROAD | 5 ROBERTSON ROAD | BUXTON | SK17 9DY | 0 | 0 | 0 | 2 | 0 | 1 | 3 | 0 |
| SHIRES HEALTH CENTRE | 18 MAIN STREET | SHIREBROOK | NG20 8DG | 0 | 0 | 7 | 0 | 0 | 1 | 6 | 0 |
| ST. OSWALDS HOSPITAL | BELLE VUE ROAD | ASHBOURNE | DE6 1AU | 0 | 0 | 16 | 2 | 0 | 5 | 16 | 1 |
| STAFFA SURGERY TIBSHELF | 13 WAVERLEY STREET | TIBSHELF | DE55 5PS | 0 | 4 | 9 | 0 | 0 | 1 | 3 | 0 |
| STAFFA SURGERY HOLMEWOOD | 19A HEATH ROAD | HOLMEWOOD | S42 5RB | 0 | 0 | 3 | 0 | 0 | 0 | 2 |  |
| STAFFA SURGERY PILSLEY | WILLOW CLOSE | PILSLEY | S45 8JA | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 |
| STAFFA SURGERY STONSBROOM | 189 BIRKINSTYLE LANE | STONEBROOM | DE55 6LD | 0 | 0 | 6 | O | 0 | 1 | 8 | 0 |
| STUBLEY MEDICAL CENTRE | STUBLYEY DRIVE | DRONFIELD | S18 8QY | 0 | 8 | 2 | 0 | 0 | 2 | 8 | 0 |
| THE SURGERY | THE GREEN | GLAPWELL | S44 5LW | 0 | 0 | 2 | 0 | 0 | 1 | 2 | 0 |
| THE SURGERY | PARKE ROAD | TIDESWELL | SK17 8NS | 0 | 1 | 0 | 4 | 1 |  | 1 | 3 |
| THE SURGERY | 30 WHEATBRIDGR ROAD | CHESTERFIELD | S40 2AB | 0 | 7 | 8 | 1 | 0 | 0 | 4 | 0 |

| TOLL BAR HOUSE | DERBY ROAD | ILKESTON | DE7 5FE | 5 | 3 | 11 | 1 | 0 | 3 | 6 | 0 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DRS ALLENBY & DAVIDSON | STUBLEY DRV MEDICAL PRACTICE | DRONFIELD WOODHOUSE | S18 8QY | 0 | 0 | 9 | 2 | 0 | 2 | 8 | 0 |

PRICING SCHEDULE

PRICING SCHEDULE

| EQUIPMENT | NEW £ | SERVICE EXCHANGE £ | REFILL/RECHARGE £ | ANNUAL SERVICE £ |
| --- | --- | --- | --- | --- |
| 9 Ltr Water |  | N/A |  |  |
| 6 Ltr Water with additive |  | N/A |  |  |
| 2 Kg CO² |  |  |  |  |
| 5 Kg CO² |  |  |  |  |
| 1 Kg Dry Powder |  |  |  |  |
| 2 Kg Dry Powder |  |  |  |  |
| 6 Kg Dry Powder |  |  |  |  |
| 9 Kg Dry Powder |  |  |  |  |
| 2 Kg Foam |  |  |  |  |
| 6 Kg Foam |  |  |  |  |
| 9 Kg Foam |  |  |  |  |
| Fire Blanket |  |  |  |  |
| 1.1 x 1.2 |  | N/A | N/A |  |
| 1.8 x 1.2 |  | N/A | N/A |  |
| Hose Reels |  |  |  |  |
| Hose with Nozzle – 30m |  | N/A | N/A |  |
| Hose with Nozzle – 45m |  | N/A | N/A |  |

Call Out Fee:

Extinguishers:

During Normal Working Hours		- £

Out of Hours					- £

Hose Reels:

Remedial Work per hour			- £

Fixing to Wall:

Extinguishers				- £

Signs:

Fire Extinguisher

(Mounted next to extinguisher)			- £

Delivery/Carriage/Attendance Fee:		- £

Minimum Invoice Total (in applicablicable):	- £

ALL PLUS VAT