Ware Town Council

Ware Priory, High Street, Ware, SG12 9AL

www.waretowncouncil.gov.uk

01920 460316

WARE TOWN COUNCIL TENDER SPECIFICATION

On behalf of Ware Town Council, I have the pleasure of inviting you to submit a fixed price tender for the following project.

Yours faithfully,

Terry Philpott

Town Clerk

| Project name | Lido Shower System Upgrade |
| --- | --- |
| Project objective | To upgrade the hot water provision to showers in the Lido to ensure there is hot water available to all users throughout the day. Also, to increase the number of showers available where possible. |
| Project location | Ware Priory Lido Priory Street Ware SG12 0DE |
| Contract value | £35k- £50k |
| Timescales | We would like this project undertaken during our closed season which will commence at the beginning of October 2023. The job would need to be finished by January 2024. |
| Contact details for further information and site visits | Kat Harter Email : kat@warepriory.co.uk Phone : 01920 888542 Mobile : 07708675762 |
| Contact details for invoice queries | Sean Higgins, Finance Manager sean@waretowncouncil.gov.uk Phone 01920 460316 |
| Primary contact details during the project period. | Kat Harter, Operations Manager Email: kat@warepriory.co.uk Phone: 01920 888542 |
| Contractor requirements essential | A site visit will be required to assess the work needed. Site visits will need to be completed by 26th May. The contractor will need previous experience of fitting commercial/leisure showering facilities. |
| Contractor requirements desirable | Local company |
| Return date for tender submissions | Tender return date 9am – 2nd June 2023 Preferred method by email to tenders@waretowncouncil.gov.uk . If large documents such as maps or visuals are submitted, please provide a paper copy to: Ware Town Council The Priory High Street Ware SG12 9AL Postal tenders or additional information should be submitted in an envelope marked, Lido Shower System Tender Please do not submit enquiries of a general nature to tenders@waretowncouncil.gov.uk as the inbox is only monitored at the time a tender is due to close. |
| Detailed specification | We have previously appointed a consultant to design this specification. Please find the report attached. Overview: Install Gas Fired Water Heaters The existing direct cylinders should be replaced with gas fired condensing water heaters in the same locations as the existing cylinders. The heaters would be approximately 700mm in diameter and around 1900mm high (60KW) or 1400mm high (32KW) For the male, female and outside shower area, 2No gas fired waters heater rated at 32KW with a storage volume of 200 litres Install a smaller 32KW model in the family changing room which would be more than sufficient and could accommodate additional showers should there be an opportunity to install these infuture. The flues for the water heaters which are around 150mm diameter would be installed through the flat roof. A new gas supply pipe could be installed from the boiler room, across the flat roof to serve the heaters. Each gas supply should be fitted with a gas safety panel which would shut off the gas supply in the event of gas leaks or fire. Replace Existing Pipework The cold water supply pipework from the plant room would need to be replaced along with the outlet pipework to include a secondary circulating system with associated pump, and all pipework insulated where possible. This will reduce energy consumption and avoid excessive dead legs in the hot water system that are currently present. Replace Existing Showers (3 in Family changing, 2 in Male Changing, 2 in Female changing. It is recommended that the existing showers, which are in poor condition be replaced with tamper proof shower panels. These will provide timed flow control via push button and automatic flow regulation along with individual thermostatic blending which will minimise any dead legs on the system. The 4 outside showers need to be converted to a hot water supply as they are currently cold water only. |
| Access and possible restrictions in the delivery phase of the project. | Access to the site will be 8am-5pm Monday-Friday as standard. Hours outside of this can potentially be arranged with the Operations Manager. The building will be unoccupied during the planned refurbishment phase. There is parking on site for site vehicles. |
| Progress reporting | The council will require reporting as required and in particular any impact on the project timescale, plus anything that may cause reputational damage to the council. |
| Payment terms | Please specify in the pricing schedule the requirement for any phased payments. WTC seek to pay all correct invoices within 30days. |
| Retention value / period | WTC will retain 10% of the contract value for a period of 3 months. |
| Penalty clauses | Clause to be inserted as required. |
| Conditions of contract | The Council require assurances from all potential contractors through the provision of appropriate documentation that: - All operatives are suitably trained and qualified to use any machinery involved in the work. - Operatives will at all times wear suitable protective clothing and high viz jackets. - Safety and advisory signage will be required as necessary - Contractors will be required to supply details of public liability insurance with the tender papers. - Contractors will be required to undertake a COSHH assessment for all chemicals used during the delivery of the contract. - Contractors will be expected to provide a method statement detailing how the various elements of the work will be undertaken. - Project timescales will be provided where applicable. |

Pricing schedule

| Contractor name |  |
| --- | --- |

| Project name | Lido Shower System |
| --- | --- |
|  | Pricing (excluding VAT) for all works as included on the specification, in the component parts as requested. |
| A |  |
| B |  |
| C |  |
| Total |  |
|  | The council seek to pay invoices within 30days of the receipt of a correct invoice after completion or delivery of the project. If there is a requirement for phased payments, please detail below. |

I / We hereby offer to carry out the works as scheduled and contained in the attached specification.

Signed

Dated

| Contractor name |  |
| --- | --- |
| Address |  |
| Name of primary contact |  |
| Email |  |
| Office phone number |  |
| Mobile phone number |  |

Contract Evaluation

The contacts will be evaluated based on a combination of price and other factors as indicated below.

Please supply information related to each of the headings to allow us to evaluate your tender submission. Please use continuation sheet where necessary.

Based on the information provided shortlisted contractors may be invited to an interview

|  | Max score | score |  |
| --- | --- | --- | --- |
| Price | 50 |  |  |
| Quality of work Training / Qualifications / Experience Please provide names of referees related to existing contracts of a similar nature | 30 |  |  |
| Reliability (Equipment strategy / contingency plans/ method statement / project plan) | 10 |  |  |
| Proximity to Ware (Location of equipment / contractors) | 5 |  |  |
| Environmental factors (Please attach environmental policy) | 5 |  |  |
| Total | 100 |  |  |

The Council reserve the right to not accept any or the lowest tender.

References:

Please provide two References below....

|  | Reference 1 | Reference 2 |
| --- | --- | --- |
| Organisation |  |  |
| Contact name |  |  |
| Contact phone |  |  |
| Contact email |  |  |
| Address |  |  |
| Type of contract |  |  |

Tender submission checklist

| Contractor name |  |
| --- | --- |

|  |  | Office use |
| --- | --- | --- |
| Cost breakdown (excluding VAT) |  |  |
| References |  |  |
| Environmental policy |  |  |
| Public liability insurance |  |  |
| Method statement detailing how the various elements of the work will be undertaken. |  |  |
| Project timescales. |  |  |
| Further information to support the tender evaluation as required |  |  |