## Sheet1
Equipment / Location | Valve Type / Serial Nos Old | New / Refurbed Safety Valve Serial Nos | Valve Size | Safety Valve Set Point | PN Rating | Details | Cert No | Cert Date | Date Installed | 24 Months after Install date | Comments
North Wing
North Wing Main Steam 1 30/PRV10/5A Tag 05 | Spirax SV 60 7AS | 292077 | DN 80/125 Flanged | 6.0 Bar | PN 25/16 | Refurbished safety | 99617 | 2020-01-28 | 2021-04-17 | 2023-04-17
North Wing Main Steam 2 30/PRV10/5B Tag 13 | Spirax SV 60 7AS | 292076 | DN 80/125 Flanged | 6.0 Bar | PN 25/16 | Refurbished safety | 99618 | 2019-12-10 | 2021-04-17 | 2023-04-17
Autoclave 30/PRV/13 5A Tag 140 | BESA 18-186-19 | Spirax SV 343139 | DN 50/80 Flanged | 4.0 Bar | PN 25/16 | Refurbished safety | 99619 | 2020-01-28 | 2020-06-09 | 2022-06-09
Autoclave 30/PRV/13 5B Tag 134 | BESA 18-186-21 | Spirax SV 343138 | DN 50/80 Flanged | 4.0 Bar | PN 25/16 | Refurbished safety | 99620 | 2020-01-28 | 2020-05-27 | 2022-05-27
AHU 30/PRV/12 5A Tag 38 | BESA 18-371-9 | Spirax SV 343134 | DN 32/50 Flanged | 3.0 Bar | PN 25/16 | Refurbished safety | 99621 | 2020-01-28 | 2020-05-27 | 2022-05-27
AHU 30/PRV/12 5B Tag 43 | BESA 18-371-10 | Spirax SV 299822 | DN 32/50 Flanged | 3.0 Bar | PN 25/16 | Refurbished safety | 99622 | 2020-01-28 | 2020-06-09 | 2022-06-09
* CSU 30/PRV/11 5A Tag 154 | Spirax SV 60 7AS |  | DN 25/40 Flanged | 2.0 Bar | PN 25/16 | Not used off line isolated | N/A | N/A | N/A | N/A
* CSU 30/PRV/11 5B Tag 148 | Spirax SV 60 7AS |  | DN 25/40 Flanged | 2.0 Bar | PN 25/16 | Not used off line isolated | N/A | N/A | N/A | N/A
LPHW Skid 1 42/HE/01 Tag 298 | Nabic Fig 542 S/N 9477706 | Nabic Fig 542 S/N None | DN 65 Screwed | 4.0 Bar | No Data | Refurbished safety | 99623 | 2020-01-28 | 2020-05-07 | 2022-05-07
LPHW Skid 2 42/HE/02 Tag 315 | Nabic Fig 542 S/N 9486029 | Nabic Fig 542 S/N None | DN 65 Screwed | 4.0 Bar | No Data | Refurbished safety | 99624 | 2020-01-28 | 2020-05-04 | 2022-05-04
HWS Calorifiers 70/HWS/01 Tag 348 | Nabic Fig 542 S/N 9477700 | Nabic Fig 542 S/N None | DN 40 Screwed | 4.0 Bar | No Data | Refurbished safety | 99625 | 2020-01-28 | 2020-05-05 | 2022-05-05
HWS Calorifiers 70/HWS/02 Tag 332 | Nabic Fig 542 S/N 9477700 | Nabic Fig 542 S/N None | DN 40 Screwed | 4.0 Bar | No Data | Refurbished safety | 99626 | 2020-01-28 | 2020-05-06 | 2022-05-06
HWS Calorifiers 72/HWS/01 Tag 365 | Nabic Fig 542 S/N 9182322 | Nabic Fig 542 S/N None | DN 25 Screwed | 4.0 Bar | No Data | Refurbished safety | 99627 | 2020-01-28 | 2020-05-05 | 2022-05-05
HWS Calorifiers 72/HWS/02 Tag 382 | Nabic Fig 542 S/N 9182322 | Nabic Fig 542 S/N None | DN 25 Screwed | 4.0 Bar | No Data | Refurbished safety | 99628 | 2020-01-28 | 2020-05-06 | 2022-05-06
HWS Calorifiers 71/HWS/01 Tag 404 | Nabic Fig 542 S/N 9477700 | Nabic Fig 542 S/N None | DN 40 Screwed | 4.0 Bar | No Data | Refurbished safety | 99629 | 2020-01-28 | 2020-05-05 | 2022-05-05
HWS Calorifiers 71/HWS/02 Tag 421 | Nabic Fig 542 S/N 9477700 | Nabic Fig 542 S/N None | DN 40 Screwed | 4.0 Bar | No Data | Refurbished safety | 99630 | 2020-01-28 | 2020-05-06 | 2022-05-06
Main Steam Seperator 30/SEP/10 | Spirax | N/A | N/A | N/A | N/A | Internal Inspection | N/A | N/A | 2020-05-30 | 2022-05-30
Laundry Steam Seperator 30/SEP11/5 | Spirax |  | N/A | N/A | N/A | Inspection Req | N/A | N/A | 2020-05-30 | 2022-05-30
Equipment / Location | Valve Type / Serial Nos Old | New / Refurbed Safety Valve Serial Nos | Valve Size | Safety Valve Set Point | PN Rating | Details | Certificate No | Cert Date | Date Installed | Due date 24 months
West Wing
Autoclave 30/PRV/15 5A Tag 83 | BESA S/N 17-945-7 | BESA S/N 19-1033-1 | DN32/50 Flanged | 4.0 Bar | PN 25/16 | New Safety | 22005 | 2019-09-24 | 2020-03-11 | 2022-03-11
Autoclave 30/PRV/15 5B Tag 76 | BESA S/N 17-896-15 | Spirax SN SV299823 | DN32/50 Flanged | 4.0 Bar | PN 25/16 | Refurbished safety | 99631 | 2019-12-10 | 2020-03-11 | 2022-03-11
AHU 30/PRV/14 5B Tag 13 | BESA S/N 17-945-3 | Spirax SN SV290967 | DN 25/40 Flanged | 3.0 Bar | PN 25/16 | Refurbished safety | 99633 | 2020-01-28 | 2020-03-11 | 2022-03-11
AHU 30/PRV/14 5A Tag 19 | BESA S/N 17-1567-13 | Spirax SN SV343131 | DN 25/40 Flanged | 3.0 Bar | PN 25/16 | Refurbished safety | 99632 | 2019-12-10 | 2020-03-11 | 2022-03-11
Main Steam Seperator 30/SEP/12 | Spirax | N/A | N/A | N/A | N/A | Inspection Req | Internal Inspection | N/A | 2020-05-30 | 2022-05-30
Equipment / Location | Valve Type / Serial Nos Old | New Safety Valve Serial Nos | Valve Size | Safety Valve Set Point | PN Rating | Details | Certificate No | Cert Date | Date Installed | 24 Months after Install date
East Wing
AHU 30/PRV/16 5A Tag 11 | BESA S/N 17-945-12 | Spirax S/N 344050 | DN 40/65 Flanged | 3.0 Bar | PN 25/16 | Refurbished safety | 99634 | 2020-01-28 | 2020-04-01 | 2022-04-01
AHU 30/PRV/16 5B Tag 12 | BESA S/N 17-840-13 | BESA S/N 19-658-2 | DN 40/65 Flanged | 3.0 Bar | PN 25/16 | New Safety Installed | 22006 | 2019-09-24 | 2020-04-01 | 2022-04-01
Autoclave 30/PRV/17 5A Tag 282 | BESA S/N 17-663-25 | Spirax S/N 343137 | DN50/80 Flanged | 3.0 / 4.0 Bar | PN 25/16 | Refurbished safety | 99635 | 2020-01-28 | 2020-03-17 | 2022-03-17
Autoclave 30/PRV/17 5B Tag 281 | BESA S/N 17-840-15 | BESA S/N 19-126-10 | DN50/80 Flanged | 4.0 Bar | PN 25/16 | New Safety Installed | 22007 | 2019-09-24 | 2020-03-17 | 2022-03-17
LPHW Skid 1 40/HE/01 Tag 192 | Nabic Fig 542 S/N 8741242 | Nabic Fig 542 Job no 99636 | DN 40 Screwed | 4.0 Bar | No Data | Refurbished safety | 99636 | 2020-01-28 | 2020-04-16 | 2022-04-16
LPHW Skid 1 40/HE/02 Tag 175 | Nabic Fig 542 S/N 9477700 | Nabic Fig 542 Job no 99637 | DN 40 Screwed | 4.0 Bar | No Data | Refurbished safety | 99637 | 2020-01-28 | 2020-04-16 | 2022-04-16
Main Steam Seperator 30/SEP/14 | Spirax | N/A | N/A | N/A | N/A | Inspection Req | Internal Inspection | N/A | 2020-05-30 | 2022-05-30
Equipment / Location | Valve Type / Serial Nos Old | New / Refurbed Safety Valve Serial Nos | Valve Size | Safety Valve Set Point | PN Rating | Details | Certificate No | Cert Date | Date Installed | 24 Months after Install date
Energy Centre
North/West/ ISO Steam 30/PRV/4A Top Tag 94 | TLV / Lesser SN 11319594 | BESA S/N 19-811-13 | DN 100/150 Flanged | 9.0 Bar | PN 25/16 | New Safety | 22004 | 2019-09-24 | 2020-01-04 | 2022-01-03
North/West/ ISO Steam 30/PRV/4B Bottom Tag 103 | TLV / Lesser SN 11358030 | Spirax Sarco SV296013 | DN 100/150 Flanged | 9.0 Bar | PN 25/16 | Refurbished safety | 99638 | 2019-12-10 | 2020-01-04 | 2022-01-03
Hotwell 1 & 2 1A Tag 135 30/PRV/5A | BESA S/N 17-1550-1 | Spirax Sarco SV260966 | DN 25/40 Flanged | 4.0 Bar | PN 25/16 | Refurbished safety | 100143 | 2019-10-17 | 2020-04-30 | 2022-04-30
Hotwell 1 & 2A Tag 142 30/PRV/5B | BESA S/N 17-896-13 | Spirax Sarco SV292440 | DN 25/40 Flanged | 4.0 Bar | PN 25/16 | Refurbished safety | 99639 | 2020-01-28 | 2020-04-30 | 2022-04-30
HVAC East 1 30/PRV/5A Tag 65 | BESA S/N 17-840-17 | Spirax Sarco SV309447 | DN 80/125 Flanged | 6.0 Bar | PN 25/16 | Refurbished safety | 99640 | 2020-01-28 | 2020-04-29 | 2022-04-29
HVAC East 2 30/PRV/5B Tag 74 | BESA S/N 17-253-14 | Spirax Sarco 309448 | DN 80/125 Flanged | 6.0 Bar | PN 25/16 | Refurbished safety | 99641 | 2020-01-28 | 2020-05-30 | 2022-05-30
ETP 30/PRV/2A Tag 37 | BESA S/N 17-945-9 | Spirax Sarco SV292395 | DN 32/50 Flanged | 9.0 Bar | PN 25/16 | Refurbished safety | 99642 | 2020-01-28 | 2020-04-30 | 2022-04-30
ETP 30/PRV/2B Tag 45 | BESA S/N 17-986-16 | Spirax Sarco SV292394 | DN 32/50 Flanged | 9.0 Bar | PN 25/16 | Refurbished safety | 99643 | 2020-01-28 | 2020-04-30 | 2022-04-30
External Steam ISOs 1 30/10/5A Tag 24 | BESA S/N 18-371-6 | Spirax Sarco SV321923 | DN65/100 Flanged | 6.0 Bar | PN 25/16 | Refurbished safety | 99644 | 2020-01-28 | 2020-04-29 | 2022-04-29
External Steam ISOs 2 30/10/5B Tag 32 | BESA S/N 18-186-10 | Spirax Sarco SV321924 | DN65/100 Flanged | 6.0 Bar | PN 25/16 | Refurbished safety | 99645 | 2020-01-28 | 2020-04-29 | 2022-04-29
External Main Steam Seperator ISOs 30/SEP/15 | Spirax | N/A | N/A | N/A | N/A | Internal Inspection | N/A | N/A | 2020-05-30 | 2022-05-30
Flash Vessel 30 FV 1 Tag 284 | Spirax | N/A | N/A | N/A | N/A | Internal Inspection | N/A | N/A | 2020-06-25 | 2022-06-25
Flash Vessel 30 FV 1 Tag 284 | BESA S/N 18-73-1 | Spirax Sarco SV292266 | DN40/65 Flanged | 3.0 Bar | PN 40/16 | Refurbished safety | 99646 | 2020-01-28 | 2020-04-30 | 2022-04-30
Blowdown Vessel | Spirax BDV60 |  | N/A | 3.0 Bar | N/A | Inspection | N/A | N/A | 2020-01-06 | 2022-01-05
North West ISOs E/C Steam Seperator 30/SEP/04 | Spirax | N/A | N/A | N/A | N/A | Internal Inspection | N/A | N/A | 2020-05-30 | 2022-05-30
East Wing HVAC Steam Sepertator 30/SEP/03 | Spirax | N/A | N/A | N/A | N/A | Inspection Req | N/A | N/A | 2020-05-30 | 2022-05-30
ETP Seperator 30/SEP/02 | Spirax | N/A | N/A | N/A | N/A | Inspection Req | N/A | N/A | 2020-05-30 | 2022-05-30
Hotwell Seperator 30/SEP/05 | Spirax | N/A | N/A | N/A | N/A | Inspection Req | N/A | N/A | 2020-05-30 | 2022-05-30
Additional
Western Boiler External PRV safety Top | Nabic 500 | Nabic 500 S/N 12132232 A | 50/40 | 6 | No data | New Safety Installed | LB68199/1/C101 | 2020-03-11 | 2020-04-07 | 2022-04-07
Western Boiler External PRV safety Lower | Nabic 500 | Nabic 500 S/N 12132232 B | 50/40 | 6 | No data | New Safety Installed | LB68199/1/C101 | 2020-03-11 | 2020-04-07 | 2022-04-07
Insectory | [10 empty] | Details are required
ASH Building | [10 empty] | Details are required
IS4L X 5
1 | Spirax SV 607AS | Spirax Sarco SV 267615 | 25/40 | 7.0 | PN 40/16 | Refurbished safety | 105802 | 2020-08-10 | TPI Installed | TPI Installed
2 | Spirax SV 607AS | Spirax Sarco SV 260969 | 25/40 | 5.0 | PN 25/16 | Refurbished safety | 105801 | 2020-08-10 | TPI Installed | TPI Installed
3 | Spirax SV 607AS | Spirax Sarco SV 292439 | 25/40 | 3.0 | PN 25/16 | Refurbished safety | 105800 | 2020-08-10 | TPI Installed | TPI Installed
4 | BESA 241-C-H4 R/A | BESA 19-437-7 | 25/40 | 5.0 | PN 25/16 | New valve | 22166 | 2020-07-24 | TPI Installed | TPI Installed
5 | BESA 241-C-H4 R/A | BESA 19-62.2 | 25/40 | 3.0 | PN 25/16 | New valve | 22166 | 2020-07-24 | TPI Installed | TPI Installed
BSU x 2
BSU No 1 Cage & Autoclave | Spirax | Spirax | 65/65 | 4.4 | PN 16 | Old Valve |  |  |  |  | Old valve to be refurbed or replaced with new
BSU No 2 AHUs | Spirax | Spirax | 40/40 ? | 2.0 ? | PN 16 | Old Valve |  |  |  |  | Old valve to be refurbed or replaced with new
ISO 8 | Out of service | [9 empty] | Details are required
ISO 9 | Out of service | [9 empty] | Details are required
ISO 10 | Out of service | [9 empty] | Details are required
ISO 11 | Out of service | [9 empty] | Details are required
ISO11 New ETP x 2 | Spirax Sarco | Spirax Sarco | Flanged PN16 | 5.0 bar | PN 16 | [5 empty] | New Valve to be ordered, old valve to be sent off for refurbishment
Formulas:
N/A = [Date Installed]+730