Provision of Pirbright Site Steam Management and Boiler Maintenance

BACKGROUND

The Pirbright Institute uses steam for a number of business and compliance critical processes. It is currently generated using natural gas, with oil backup fuel using two steam supply networks from two locations:

Energy Centre (EC1) 4 x horizontal shell and tube packaged boilers rated at 6,510 kg/h supplying:

- Plowright (North, East, West wings, ETP)

- Isolation units (Biggs, ISO 11, PMINCIN, ISO 8, ISO 11 ETP)

- Future Brooksby building.

Western Boilerhouse 3 x vertical shell and tube packaged rated boilers rated at 960 kg/h supplying:

- IS4L Insectary

- Phillip Mellor Insectary (PMI)

- Ash building

- Biological Support Unit (BSU).

Other buildings on site not fed by steam are not included within the scope of this contract.

WORKS INFORMATION

The scope of this contract is to ensure continuity of steam generation and supply to The Pirbright Institute (TPI) site steam distribution networks described above. Steam provides both a process function as well as a heating and humidification function across TPI. The steam distribution system will have future connections to other projects and other existing Institute buildings, most notably the Brooksby large Animal Facility and a steam feed from a Combined Heat & Power Plant (ETA for steam generation: Q2 2022).

The contractor shall ensure that the continuous safe, seamless and uninterrupted supply of steam from 760 kg/h to 18,000 kg/h of steam (EC1) at a generation pressure between 9 and 9.5 bar(g) (EC1) and between 7.0 and 7.5 bar(g) of steam (Western Boiler house).

The contractor shall provide suitably qualified and experienced operatives to manage the energy centre and follow the guidelines laid down in BG01 and INDG436.

The contractor’s Lead boiler operator must be Boiler Operator Accreditation Scheme (BOAS) trained & certified, additionally all other engineers / operatives preferably to be trained & certified or actively being trained & working towards certification.

The contractor shall maintain and regularly review a Boiler house Technical Risk Assessment and work instructions for the operation and management of both boiler houses. The contractor shall produce and maintain individual task specific RAMS for tasks carried out within the contract.

The Contractor shall comply with the requirements of the written scheme and to ensure the steam system is kept within the boundaries of the written scheme at all time by means of planned annual inspections. Annual boiler inspections are to be co-ordinated with SEO – Infrastructure.

The Contractor shall follow TPI’s Safe System of Work, including Permit and LOTO system at all times.

Daily liaison with TPI Specialist Equipment Owner (Infrastructure) to discuss operational issues.

The contractor shall maintain daily logs of boiler operations, temperatures, usage, chemical and water quality levels and save these to TPI’s company network drive.

Attendance and routine testing to be carried out as per BG01 arrangement 2. Call out to be available 24 / 7, with attendance within 2 hours.

Site opening hours are 0700 - 1900 hours weekdays Anticipated working hours are 08:45 hours to 16:45 hours. Weekends, bank holidays and out of hours presence as required is permitted following approval through TPI security.

Work location: The Pirbright Institute, Ash Road, Pirbright GU24 0NF.

EQUIPMENT RESPONSIBILITY AND DEMARCATION

Maintaining steam supplies to TPI requires a number of connected systems to be monitored and maintained as well as the steam boilers. These are listed below and are included in this maintenance and operations package:

Water Services

Scope of responsibility shown in document #20 for EC1 and includes the following:

- Domestic cold water tanks and Pumps Softener plant and bulk salt saturator

- Domestic soft water tanks and Pumps Process soft water tanks and Pumps

- Lab cold water tanks and Pumps Carbon Filters

- Reverse Osmosis (RO) water skids serving boilers and Process Soft water

- P5 pump serving Hotwell tanks

- Western boilerhouse water supply and treatment

- All consumables for the above including water treatment and salt.

Bulk Oil Storage

Main steam generation system items:

- (EC1 ONLY) Cold tanks

- Hotwells

- Packaged Steam Boilers.

- Feedwater pumps

- Blow down vessels.

- Boiler chemical dosing skids

- All interconnecting pipework and ancillaries (valves, instruments etc.)

- Condensate receivers and pumps

- Plowright Hot water system (HWS) skids x 6

- Low pressure hot water (LPHW) steam exchanger North Wing and East Wing

- Gas, Steam and condensate meters

The Contractor is responsible for all aspects of maintaining the steam systems and associated utilities listed above within the Energy Centre (EC1) and the Western Boilerhouse and all steam distribution & condensate return plant shown in demarcation drawings within the attached Document Register.

As a general principle the Contractor shall be responsible for the maintenance of all steam distribution plant located outside of contained areas and before point-of-use.

MAINTENANCE ACTIVITIES

The following notes are intended as a guide to required maintenance activities for pricing purposes:

Mains Incoming Cold Water Service

- Daily: Mains water meter readings incomer

- Weekly: Mains water pipe work checks, Valves and components check

Cold water storage and supply systems

- Daily: Checks required Tank levels and temperatures, pump checks, tank status lids secure, overflow checks.

- Weekly: Meter readings, Operational check on valves and components

- Monthly: Water analysis checks

- Quarterly: Pump service.

Water Softeners

- Daily: Bulk salt saturator visual checks Bund area sump pump checks, water softness tests on all systems, flow meter checks when in operation, brine tank checks.

- Daily: Main filter units Small Blended backwash auto cycle check operational Main filter units large serves RO backwash auto cycle check operational. Water softener Monitoring panel check operation and water quality for soft water

- Quarterly: Blended water filter pressure drops and filter change as required, Soft water to RO carbon filters and RO skids pressure drops and filters change as required.

Reverse Osmosis plant

- Daily: Checks, Skid operation Running hours, Water quality, Pre filter pressure drops, General check of RO skid operation and visual of components Carbon filter check of operation i.e. backwash and regen cycles P5 Pump check of operation. General component checks of pumps etc RO feed water meter readings daily, RO Water tank checks external and internal.

- Weekly: Soft water check water softness

- Monthly: Check on redundancy changeover of water supplies

- Quarterly: Pre Filter change out 6 filters every three months or as required

Hotwell tanks

- Daily: Check tank level indicator, Steam injection temperature, Tank checks for leakage, level control panel operation levels, Circulating pump operation.

- Weekly: Operation of steam lances, RO feed water check of solenoid valve operation and bypass, Circulating pump operation checks. Chemical dosing lines, Condensate return.

Steam Boilers

- Daily: General visual checks on boiler and components, Daily gas meter readings, Boiler steam load / output daily readings, Steam pressures recorded, Sight glass checks daily Boiler Water meter readings, Daily bottom blow down. Due to the uncertainty of load conditions boiler water quality should be checked daily and adjusted to suit and closely monitored.

- Weekly: Boiler weekly evaporation tests to be carried out on each boiler to check low water cut out and low-level lock out. Gauge glass blowdown, 1st high and 2nd high tests pump change over duty stand by. Boilers should be changed from gas to oil for 1 hour duration weekly and changed back to gas.

- Monthly: Feed water pump strainer checks, Steam trap checks (via local monitoring system)

Boiler Chemical treatment plant

- Daily: Checks on dosing pumps and chemical levels, Chemicals 1568, 1258 and 1110 dosing feed tank checks daily Check dosing lines visual for correct operation. Order stock of reserve chemicals for shot dosing or top up main storage facility if required.

- Weekly: Employ water treatment specialist for samples and lab test say 1 month but may require weekly attendance dependant on loads and boiler water quality.

Boiler back up oil system

Boilers are fed from the oil system to provide back in case of gas disruption and also serves the generators (EC1).

- Weekly: Tank level checks on external monitoring system, Check tank levels from building management system compare against external monitoring Tank bund alarms checks, General tank external status, Run pump duty stand by in hand proving pump operation.

- Monthly: Check for oil leaks in general, Check operation / meter readings on each boiler Check fire alarm interface on oil solenoid valve.

- Quarterly: Check duplex filters / strainers, Check Boiler oil control valve for correct operation Check each boiler’s oil feed strainer.

Meters and Probes

- Quarterly: Steam meters, Pressure reducing valve (PRV), Hotwell level controls to be maintained / calibrated.

Steam to point of use

- Weekly:

Energy centre Main PRV sets North check general operation of compressed air valves

Energy centre Main PRV sets East Heating Ventilation Air Conditioning (HVAC) check general operation of PRV valves and pressure drop settings

Energy centre Main PRV sets East ETP check general operation of PRV valves and pressure drop settings

Energy centre Main PRV Hotwell check general operation of PRV valves and pressure drop settings

Western Boilerhouse PRVs check general operation of PRV valves and pressure drop settings.

- Quarterly

The above PRV sets have in line strainers and these should be checked

The steam to the point of use have strainers fitted on Air Handling Units (AHU) frost coils, reheat coils, PRVs sets and would need to be checked on a regular basis

Steam trap checks (via local monitoring system).

- 2-Yearly

Removal, refurbishment and replacement of all Safety Valves within steam distribution network. (Not including boilers, these are Annual). Programme of replacements should be staggered and programmed with existing planned shutdown schedules where possible.

Condensate recovery receivers

- Weekly: Check on level control and pump operation. Condensate return line isolation valve, Rotate duty stand by pumps. Visual checks of receivers and pump sets

- Annual: Service.

HWS Steam Skids North wing

- Weekly: HWS storage temperatures, Cold water feed pressures, Steam general visual checks High temperature cut out checks, HWS Circulating pump operational.

- Quarterly: full service.

LPHW Steam exchanger North wing and LPHW East wing Exchangers

- Monthly: General checks on skids including Steam general visual checks, High temperature cut out checks Secondary heating pumps operational checks

- Quarterly: full service.

Boiler Annual Checks

Annual inspection of 4 boilers in two parts:

Part 1

Each boiler will require the following strip down for insurance inspection,

- Remove Top and bottom mud holes gaskets required Remove rear furnace plate new gaskets required Remove back end plates new gaskets required

- Remove front furnace inspection doors gaskets required Remove crown valve for inspection new Gaskets required

- Remove safety valves and send away for re certification new gaskets required x 2 per boiler

- Remove burner

- Boiler pressure gauge removal and send for recertification Pump pressure gauge remove and send for recertification

- Remove Sight glasses new gaskets, New glass required (pain in arse)

- Remove all level probes and flanges 4 probes and two flanges new gaskets required Remove auto TDS valve and fittings new gaskets required

- Remove bottom blow down valve and fittings new gaskets required Remove Feed water valve and NRV new gaskets required

After inspection by Insurance inspector rebuild boiler Service of burner oil and gas full combustion tests All safety interlock checks.

Full working inspection to be carried out prior to insurance inspection internal test against closed crown by Boiler engineer

Part 2

- Full working inspection Evaporation tests 1st low, 2nd low 1st high 2nd high

- Safety valve accumulation test Boiler high pressure stat check Sight glass checks

- Other safety checks as required to be determined by Insurance inspector.

Additional Requirements

Contractor to conduct survey and identify, order and hold stock of critical spares required to maintain the systems as required.

Hold stock of chemicals as directed by treatment requirements.

PARTICULAR REQUIREMENTS

- Area of responsibility (demarcation) includes all steam generation and distribution plant within:

  - P505 Energy Centre (EC1)

  - P095 Western Steam Plant

  - Steam distribution plant outside of these areas up to (but not including) containment barrier or point of use.

- Area of responsibility is marked on drawings referenced in Appendix 1: Document Register.

- Contractor to maintain (in-house or subcontract) for plant:

- Steam generation and distribution plant within area of responsibility

- RO plant serving EC1 and Western boilers.

- Water softeners serving EC1 and Western boilers.

- Boiler feedwater and domestic / process / lab CWS tanks & pumps (asset list of pumps and tanks).

- Boiler feedwater treatment and chemistry.

- Steam (heat) meter maintenance and yearly calibration.

- Steam generation and distribution system Safety Valves within Area of responsibility.

- Contractor to oversee and or escort site visits for:

(1) EC1 and Western boiler insurance inspections

(2) Bulk salt delivery Energy Centre

(3) Fuel oil delivery to main and western boilers houses

(4) Any contractor visiting site in relation to steam Production and distribution.

- Contractor to have no responsibility for:

- CHP plant waste heat boiler

- Steam infrastructure inside of contained area or as part of barrier / process equipment (See Appendix 1: Demarcation of Services)

- Contractor will undertake regular reviews of all current subcontractors and will make any recommendations for change at Monthly meetings.

- Contractor to report the following monthly Key Performance Indicators (KPIs):

- Boiler efficiencies (Gas vs steam output per boiler).

- Cumulative steam produced per boiler (kg).

- Condensate return percentage per condensate return meter / system.

- Total Gas and Oil usage.

- Boiler up / down time.

- Contractor to adhere to all of The Pirbright Institute’s Safe System of Work and LOTO systems.  Contractor will also commit staff to undertake The Pirbright Institute’s SSoW and LOTO training programmes.

- Contractor to identify and maintain critical spares stock to operate and maintain steam services in collaboration with TPI Infrastructure Specialist Equipment Owner - Infrastructure. Existing critical spares list shown in APPENDIX 2.

- Contractor to provide average cost of NDTs and five yearly inspections to The Pirbright Institute.

- TPI to arrange and manage insurance inspections for field equipment on the steam system i.e. heat exchangers, relief valves etc.

- Contractor to undertake based on industry knowledge best practices and competent training activities for the safe and continuing operation of the critical steam systems. (Twice Weekly water quality tests and associated test kits as an example).

- Contractor and TPI to meet monthly to review areas of concern, discuss outstanding defects and plant performance. This meeting to be chaired and minuted by Specialist Equipment Owner – Infrastructure.

- Contractor to adopt and use the Pirbright Institute CMMS system to record all Planned Preventative and Reactive Maintenance tasks.

- Contractor to use the TPI N: drive location to store all 3rd party Service Reports, and statutory evidence, referenced to appropriate CMMS Work Order number.

- Contractor to Provide future recommendations and advice to The Pirbright Institute on improved steam management and cost saving techniques, including developing and introducing Energy Efficiency Measures. Also to be discussed at monthly meeting.

- Contractor to provide basic boiler house familiarisation to The Pirbright Institute Call Out and BMS engineers.

- Contractor to state markup on replacement parts and other services & subcontracting to be stated.

- Each on site engineer to hold industry relevant accreditation such as Boiler Operations Accreditation Scheme.

- Security clearance of all site engineers to be applied for not more than 2 months before contract commencement.

- Out of hours work: Contractor to maintain steam supply 24/7/365 through out-of-hours working as required.

- Callout: 2 hours maximum response to attend site and reinstate steam supply following out of hours failure.

- KEY CONTACTS

Dirk Duncan					SEO- Critical Infrastructure

Tel No: 01483 231144

Email: dirk.duncan@pirbright.ac.uk

APPENDICES

APPENDIX 1: Document Register (contains demarcation drawings)

APPENDIX 2: 24m SAFETY VALVE SCHEDULE