Call-Off Schedule 20 (Call-Off Specification)
This Schedule sets out the characteristics of the Deliverables that the Supplier will be required to make to the Buyers under this Call-Off Contract.

Contents:
Appendix 1 – Detailed Services Specification
Appendix 2 – The Facilities (separate excel file)
Appendix 3 – Output Specification Availability Standards

APPENDIX 1

Lewisham Brockley PFI Housing Condition Survey SPECIFICATION

SERVICES
# Introduction
    1. The Services to be provided by the Surveyor are aimed at ensuring that the Contract Data upon which the complete estates management service (those services to be provided by Project Co pursuant to the output specification in the various schedules and the Project Agreement in general) relies is robust, accurate, complete and represents good industry practice, all as required by the Project Agreement.
    1. The Contract Data (“Contract Data ”) shall comprise of the:
      1. Schedule of Accommodation/asset register;
      1. Maintenance manuals;
      1. Condition Appraisal reports
      1. Original (Hunters) condition survey data
      1. SAP (Standard Assessment Procedure) assessment of the dwellings energy performance and environmental impact. (This SAP calculation is then incorporated into the EPC to rate the building from A to G).
      1. PPM Task Lists;
      1. PPM schedules; and
      1. MEP Equipment Schedules.
    1. The Services listed in this Schedule are a non-exhaustive list of activities aimed at ensuring the Surveyor undertakes sufficient inspections, analysis and surveys to provide a suitable Condition Appraisal for each of the 1829 dwellings. Also to provide a priced schedule of any required remedial works found to be required. The Surveyor shall include for verifying that any remedial works have been satisfactorily completed either in person or by photographic evidence once the Surveyor is notified that this work is complete. For pricing purposes, the surveyor should assume that 20% of the dwellings require some remedial work.
    1. In the event of any inconsistency between the requirements of this paragraph 1 and the requirements of the remainder of this Schedule, the requirements of this paragraph 1 shall take precedence.
    1. The Services listed in this Schedule require the Surveyor and the Authority to agree certain matters relating to the Services to be performed. In respect of such matters, the Surveyor shall be required to act impartially, in good faith and in an open and transparent manner.
# Surveyor’s Method Statement
    1. The Surveyor shall prepared a method statement detailing the manner in which it shall deliver these Services which will be updated following the review of the Project Agreement standards and agreed with the Authority (“Method Statement”). The Method Statement shall include the Surveyor’s draft templates and methodology for the Survey (the survey produced pursuant to paragraph 4 below), and the Compliance Audit, which shall then be developed as detailed in this Schedule. The Surveyor shall also provide a Programme of Work of activities that they expect to follow which shall be updated at least fortnightly as necessary to show activities and anticipated end dates.
    1. For the avoidance of doubt, the Surveyor is required to deliver the Services in full. In the event of any inconsistency between the terms of the Surveyor’s Method Statement and the requirements of this Schedule, this Schedule shall take precedence.
  1. Review of the Contract Data
    1. The Authority, shall provide the Surveyor with the existing Contract Data and a copy of the Project Agreement. The Surveyor shall review the Contract Data and identify to the Authority any additional information which the Surveyor reasonably requires to perform the Services. The Authority shall provide, or procure that its sub-contractors provide, the additional information requested by the Surveyor.
    1. The Surveyor shall identify the project specific requirements as set out in the Project Agreement relating to the delivery of the complete estates maintenance service, and agree these with the Authority (“Project Requirements”) at the following levels:
      1. in respect of individual dwellings;
      1. in respect of individual buildings; and
      1. in respect of individual compliance requirements.
The Surveyor shall review ANNEX 1 OUTPUT SPECIFICATION AVAILABILITY STANDARDS as annexed to this document and any relevant clauses and schedules in the Project Agreement that impact or influence the AVAILABILITY STANDARDS and other project requirements and determine whether this is a condition related requirement or a compliance related requirement. See also the pricing matrix, Attachment 4 Price Schedule.
    1. The Authority requires the Surveyor to use the agreed Survey template when carrying out the Survey. Each dwelling, system and area shall be assessed against ANNEX 1 OUTPUT SPECIFICATION AVAILABILITY STANDARDS as annexed to this document and any relevant clauses and schedules in the Project Agreement that impact or influence the AVAILABILITY STANDARDS and other Project Requirements.
The Surveyor shall review the documents provided and create a survey standards template for the approval of the Authority against which the CONDITION of each dwelling or asset shall be assessed as either a “Pass” (compliant) or “Fail” (non compliant).
In the event of a Fail, the surveyor shall;
1. Identify what work is required to rectify the defect identified as a Fail so that upon completion of any work to rectify, it will achieve the Availability Standards
2. Estimate the cost to rectify the failure based on normal costing methods as agreed with the Authority such as RICS BCIS costs, including any design and management fees, prelims, profit, management and VAT.
3. Check any “Fail” item upon completion to certify that it has been adequately rectified or otherwise. This may be via photographic evidence, documentation (e.g. commissioning certificates or gas safe certificates) or physical check on site. At least 40% shall be by physical checking by a qualified surveyor.
    1. The Authority has developed the following standards to be adopted when carrying out the Compliance Audit (“Compliance Standard”). Each asset, and system shall be assessed against ANNEX 1 OUTPUT SPECIFICATION AVAILABILITY STANDARDS as annexed with this document and all relevant clauses and schedules in the Project Agreement that impact or influence the AVAILABILITY STANDARDS and other Project Requirements. The Surveyor shall record the results using the following criteria, with Grade “Green” being deemed compliant and Grades “Amber” and “Red” being non-compliant: The Surveyor shall review the documents provided and create a Survey Standards Template for the approval of the Authority against which the COMPLIANCE of each dwelling or asset shall be assessed.
Standard/Grade
Green	Compliant – all the necessary equipment, systems, and health & safety control measures are functioning as intended and the relevant Project Requirements and AVAILABILITY STANDARDS as set out in the Project Agreement are met in full.
Amber	Evidence of partial compliance - some of the relevant Project Requirements and AVAILABILITY STANDARDS as set out in the Project Agreement are met; however, issues were noted that mean it does not meet all of the Relevant Project Requirements. Actions will be necessary to address the deficiencies noted.
Red	Limited or no information of compliance, or the basic requirement is not being met. Systems, procedures and/or control measures are not functioning as designed and/or will have an impact on either statutory compliance and/or relevant Project Requirements and AVAILABILITY STANDARDS as set out in the Project Agreement. Action is required in order to demonstrate compliance.
Grey	System, service or requirement is not applicable to the site or the relevant Project Requirements and AVAILABILITY STANDARDS as set out in the Project Agreement.

    1. The Surveyor shall provide the Authority with its proposed templates and methodology for the Condition Survey, the Compliance Audit and the Environmental Condition Audit, taking full account of the list of standards agreed with the Authority. The Surveyor’s proposed templates and methodology shall address each of the items listed in the Availability Standards and be consistent with recognised surveying practices that are commensurate with the intended purpose of the Condition Survey, Compliance Audit and the Environmental Condition Audit.
    1. The Surveyor shall meet with the Authority to discuss the proposed templates and methodology for the Survey, the Compliance Audit, and the Environmental Condition Audit and agree any amendments or additions. If requested, the Surveyor shall participate in the following activities with the Authority:
      1. A meeting to discuss and agree:
        1. the practical application of the Condition Standard for use in the Survey (“Condition Standard Interpretation Guide”);
        1. the practical application of the Compliance Standard for use in the Compliance Audit (“Compliance Standard Interpretation Guide” which shall include Environmental Standards Compliance Guide);
      1. A pilot survey to assess the suitability of templates, methodology, the Compliance Standard Interpretation Guide and Condition Standard Interpretation Guide to be implemented in the Survey. The Authority may participate in the pilot survey process.
    1. Following completion of the above, the Surveyor and the Authority shall agree the templates, methodology, the Compliance Standard Interpretation Guide and Condition Standard Interpretation Guide prior to commencement of the Survey, Compliance Audit and the Environmental Condition Audit.
  1. Condition Survey
    1. In preparing the templates, methodology, Condition, Compliance and Environmental Standard Interpretation Guides for use in the Survey, the Surveyor shall adopt the following principles:
      1. The Survey shall be a comprehensive, condition, compliance and environmental survey as described herein. The facilities to be surveyed shall be determined from the existing Accommodation Schedule and any additional information taken from the available project data;
      1. Subject to any specific requirements of this agreement, the Survey shall be non-intrusive and shall not include the following (unless instructed by the Authority, in which case the carrying out of such activities shall form Additional Services):
        1. Physical dismantling;
        1. Destructive Opening-up requiring subsequent repairs;
        1. Disruptive investigations;
        1. Survey subjects which are: covered, unexposed or inaccessible; (although the surveyor will be expected to access roofs where condition cannot be determined from a vantage point. Pole or drone surveys should be considered)
        1. Any form of physical or material testing or analysis;
        1. Validation of the combustibility, surface spread of flame characteristic or similar Building Regulation compliance of cladding panels or any other materials in the buildings;
        1. Structural engineering appraisal of the building; (aside from identifying structures of concern)
        1. Inspection of cavity or other restraint wall ties or structural connections which by their nature are built into the construction and not visible without a measure of disruptive works;
        1. Design audit, asbestos survey, any underground services inspections (save for where expressly included in this specification or agreed between the Authority & the Surveyor), environmental or nature audit or exploration for the incidence of Japanese knotweed;
        1. Investigation into seepage pollution or contamination of any kind in, on, or around the assets, or which may affect the subject of Survey;
        1. Re-measurement of the facilities;
        1. Full timber inspection (only a statement that parts or services are free from rot, beetle, contamination, corrosion or other similar defects); visual inspection only is expected unless further testing is advised.
        1. Investigation into the unsuitable use of high alumina cement or calcium chloride, calcium silicate brickwork, calcium silicate reaction in concrete, wood wool slabs used as permanent shuttering, cavity wall tie failure, radon gas seepage, or other materials considered as deleterious in construction, except insofar as such matter may come to knowledge in the normal course of inspection of the materials and state of repair;
        1. Full access and itemised fire-stopping inspections; visual inspection only is expected unless further testing or inspection is advised.
        1. Sample or analysis of the sulphate content of the load bearing sub-soil adjacent to the foundations, or enquiries as to general ground conditions;
        1. Environmental Risk Assessments or Flood Risk Assessments;
        1. Written enquiries in respect of existing user rights, proposed use, town planning and road widening, legal interests, prescriptive rights, easements, wayleaves or statutory consents;
        1. Disability Access Audit pursuant to the Disability Discrimination Act 2005.
      1. The level of asset capture shall be room-by-room, to NRM 3 level 4 maximum (unless reduced and agreed by the Authority after discussion with the Surveyor) including external areas and ancillary buildings comprising each dwelling with comprehensive coverage versus the Accommodation Schedule in order to test the condition, compliance and environmental standards in the Project Agreement, including the Schedule 1 Availability Standards. For the CONDITION SURVEY to the Surveyor shall undertake a visual appraisal only of the following:
        1. Building fabric
        1. Mechanical ventilation
        1. Electrical systems
        1. Gas systems
        1. Lighting
        1. Fire and passive fire protection including fire stopping
        1. Wall, floor, ceiling finishes
        1. Doors
        1. Windows, condition. (See also Section 5 below)
        1. Internal glazing
        1. External visible parts of buildings including roofs
        1. Ancillary buildings within the demise, garages, sheds etc. as separately listed
      1. The Survey templates shall provide for the following outputs:
        1. MS Excel data file (or such other means agreed between the Authority and the surveyor)
        1. Photographic record of each element considered to be Non Compliant, ie a “Fail” Photographs shall be taken in a manner that enables the full extent of the defect(s) to be evident. All photographs shall be uniquely named with the rectification works reference number followed by a unique identifier based on the dwelling unique identification number. This will be used to identify the item and used to compare with the repaired item for checking and sign off by the surveyor as required by Specification Section 9 below.
        1. Asset description and Location (per room and per dwelling) where a Non Compliant element is noted, ie one that doesn’t comply with the Project Agreement.
        1. Condition score (by reference to the Condition Standard and Condition Standard Interpretation Guide) Compliant or Non-Compliant.
        1. Known / estimated asset age (whole years) and likely remaining life (over 30 years) in view of condition of only main elements and services. (List to be agreed with the Authority prior to surveys)
        1. Manufacturer, make and model of services items, eg lifts, (where readily available and within survey scope)
        1. Backlog Costing per dwelling/building: The Survey shall include the Surveyor’s assessment of the backlog maintenance costs of all assets, systems, areas and their sub-elements where they are found to be Non-Compliant and have thereby created a Fail Event as described in the Project Agreement and schedules (Including Annex 1 to the Output Specification that sets out details of the Availability Standards Rented and the Availability Standards Leasehold).
    1. The Surveyor shall undertake the Survey of the Facilities in accordance with the templates, methodology, the Condition Standard and Condition Standard Interpretation Guide agreed with the Authority.
    1. A general photographic record shall be made of each tenanted room, common parts and external elevations for record purposes only, (excluding any individual person from photos).
    1. A record of the security access provisions and equipment in place for each converted street property or purpose built block containing more than one dwelling.
    1. Hazards and concerns - During the site Survey, the Surveyor shall immediately notify the Authority of any matters which, in the reasonable opinion of the Surveyor, represent a material or imminent risk to the health and safety of staff, occupants or visitors including, without limitation, notifications required under the RICS Surveying Safely / HSAWA Duty of Care.
      1. The Surveyor should be aware that they are visiting people’s homes and should act accordingly. The Surveyor shall note during each survey any potential vulnerabilities including matters that raise their concerns such as hoarding, tenant created fire risks, self-neglect, isolation, properties not being heated, or potential mental health issues. Where the concern is such that the Surveyor is uncomfortable continuing with the survey, the surveyor should leave the premises and the concerns should be reported by email to the Authority within 24 hours so that alternative arrangements for the survey can be arranged. This will then be treated as a “No Access” visit.
      1. The Surveyor shall otherwise make 3 physical attempts to gain access by calling at the dwelling before treating the dwelling as a “No Access”.
      1. In addition to the above the Surveyor should note signs of potential illegal subletting such as subletting signs, locks on internal doors/extra fridges etc., which should be included with the submission of the condition element of the Survey Reports.
      1. For the avoidance of doubt, the Authority shall be responsible for the notification of such matters to the Helpdesk (as defined in the Project Agreement).
    1. The Surveyor shall issue the following to the Authority: the completed “Survey Reports” on at least a monthly basis, all completed reports shall comprise:
      1. The report per building, per street property subdivided into flats/dwellings or per purpose-built block of flats along with any associated ancillary buildings;
      1. The Condition Appraisal, showing Compliant or Non-Compliant;
      1. The Surveyor’s recommendations in accordance with paragraph 7, Further Investigation.
    1. The Surveyor shall meet with the Authority to discuss the findings of the Survey Reports and agree any further action to be taken in respect of the Survey process (including any Additional Services or other action to be taken as a result of the Survey Reports). Meetings shall be via Teams unless otherwise agreed.
  1. Compliance Audit
    1. The surveyor shall undertake a compliance audit against the compliance availability standards as set out in the Project Agreement, including those in Schedule 1 Availability Standards. This should include the following:
      1. Facilities compliance with availability standards Common parts
      1. Safe electrical systems site visual and desktop review of records
      1. Temporary heating and review of records
      1. Safe gas systems site and desktop review of records
      1. Windows - visual
      1. Heating including measurement and calculation. See Availability Standards
      1. Water supplies - visual and measurement
      1. Kitchen facilities visual, desktop and measurement
      1. Bathroom facilities - visual, desktop and measurement
      1. Lighting visual and simple measurement
      1. Ventilation kitchen & bathroom mechanical extracts visual and simple measurement by handheld anemometer where required.
      1. Current SAP (EPC) ratings, SAP compliance & average calculation. An accredited assessor isn’t necessary as only an approximate rating is required but SAP software will be needed. The required standard is 70 (C). Only where the score is 60 or below will an accredited assessor be required as an additional service.
      1. Utilities supply systems - visual
      1. Drainage systems - visual
      1. Internal & external finishes
      1. Access availability
      1. Safety and security visual and desktop.
      1. Statutory obligations including asbestos management provisions.
Only the last 3 years of records need be reviewed. Also see Availability Standards for the above items as these show the simple nature of the requirements. The Authority does not require British Standard measurements. The above requirements relate directly to the Availability Standards appended to this Specification which should be read and understood and agreed with the Authority as part of the survey templates. The Authority surveyors will work with and assist the Surveyor to understand the Project Agreement documents during mobilisation and beyond.
    1. In addition, the Surveyor shall undertake a review of asset data, lifecycle activities and PPM activities undertaken over the last three (3) years. In preparing the templates and methodology and Compliance Standard Interpretation Guide for use in the Compliance Audit, the Surveyor shall adopt the following principles:
      1. The Compliance Audit shall assess the asset data, lifecycle activities and PPM systems in place, comment on the management of
        1. health and safety; and
        1. statutory compliance and
        1. application of lifecycle funds and provide recommendations on past activities and any actions to be taken to achieve compliance with the Project Requirements;
      1. The Compliance Audit templates shall provide for the following outputs in respect of all mechanical and electrical, and building fabric assets:
        1. Compliance requirement and reference desktop study
        1. Identifier: routine, statutory or mandatory desktop study
        1. Observation on site
        1. Compliance score (by reference to the Compliance Standard and Compliance Standard Interpretation Guide)
        1. Actions and recommendations in the event of non-compliance
    1. The Surveyor shall undertake the Compliance Audit in accordance with the templates and methodology, the Compliance Standard and the Compliance Standard Interpretation Guide agreed with the Authority.
    1. In carrying out the Compliance Audit, the Surveyor shall immediately notify the Authority of any matters which, in the reasonable opinion of the Surveyor, represent a material or imminent risk to the health and safety of staff or visitors (including, without limitation, notifications required under the RICS Surveying Safely / HSAWA Duty of Care or statutory breach). For the avoidance of doubt, Authority shall be responsible for the notification of such matters to the Helpdesk (as defined in the Project Agreement).
    1. As soon as reasonably practical and in any case within 28 days of completion of each Compliance Audit or such other date agreed with the Authority, the Surveyor shall issue their reports on the Asset Register Review, the PPM Scheduling Review and the Lifecycle Review to the Authority (the “Audit Reports”).
    1. Housing Health and Safety Rating System (HHSRS). The Surveyor shall note and report on any Category 1 hazards affecting the dwelling. Any such hazards noted should be noted as a “Fail” or “Non-Compliance”.
    1. The Surveyor shall meet with the Authority to discuss the findings of the Audit Reports and agree any further action to be taken in respect of the Compliance Audit process (including any additional audit or other action or remedial work to be taken as a result of the Survey Reports).
  1. Environmental Condition Audit
    1. The Surveyor shall, via survey and measurement, validate the environmental conditions within all areas of the facilities against Project Requirements. The Surveyor’s Method Statement shall detail the templates and methodology in respect of each environmental parameter, which the Surveyor proposes to adopt in order to achieve this outcome.

    1. The following principles shall be adopted for the validation process against Schedule 1 Availability Standards:
      1. Any test shall be conducted by competent operatives using appropriately calibrated equipment e.g. digital thermometer, airflow vane anemometer, etc. The test does not require formal British Standard testing conditions to be created; The Surveyor shall read and understand the standards as set out in the Availability Standards.
      1. Testing will be conducted under normal operating conditions (i.e. without disruptive testing set-up);
      1. Base Test Standard validation shall have a binary outcome when measured against the Project Availability Standards;
        1. Tests that Pass – i.e. achieve or exceed the Availability Standard will be deemed compliant and noted as a “Pass”.
        1. Tests that Fail – i.e. fail to achieve the Availability Standard will be deemed non compliant and noted as a “Fail” and appropriate remedial action shall be recommended, the scope of which shall be dependent on the nature and circumstances of the failure. Where a test fails by less than 10% of the target, it should be noted as such but no remedial action will be necessary.
    1. The Surveyor shall undertake the Environmental Condition Audit of the Facilities in accordance with the templates and methodology agreed with the Authority.
    1. In carrying out the Environmental Condition Audit, the Surveyor shall immediately notify the Authority of any matters which, in the reasonable opinion of the Surveyor, represent a material or imminent risk to the health and safety of staff, patients or visitors (including, without limitation, notifications required under the RICS Surveying Safely / H&SAWA Duty of Care). For the avoidance of doubt, the Authority shall be responsible for the notification of such matters to the Helpdesk (as defined in the Project Agreement).
    1. As soon as reasonably practical and in any case within 28 days of completion of the Environmental Audit, the Surveyor shall issue a report detailing the findings of the Environmental Condition Audit to the Authority (the “Environmental Condition Audit Report”).
    1. The Surveyor shall meet with the Authority to discuss the findings of the Environmental Condition Audit Report and agree any further action to be taken in respect of the Environmental Condition Audit process (including any additional survey, audit remedial or other action to be taken as a result of the Environmental Condition Audit Report).
  1. Further investigation
    1. In addition to the reporting requirements set out above in relation to the Survey Reports, Compliance Audit Reports and Environmental Condition Audit Report, the Surveyor shall provide recommendations for any further investigative action to be taken, which may include:
      1. Undertaking no further action in respect of a particular sample;
      1. Undertaking more targeted review of particular issues; and/or
      1. Such other action as the Surveyor considers appropriate to ensure that the Facilities comply with and can be reasonably demonstrated to comply with the Project Requirements
    1. The Surveyor shall meet with the Authority on a regular basis to discuss the findings reported to date and any recommendations made and agree the further action to be taken. Such action shall be Additional Services and shall be completed prior to issue of the Final Report.
    1. Not used
  1. Report and Recommendations
    1. The Surveyor shall provide the Authority with the Survey Reports on a monthly basis as programmed by the Surveyor.
    1. The Survey Report shall, in addition to the specific requirements set out above:
      1. include full details of the findings of the completed Condition Survey, the completed Compliance Audit and the completed Environmental Condition Audit for each of the separate dwellings surveyed and recommend any additional survey and/or audit activities recommended;
      1. provide a summary table confirming the level of compliance of each asset, by reference to:
        1. In the case of the Condition Survey findings, by reference to the Condition Standard and Condition Standard Interpretation Guide, being deemed compliant (Pass) or non-compliant, (Fail) all as set out in Clause 2.3 above, along with
        1. In the case of the Compliance Audit findings, by reference to the Compliance Standard and the relevant Compliance Standard Interpretation Guide, Grade “Green” being deemed compliant and Grades “Amber” and “Red” being non-compliant; and
        1. In the case of the Environmental Condition Audit, on a pass or fail basis, with “pass” being deemed compliant and “fail” being non-compliant.
      1. identify the existence of any non-compliance of the Contract Data or the Facilities with the Project Requirements;
      1. maintain an Excel based live record of recommendations and the remedial actions to be taken in respect of any Fail or non-compliance identified (“Remedial Actions”); Each Remedial Action shall be classified as follows
         The status of each Remedial Action identified in the Excel Survey Report, to be classified as:
        1. Completed;
        1. Urgent (eg category 1 Hazards, damp & mould, safety issues etc to be completed within the time period set out in the Availability Standards table.
        1. Semi Urgent to be completed within 3 months
        1. Included in planned works to be completed within 12 months (provided the Remedial Action has been identified in a list of Remedial Actions which the Authority has agreed are suitable to be undertaken as planned works);
        1. The long-stop period for completion is 1st February 2027.
           and
      1. recommend the processes and procedures to be adopted in the future up to Contract Expiry to ensure that the Facilities are maintained in accordance with the Project Requirements following the completion of the Remedial Actions and that assets are handed back to the Authority in the required condition.
    1. The Surveyor shall meet with the Authority and, if required by the Authority, to discuss the findings and recommendations of the Survey Report and address any queries or observations which the Authority may raise. The Surveyor shall subsequently update and re-issue the Survey Report as a Final Survey Report, taking reasonable account of any queries and observations raised by the Authority. The Final Report will include a full schedule of outstanding Remedial Actions with associated costs of these and proposed timescales for remediation.
    1. The Surveyor may upon written acceptance of these Survey Report/s, issue a monthly statement of percentage completion of Condition reports using the Pricing Schedule, for agreement by the Authority upon which any subsequent invoice shall be based in accordance with the Surveyor Appointment. This shall include a note of “No Access events” (following 3 date recorded attempts to gain access) which shall be invoiced at 25% of the value of the Average Survey Cost Per Dwelling. Interim completed survey reports issued on a monthly basis should include all reporting requirements for each dwelling if they are to be included in the number of reports on which any interim invoice is based.
  1. Remediation checks and close out of Remedial Actions
    1. If required by the Authority, the Surveyor shall, provide advice and assistance to Project Co and its contractors with a view to ensuring the Remedial Actions are carried out in order to fully remedy the “Fail” and non-compliance elements identified. Such advice and assistance shall be limited to providing further explanation of the non-compliances identified and the Remedial Actions required as Project Co and its contractors may reasonably require to enable the Remedial Actions to be implemented within the given timeframe. The Surveyor shall inform the Authority of the advice and assistance provided to Project Co and address any queries or comments raised by the Authority.
    1. The Surveyor shall check and confirm the completion of all remedial work as it arises and at least within 28 days of the report that such works are completed, either by visual site check, checking of completion documents (commissioning reports, inspection certificates, completion certificates) or by photographic proof. At least 40% of these checks shall be by surveyor site visit and no more than 60% by photographic evidence provided by the FM contractor or SPV, which evidence must be sufficient to confirm the correct remediation such that the building element meets the standards required by the Project Agreement and Availability Standards. For bid pricing purposes the Surveyor should assume that 20% of the dwellings fail and require remedial works. The Surveyor shall maintain a master data set that records all completed and not completed work and shall at least monthly issue a “Completion Report”) detailing the following:
      1. The status of each Remedial Action identified in the Interim Summary Report, in a form agreed by the Authority to be classified as:
        1. Completed;
        1. Incomplete Urgent (eg category 1 Hazards, damp & mould, safety issues etc to be completed within 28 days, with target completion dates.
        1. Incomplete Semi Urgent to be completed within 3 months, with target completion dates.
        1. Incomplete Included in planned works with target completion dates (provided the Remedial Action has been identified in a list of Remedial Actions which the Authority has agreed are suitable to be undertaken as planned works, such list to be confirmed to the Surveyor by the Authority); or
        1. Open, with target completion dates. Long-stop date is 3/6/2027.
      1. The Surveyor’s further recommendations (if any) in respect of the completion of the Remedial Actions and future processes and procedures to be adopted to ensure the future compliance of the Facilities with the Project Requirements.
      1. The Surveyor shall review all Remedial Action works as listed in 8.2(a) above when claimed as being completed and confirm satisfactory completion of same by means of a Final Report encompassing all dwellings and assets.
  1. General Services
    1. If at any stage the Surveyor becomes aware of any circumstances which will or might prevent it from carrying out the Surveyor's functions adequately or at all, or which will or might compel the Surveyor to give any notice to any person, except where such notice is dealt with elsewhere in the Agreement, the Surveyor shall notify the Authority in writing as soon as possible and consult with the Authority as to the measures to be taken to resolve such matter by the most appropriate means.
    1. The Surveyor shall make recommendations if and as appropriate as to the need to appoint any specialist consultants to carry out any specialist design, analysis, calculations or testing, in order to ensure that the Contract Data and Facilities comply with and can be demonstrated to comply with the Project Requirements.
    1. The Surveyor shall attend project meetings whenever reasonably requested to do so.

APPENDIX 2
# The Facilities

The Schedule of Accommodation/property list is provided as a separate Excel file (Appendix 2 The Facilities (PLO82 Property List 010424 to 310325 Combined) V2 11-3-2025) which the Surveyor may use as the basis for pricing, data collection and reporting.

APPENDIX 3

ANNEX 1
OUTPUT SPECIFICATION
AVAILABILITY STANDARDS
Part 1 – Availability Standards (Initial)

All standards must be satisfied to achieve certification of the Availability Standard (Initial) for Rented Dwellings and Leasehold Dwellings; an indication is given on a yes/no (Y/N) basis of the standards which need to be satisfied to achieve the relevant Availability Standards (Initial). Failure Events (as defined in the tables below) which are not applicable to either the Availability Standards Leasehold (Initial) or Availability Standards Leasehold (Full) are indicated as such (N/A).

#### CERTIFICATION REQUIREMENTS
Ref	Certification Requirements	Indication of Failure Event (not exclusive)	Availability Standards Rented (Initial)	Availability Standards Leasehold (Initial)
General
A	Every Dwelling to be fit for human habitation, free from disrepair and structurally sound, wind and weather tight / Specifically every existing Dwelling in the PFI Area should be: / Free from serious disrepair of a type which could be the subject of a Disrepair Action, / Structurally stable, / Free from penetrating dampness prejudicial to the health of the occupants, / Have adequate provision for heating ventilation and lighting, / Have an adequate supply of wholesome water, / Have an effective system for the drainage of foul, waste and surface water, / Have a suitable located WC for the exclusive use of the occupants, / Have a bath OR shower AND wash hand basin with a satisfactory supply of hot and cold water, / Have satisfactory facilities for the preparation and cooking of food including a sink with a satisfactory supply of hot and cold water.	Properties which are certified as unfit will fail to meet the one or more items in the list of specific criteria opposite.	Y	Y

Ref			Certification Requirements		Indication of Failure Event (not exclusive)	Availability Standards Rented (Initial)	Availability Standards Leasehold (Initial)
Common Parts
B1		All Common Parts to be maintained free from hazards including, stairs, banisters and balustrades which will be secure and free from damage, decay and trip hazard.		Staircases: damage, decay or trip hazard to floorings, stairs, banisters and balustrades are likely to present a serious health and safety risk.		Y	Y
B2		All fixtures and fittings will be securely and safely installed. / Note: this clause will not apply to anything installed by Leaseholders or Tenants.		Fixtures & fittings: insecure fixtures which could pose a serious health and safety risk.		Y	Y
B3		Passenger lifts shall be fully operational unless refurbishment works are being carried out (when minimum 48 hours notice will be given to Leaseholders or Tenants), or when alternative arrangements will be made for access or where more than one lift is available.		Lifts: lift failure when occupied. Failure to release trapped occupants in less than 2 hours from when report is received by Helpdesk.		Y	Y
				Non-operation of lifts except where minimum 48 hours prior notice has been promulgated to Leaseholders and Tenants.		Y	Y
	Electrics
	C1	Maintain safe electrical distribution systems. (“Safe ” shall be deemed to be tested and confirmed to be in compliance with latest edition of IEE Regulations.)		Failure to provide safe electrical systems and/or maintain such systems in operational condition.		Y	N/A

 Availability Standard (Initial) Reference:

Building Requirements

Ref	Certification Requirements		Indication of Failure Event (not exclusive)	Availability Standards Rented (Initial)	Availability Standards Leasehold (Initial)
Heating AND HOT WATER
D1	Provision for temporary rectification to heating failure events must be made by the Contractor to any Dwelling in which the main source of heating is incapable of meeting the standards set out above for 2 hours or more and there is no operable secondary source of heating (i.e. appliances or systems capable of raising the internal temperature to a minimum of 21 degrees Centigrade and maintaining it thereat) to at least to one living room (i.e. a room that is not the kitchen, bathroom, bedroom, storage or corridor area).	Failure to provide temporary rectification where no other form of heating is available within the Dwelling.		Y	N/A
Incoming Services
E1	GAS SERVICES / Gas systems to be maintained checked and certified in accordance with good practice and Gas Safety (Installation and Use) Regulations. The Contractor to carry out any necessary improvements and repairs to ensure continued safe use.		Non compliance with the Gas Safety (Installation and Use) Regulations. / Failure to carry out safety check where suspected presence of unsafe gas installations is reported.	Y / Y	N/A / N/A

Part 2 – Availability Standards (Full) and Availability Standards (Garages)

Availability Standards (Full) Reference:	1
#### Building Element/Service: Windows

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
1.1	Windows	Windows at first floor level and above shall be fitted with a means of restricting opening to prevent accidental falls.	Lack of means of restricting opening to upper floor windows.	3 days		Y	Y
1.2		All existing Dwellings which are / not in Conservation Areas (meaning an area within the PFI Area where there is for the time being an Article 4 (2) Direction in force) and / do not have existing sealed unit double glazing / shall be fitted with sealed unit double glazing subject to the approval of the local planning authority.	Lack of sealed units to new windows except where the local planning authority has expressly not approved double glazed windows and existing has been repaired.	21 days	.	Y	Y
1.3		All Dwellings which are located within Conservation Areas and other areas within the PFI Area as may be designated by the local planning authority shall have replacement or improvements to existing windows agreed by the Authority’s officers responsible for Conservation Areas or planning.	Lack of suitable double glazed windows with effective draught proofing except where local planning authority has expressly not approved double glazed windows and existing has been repaired.	21 days		Y	Y
1.4		Glazing below 800mm shall be in safety glass to reduce the risk of injury.	Glazing below 800mm fails BS6206.	21 days		Y	Y

Availability Standards (Full) Reference:	2

Building Element/Service:	An operational, fuel-efficient heating system that consistently meets these standards.

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
2.1	The system must be capable of independent operation from the water heating system.		Heating system cannot be operated independently from the water heating system.	21 days.	Part. L1 Building Regulations / Insulation to BS 5422:2001	Y	N
2.2	The Dwelling heating system shall be capable of reaching the required internal room temperatures from cold within 45 minutes of heating installation being started.	When the external air temperature is -1°C or above, the system must achieve the following heating standards within 1 hour of heating installation being started: / Halls 18ºC / Kitchens 18ºC / Bedrooms 18ºC / Bathrooms 22ºC / Dining rooms 20ºC / Living rooms 21ºC	One or more rooms do not achieve the defined temperatures (as measured by a thermometer 1.5 m above finished floor level at the centre of the room) within the time allowed with windows and doors to the rooms closed.	21 days.		Y	N
2.3		All heating pipes and ducts (where practicable) must be insulated.	Absence of insulation to pipes except where exposed pipes contribute directly to heating habitable rooms.	21 days.		Y	N
2.4	Tenants should be able to exercise control over the heating system on both a “whole house’ and a room-by-room basis.	All newly installed heating systems must be fitted with zone and timing controls and boiler control interlocks	Inability of tenants to control system on a room-by-room basis.	21 days.		Y	N
2.5	Where a fixed source of heat is provided in the main living area this must be capable of operation independent from the main Dwelling heating system.		Non-provision or non-operation of the fixed source of heat.	21 days.		Y	N

Full Availability Standard Reference:	2 (Continued)

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
2.6		Provision for temporary rectification to heating failure events must be made by the Contractor to any Dwelling in which the main source of heating is incapable of meeting the standards set out above for 2 hours or more and there is no operable secondary source of heating (i.e. appliances or systems capable of raising the internal temperature to a minimum of 21 degrees Centigrade and maintaining it thereat) to at least to one living room (i.e. a room that is not the kitchen, bathroom, bedroom, storage or corridor area).	Failure to provide temporary rectification where no other form of heating is available within the Dwelling.	12 hours		Y	N

Availability Standards (Full) Reference:	3

Building Element/Service:	Hot and cold water supply system.

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
3.1	All Dwellings must have hot and cold water supplies.	The water distribution system will have sufficient capacity throughput to provide hot and cold water at all outlets simultaneously without flow starvation.	Insufficient capacity of system. / There shall be no failure event if the statutory undertaker reduces water pressure to less than the current statutory minimum of 1bar	21 days.		Y	N

3.2		Hot water temperature will be capable of tenant control.	Inability of system to provide for user control of temperature.	21 days.		Y	N
3.3	All Dwellings must have mains fed drinking water supplies in adequate quantities.	There will be a continuous supply of drinking water at all times.	Failure to provide continuous supply (other than where failure of supply is established as the fault of the statutory undertaker). / There shall be no failure event if the statutory undertaker reduces water pressure to less than the current statutory minimum of 1bar.	Provide a provision for drinking water within 2 hours. Restored to Dwellings within 24 hours.		Y	N

Availability Standards (Full):	3 (Continued)

Building Element/Service:	Hot and cold water supply system.

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
3.4	All water heaters fuelled by gas, oil or coal (where fitted) must have adequate air supplies.	HOT WATER / Every Dwelling to be provided with domestic / hot water at all appropriate outlets as follows: / Where provided from a storage system, the / delivery of at a stored water temperature of / 60°C. The stored water heating system shall / provide a maximum recovery from ambient / external temperature to 60° Centigrade of 45 / minutes. A minimum delivery of 12 litres per / minute at a temperature of at least 44° / Centigrade to a 20mm diameter tap outlet or / 6 litres a minute at a temperature of 41° / Centigrade to a 12mm diameter sink tap / outlet. Sizes of hot water tanks shall be as follows: / 1 Bedroom Dwelling: 100 litres / 2 Bedroom Dwelling: 120 litres / 3 Or more bedroom Dwelling: 135 litres / Where hot water is provided by a combi / system, a minimum delivery of 12 litres per / minute at a temperature of at least 44° / Centigrade to a 20mm diameter tap outlet or / 6 litres a minute at a temperature of 41° / Centigrade to a 12mm diameter sink tap / outlet.	Failure of system to provide hot water at the temperature required and in the time allowed.	24 hours where no hot water or water is provided at over 41 degrees Centigrade at any outlet. / 21 days any other failure	Part. J Building Regulations	Y	N

3.5		Where installed, all hot water storage systems must be capable of delivering in sufficient quantities to fill a bath with a recovery period of 45 minutes.	Failure to provide alternative means where appropriate.	21 days.		Y	N
3.6		The water heating system should be capable of independent operation from the space heating system.	Inability of system to be used independently of and/or in conjunction with space heating.	21 days.		Y	N

Availability Standards (Full) Reference:	4

Building Element/Service:	Kitchen Facilities

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
4.1	All Dwellings must be fitted with adequate facilities within the confines of the existing Dwelling for the preparation and storage of food.	Provide kitchen storage units, food preparation areas, sink unit and service connections for kitchen appliances.	Non-provision of any or all of: kitchen storage units, food preparation areas, sink unit, service connections to kitchen appliances.	21 days.	A Decent Home (2002) / Part F of Building Regulations (Ventilation)	Y	N
4.2	All kitchens must have adequate provision for the size of Dwelling, except that no kitchen shall require structural alterations to enable it to be extended.	Whenever possible kitchen layout and design will provide space for cooker, fridge/ freezer dishwasher and washing machine.	Poorly planned defines as – “normally, where the distances between cooker, refrigerator and sink do not exceed 2m in a Contractor refurbished kitchen layout,” and/or non- provision of space for: / cooking, / cold storage of food and washing.	21 days.		Y	N
4.3	All kitchens must have washable surfaces capable of being maintained in a clean and hygienic condition. Wall tiles to splashbacks of not less than 300mm high.		Contractor refurbished kitchen that does not have washable surfaces or can be maintained in a clean and hygienic condition e.g. missing sealant between wall and work surfaces. Tiled splashbacks less than 300mm high where possible.	21 days.		Y	N
4.4		Mean of mechanical extraction of moisture from kitchens capable of providing at least one air change per hour.	Absence of extractor fans or other means of rapid moisture dispersal to provide minimum one air change per hour in a kitchen where such a provision is practical. Except where it is agreed by the Independent Certifier that the kitchen will not be refurbished or means of mechanical ventilation is impractical to install.	3 days.		Y	N

Availability Standards (Full) Reference:	4 (Continued)

Building Element/Service:	Kitchen Facilities

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
4.5		All kitchen fixtures and fittings must be robust, well maintained and modern. ‘Modern’ is defined as being no more than 20 years old.	Failure to provide fixtures, fittings that are robust, well maintained and ‘modern’ save that the Contractor will not be required to install lockable cabinets or child-proof catches.	21 days.		Y	N
4.6		Kitchens must include an independent electrical cooker power supply.	Failure to supply independent electrical cooker supply.	21 days.		Y	N

Availability Standards (Full) Reference:	5

Building Element/Service:	Bathroom Facilities

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
5.1	All bathrooms must be modern, well maintained and have a working: / bath (with mixer taps and shower attachment) wash hand basin, WC, WC and rinse hand basin in separate WCs ‘modern' is defined as being no more than 30 years old and not in poor condition. / Note: scope of work excludes towel rails, toilet roll holders, mirrors, shelves and medicine cupboards.	Capable of allowing showers and being waterproof. / Note the Contractor will not be responsible for the satisfactory function of showers over baths (mixer tap supplied) where operation is dependent upon existing location of header tanks or statutory undertaker’s supply pressure.	Required sanitary ware not provided and /or non-operational (including blockages and overflows). / Sanitary ware in poor condition and over 30 years old.	Blockages 24 hours / 21 days for replacing sanitary ware. / Clean water overflows 3 days.	To comply with Part F (Ventilation), G (Hygiene) & H (Drainage) of the Building Regulations. / A Decent Home (2002)	Y	N
5.2	All bathrooms must have wired extractor fans with door or light operated power control.	Energy efficient ventilation system.	No energy-efficient ventilation system or system non-operational.	21 days.

Availability Standards (Full) Reference:	6

Building Element/Service:	Gas Installations

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
6.1	Gas installations to be maintained in accordance with gas regulations.		Non-compliance with Statutory Regulations.	21 days.	Compliance with Gas Safety, (Installation and Use) Regulations 1998.	Y	N
6.2			Failure to carry out safety check where the presence of unsafe gas installations is suspected reported to Helpdesk.	24 hours.
6.3	Necessary improvements and repairs to be carried out to ensure continued safe use.	Gas installation should be maintained to a safe standard and in good working order.	Failure to carry out necessary repairs/improvements.	21 days.	Part L1 & L2 of the Building Regulations.	Y	N

Availability Standards (Full) Reference:	7

Building Element/Service:	Electrical Installations

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
7.1	Electrical distribution systems shall be safe and maintained.	Authority’s fixtures and fittings to be maintained in full working order.	Failure to provide safe systems and/or maintain systems.	21 days.	Current IEE Regulations	Y	N
7.2			Electrical installations not modern i.e. more than 25 years old and in poor condition.	21 days.		Y	N
7.3			Smoke and or heat detectors not electrically wired or over 25 years old and in poor condition.	21 days.		Y	N
7.4		Mechanical and electrical installations (lifts & fittings).		21 days		Y	N
7.5	Future renewals to comply with prevailing IEE Regulations and Regulations under the Electricity Acts.	All electrical fittings and wiring should be in good working order and meet current standards and regulations.	Fittings do not comply with current Regulations or over 25 years old and are in poor condition.	21 days.		Y	N
7.6	Electrical distribution systems shall be safe and maintained.	Maintain safe and modern electrical distribution systems. (“Safe and Modern” shall be deemed to be / (a) tested and confirmed to be in compliance with latest edition of IEE Regulations); and / (b) having wiring and fittings not exceeding 25 years old and where the system requires replacement or major repair.	Failure to provide safe electrical systems and/or maintain such systems in an operational condition.	1 day.		Y	N

Availability Standards (Full) Reference:	7 (Continued)

Building Element/Service:	Electrical Installations

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
7.7	Electrical distribution systems shall be safe and maintained.	Socket outlets and switches will be position so as to be safe (as defined above) and not concealed behind permanent fittings or fixtures. The minimum numbers of single socket outlets in each Dwelling will be not less than: / Kitchen - 6No outlets plus fused spurs for refrigerator, cooker and washing machine / Bathroom - NIL / Living Areas - 4No outlets / Hallways - 1No outlet at each floor level. / Bedrooms - 3No (main) 2No (other bedrooms) / Dining room - 2No outlets / For the avoidance of doubt the Contractor will not be required as part of this output to ensure that existing fittings and switches comply with the Disability Discrimination Act 1995 requirements of Tenants.	Insufficient socket outlets or concealed socket outlets and/or switches.	3 days		Y	N

Availability Standards (Full) Reference:	8

Building Element/Service:	Lighting

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
8.1	All Dwellings must have adequate provision for lighting / Note: Where windows do not have adequate provision for natural light (as defined by Building Regulations) the Contractor will not be required to make structural alterations to increase the size of any windows.	Light fittings to all habitable and non-habitable rooms to comply with current IEE Regulations. The following minimum numbers of pendant light fittings will be provided: / Habitable rooms less than 18 m2: 1No / Habitable rooms / Common areas` and hallways: 1 no per landing / Other rooms; 1 No	Natural light inadequate. / Less than number of operational pendant light fittings.	10 days	Current IEE Regulations	Y	N

Availability Standards (Full) Reference:	9

Building Element/Service:	Ventilation

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
9.1	The extraction of moisture from kitchens and bathrooms.	Bathrooms and kitchens are fitted with a system of moisture extraction and heating that will keep the walls free of condensation damage and/or mould growth.	Presence of condensation and/or associated damage and/or mould growth unless such growth is demonstrably failure on the part of the tenant to ventilate and heat the room.	21 days.		Y	N
9.2	The requirements of fuel burning and other appliances can be met.	Fuel burning appliances must have ventilation that meets current regulations and standards.	Ventilation requirements of installed appliances not met.	21 days unless it warrants an appliance unsafe then 24 hrs.		Y	N

Availability Standards (Full) Reference:	10

Building Element/Service:	Energy Efficiency

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
10.1	All Dwellings within the PFI Area will, on average, meet the SAP 70 rating as a minimum.	Individual Dwellings will meet SAP 70 rating wherever practical using NHER or other accredited software. / “Wherever practical” in this output will be deemed to mean undertaking any insulation work except insulation to the interior or exterior face of internal or external solid walls or solid or suspended floors.	Failure to take practical measures in each Dwelling to ensure SAP 70 ratings is attained using NHER or other accredited software. / Whole portfolio of Dwellings in PFI Area fails to reach or maintain an average of SAP rating 70 using NHER or other accredited software but disregarding any Dwellings which fail to achieve such rating solely as a result of a requirement by the Authority's officers responsible for Conservation Areas or planning to retain existing single glazed windows.	21 days	Part F Building Regulations	Y	N

Availability Standards (Full) Reference:	11

Building Element/Service:	Utilities

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
11.1	The Contractor shall ensure the provision of those utilities, which are the landlord’s responsibility. All Dwellings will have well maintained and safe access to: / water supply / sewerage facilities / electrical supply / gas supply (where gas is required for heating and hot water appliances). / The Contractor will have no responsibility for removal and replacement or maintenance of satellite dishes or other tenant aerials and appliances fixed externally to Dwellings. / The Contractor will have responsibility for maintaining communal aerials in blocks of flats.	Meet current standards of utility and performance.	Failure to ensure safe provision of any/all listed utility supplies at standards required by relevant legislation. / There shall be no failure event if the statutory undertaker reduces supplies to less than: / 1bar in the case of water supply / 220volts in the case of an electricity supply required to provide safe operation of gas appliances. / Failure to maintain a communal aerial in operational condition.	Total service failure 24 hours. / 21 days to bring up to standard in all other cases.	Compliance with all utility bye-laws.	Y	Y

Availability Standards (Full) Reference :	12

Building Element/Service:	Structure and Fabric

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
12.1	All Dwellings shall be structurally sound and stable.		Evidence of serious structural damage, draughts and /or water penetration, visible signs of dampness or damp staining.	21 days. / .	Part A (Structure) & B (Fire Safety) Building Regulations	Y	Y
12.2	All Dwellings shall be wind and weather tight.					Y	Y
12.3	All Dwellings shall be free from water penetration and rising or penetrating damp.		Building fabric attains moisture content outside acceptable range as defined in Building Research Establishment Good Repair Guide 33 Part 3 “Assessing Moisture in Building Materials – Interpreting Moisture Data: Typical Action Points”. In the case of each of the following materials remedial action is required where the following percentages by volume are exceeded: / Exposed brickwork: commons 14% / facings: 10% / engineering: 6% / calcium silicate: 9% / Concrete (low density) 10% / Concrete (high density) 12% / Plaster: 3% / Render: 5% / Timber: 20%	21 days.		Y	Y

Availability Standards (Full) Reference:	12 (Continued)

Building Element/Service:	Structure and Fabric

Ref	Scope		Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
12.4		All Dwellings shall be free from dry or wet rot or fungal infestation / See note above.		Rot, fungal infestation or any other attack causing deterioration of building element.	21 days.		Y	Y
12.5		All Dwellings shall be free from serious disrepair following refurbishment.		Failure to meet the fitness standard (S604 1985 Housing Act) (as amended by the Local Government and Housing Act 1989) and Section 10 of the Landlord & Tenant Act 1985.	21 days.	Section 604 1985 Housing Act / Local Government and Housing Act 1989) Landlord & Tenant Act 1985.	Y	Y
12.6		All Dwellings shall be/ shall have windows and doors free from rot, rust, decay or damage.		Rot, rust, decay or damage causing deterioration of building element and any failure in the wind and weather-tight properties of the building envelope.	21 days.		Y	Y

Availability Standards (Full) Reference:	13

Building Element/Service:	Drainage

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
13.1	An effective system for draining waste and foul water	Installation must be adequate for size of property and number of fittings attached to it.	Installation must be free from leaks and blockages with provision for clearing blockages (where these are fitted at Commencement Date or as part of the Refurbishment Works).	1 day.		Y	Y
13.2			Installation must be free from backsurge and syphonage.	1 day.		Y	Y
13.3			All installation catering for foul and waste material must be adequately ventilated and prevent foul air entering the Dwelling.	3 days.		Y	Y

Availability Standards (Full) Reference:	14

Building Element/Service:	Acoustic Performance

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
14.1	Works undertaken by the Contractor will contribute, where possible, to improving the acoustic performance of the building or the fabric of the building i.e. to reduce noise transmission between Dwellings and reduce noise from external sources.		Decrease in acoustic performance following replacement of single glazed windows with sealed double-glazing units and external doors with draught stripping.	One off improvement works measured to qualify for payment of Unitary Charge based on the Full Availability Standard.		Y	Y
14.2	The acoustic performance of the building or the fabric of the building will not be decreased as a result of permanent works carried out by the Contractor.		Decrease in acoustic performance following replacement of single glazed windows with sealed double-glazing units and external doors with draught stripping.			Y	Y
14.3	Windows	All new replacement windows shall be fitted with sealed unit double-glazing, or in the case of Conservation Areas and other areas within the PFI Area as may be designated by the local planning authority such alternative as may be agreed to comply with the requirements of the Building Regulations.	Lack of sealed units to new windows except where local planning authority has expressly not approved double glazed windows and existing has been repaired..	21 days.	Building Regulations Part L.	Y	Y

Availability Standards (Full) Reference:	15

Building Element/Service:	Internal/External Finishes

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
15.1	Serviceable and providing a sound base for decoration. / Note no internal decorations will be undertaken by the Contractor other than to replacement windows, doors, replacement kitchens and bathrooms or other ancillary components e.g. skirtings and trim. In particular, no decorations to replacement board or in-situ finishes will be undertaken by the Contractor other than in association with the above works.	Internal surfaces must be free from any polystyrene insulation materials.				Y	N
			Plaster is detached from backing or structural wall or missing.	21 days.		Y	N
			Ceiling finish missing. / Walls and/or ceiling not plastered. / Wall and ceiling surfaces free from polystyrene insulation material.	21 days.		Y	N
15.2	External decorations where required to replacement external components which require decoration e.g. fascias, weatherboarding, barge boards and eaves soffits will be undertaken by the Contractor	Free from loose and/or flaking paint / Applied finishes (e.g. rendering) free from blown patches/separation of finish from base structure or missing patches	Failure to meet Standards.	21 days		Y	Y

Availability Standards (Full) Reference:	16

Building Element/Service:	Access

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
16.1	All internal and external access-ways must provide free and safe access to and from individual Dwellings and residential blocks within the PFI Area. / To include maintaining lift access to higher floors where existing.		Individual Dwellings are not accessible.	Trapped persons in lifts: 2 hrs. / More than 50% of lifts out of action in one block: 4 hours / Less than 50% of lifts out of action in one block: 24 hours.	Secure by Design (lighting)	Y	Y

Availability Standards (Full) Reference:	17

Building Element/Service:	Safety and Security

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
17.1	All flooring, stairs, banisters and balustrades.	Must be secure and free from significant damage, decay and trip hazard during reasonable use.	Insecure, evidence of damage, decay or trip hazard that presents a serious health and safety risk.	Temporary repair in 24 hrs: Permanent repair in 7 days.	Secured By Design Standards for all security fittings.	Y	Y
17.2	Mains powered smoke detection devices.	Devices tested and serviced regularly (i.e. in accordance with manufacturer’s recommendations) and operational on each floor of each Dwelling.	Non-provision or non-operation (through neglect or omission on the part of the Contractor) of smoke detection system.	Temporary repair in 24 hrs: permanent repair in 21 days.	COSHH	Y	N
17.3	Fire stopping between Dwellings at party wall.	Adequate to meet Fire Regulations.	Inadequate fire stopping.	21 days.		Y	Y
17.4	External doors to all blocks of flats fitted with existing entry-phone systems.	Fitted and fully operational in cases where it is practical to close an entrance.	Non-provision or non-operation of door entry system.	Entry-phones locked shut 4 hours / All other repairs 24 hours.		Y	Y
17.5	External doors, front and rear doors and all windows with direct and indirect ground floor access.	Will be designed to deter, prevent and reduce crime.	Failure of operation of locks to doors and windows.	24 hours.		Y	Y
17.6	Security devices where fitted.	Fully operational.	Non-operation of fitted security devices (i.e. security devices other than locks to doors and windows) / The operation of specialist security and safety devices for mobility impaired persons or those provided solely for reasons of occupational therapy will not be the responsibility of the Contractor.	3 days.		Y	Y

Availability Standards (Full) Reference:	17 (Continued)

Building Element/Service:	Safety and Security

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
17.7	Asbestos	Disturbed asbestos removed.	Asbestos not removed or encapsulated. This clause will only apply to asbestos disturbed or exposed during maintenance works.	Make safe in 24 hours.		Y	Y (external to Dwelling only)
17.8		Undisturbed asbestos encapsulated.	Asbestos encapsulation broken down.	21 days.		Y	Y (external to Dwelling only)

Availability Standards (Full) Reference:	18

Building Element/Service:	Legal Availability

Ref	Scope	Standards	Determination of / Failure Event	Rectification / Period	Reference / Documents	Availability Standards Rented (Full)	Availability Standards Leasehold (Full)
18.1	All Property in the PFI Area to comply with Authority’s statutory obligations.		Where Contractor has not kept the Properties in a condition that complies with statutory obligations.	21 days.	s.11 Landlord and Tenant Act 1985 / s.4 Defective Premises Act 1972 / Pt.III s.79/82 Environmental Protection Act 1990 / s.604 Housing Act 1985 as amended by Local Government and Housing Act 1989. / Section 10 of the Landlord & Tenant Act 1985.	Y	Y
18.2	Garages and Outbuildings.	Structurally sound and watertight with opening lockable external doors.	Structural failure. / Failure to maintain in a watertight condition. / Failure to maintain fully functioning, lockable and secure access.	21 days		Y	N/A