## Datasheet
|  |  |  | Process Data Sheet: Chiller | [6 empty] | Document Number:
DRAFT - P3
Project: CPF Project |  |  |  |  | Site: Preston |  |  |  |  | Building No: A709
Project No: 13771.240 |  |  |  |  | System: 132 |  |  |  |  | Plant Item No: E13201
The Coated Particle Fuels (CPF) programme is to install an overall capability to produce Tri-structural Isotropic (TRISO) fuel in United Kingdom National Nuclear Laboratory (UKNNL)’s Preston Laboratory. The CPF line has four items of equipment that require cooling during operation – these fall in two systems, “Coater” (2 users) and “Compaction” (2 users). The purpose of the attached RFI is to determine whether it would be optimal to have 1 or 2 chillers supplying the system, what ancillaries would be recommended and to identify suitable suppliers. This Datasheet details the technical requirements of the chiller(s), and should be used to help determine the number of chillers. It details the scope of supply with respect to equipment items. Non-equipment items (e.g. details of paperwork, etc.) will be detailed in a separate specification which will be published with the full tender at a future date.
GENERAL DATA
Description: |  |  |  | Chiller |  |  |  | % Duty: |  |  | 100
Associated Drawings: |  |  |  | TBC |  |  |  | Installed Spares: |  |  | 0
Function: |  |  |  | To provide cooling water / fluid to CPF users. |  |  |  | No. installed: |  |  | TBC
Hazardous Area Classification: |  |  |  | Non-Hazardous |  |  |  | Location: |  |  | Preston
Radiation/Contamination Zoning: |  |  |  | R2/C2 |  |  |  | Indoor/Outdoor: |  |  | Indoor
ENVIRONMENT CONDITIONS
|  |  |  | Mininum |  | Normal |  | Maximum
Temperature |  |  |  | 10 |  | 20 |  | 30 |  | ˚C
Humidity |  |  |  | 60% |  | -- |  | 90%
Pressure |  |  |  | Atmospheric
FLUID DATA
Cooling Fluid state: |  |  |  | Liquid
Fluid composition: |  |  |  | Water with anti-foulant
Fluid Code: |  |  |  | CW
Corrosive/Errosive: |  |  |  | N/A
Toxicity/Hazardous Handling: |  |  |  | N/A
|  |  |  | Mininum |  | Normal |  | Maximum
Outlet Fluid Temperature |  |  |  | VTA |  | 10 |  | 15 |  | ˚C
Outlet Density |  |  |  | VTA |  | 999 |  | 999 |  | kg/m3
Inlet Fluid Temperature |  |  |  | TBC |  | Variable |  | 60 |  | ˚C
Inlet Density |  |  |  | TBC |  | Variable |  | 983 |  | kg/m3
Outlet Pressure |  |  |  | 3 |  | VTC |  | 4.5 |  | barg
Return Pressure |  |  |  | TBC |  | TBC |  | TBC |  | barg
Viscosity @ 10˚C |  |  |  | 0.0011373 | [5 empty] | Ns/m2
Foaming Tendency |  |  |  | N/A
PER/PED Fluid Group |  |  |  | 2
OPERATING/PERFORMANCE PARAMETERS
Individual User Requirements
|  |  |  | Cooling |  | Flow rate |  | Temperature |  | Pressure
|  |  |  | kW |  | m3/hr |  | ˚C |  | bar(g)
User 1 |  |  |  | 48.7 |  | 1.8 |  | ≤15 |  | 3 - 4 |  | Note: all four users are independent, but could operate simultaneously. |  | Coating | Scrubber
User 2 |  |  |  | 30 |  | 1.8 |  | ≤30 |  | < 3 |  |  |  | Coating | Furnace Cooling
User 3 |  |  |  | 30 |  | 1.2 |  | <25 |  | 3 - 4 |  |  |  | Compaction | Carbonising Furnace
User 4 |  |  |  | 110 |  | 5.5 |  | <30 |  | 3 - 4 |  |  |  | Compaction | Annealing Furnace
Design Rating of Equipment
|  |  |  | Requirements |  |  |  | The users have fault conditions that require the equipment to have increased temperature and pressure ratings.
|  |  |  | Temperature |  | Pressure
|  |  |  | ˚C |  | bar(g)
User 1 |  |  |  | 40 |  | 5 | [7 empty] | Coating | Scrubber
User 2 |  |  |  | 160 |  | 5 | [7 empty] | Coating | Furnace Cooling
User 3 |  |  |  | 55 |  | 5 | [7 empty] | Compaction | Carbonising Furnace
User 4 |  |  |  | 160 |  | 5 | [7 empty] | Compaction | Annealing Furnace
Overall Chilling Capacity
|  |  |  | Mininum |  | Normal |  | Maximum |  | Design
Cooling Capacity |  |  |  | 0 |  | 30 - 219 |  | 262* |  | VTA |  | kW | * inc. 20% margin
Cooling Fluid delivery flow rate |  |  |  | 1.2 |  | 10.3 |  | 12.4* |  | VTA |  | m3/hr
CHILLER DETAILS
Manufacturer
Model
|  |  |  | Length |  |  | Width |  |  | Height
Dimensions |  |  |  | VTA |  | mm | VTA |  | mm | VTA |  | mm
Design Life |  |  |  | 25 |  | years
Materials of construction |  |  |  | <element> VTA |  |  | <material> VTA
Materials of construction |  |  |  | <element> VTA |  |  | <material> VTA
Materials of construction |  |  |  | <element> VTA |  |  | <material> VTA
INCLUSIONS | [7 empty] | EXCLUSIONS
Pump
Expansion Vessel
Integral display.
Alarm to alert to low flow/fault conditions.
Electrical connections.
Control input/output.
Works testing, with certificates.
CE Marking
Documentation
Option price for installation support. | [7 empty] | Installation
Notes:
VTA | = | Vendor To Advise
Date |  | Issue | By |  | Checked |  | Approved |  | Purpose / Alterations
2025-01-16 |  | P3 | C. Haywood |  | R. Tara |  | K. Delaney |  | First issue.

## Sketch
|  |  | Process Data Sheet: Chiller |  |  |  |  | Document Number:
Project: CPF Project |  |  |  | Site: Preston |  |  | Building No: A709
Project No: 13771.240 |  |  |  | System: 132 |  |  | Plant Item No: E13201
EQUIPMENT SCHEMATIC AND PROVISIONAL NOZZLE ARRANGEMENT
EXPANSION VESSEL
| Towns Water Inlet | N1
[7 empty] | N3 | Cooling Fluid Inlet
[7 empty] | N2 | Cooling Fluid Outlet
NOZZLE SCHEDULE
Nozzle Number | Nozzle Duty |  |  | Nozzle Size | Connection | Rating |  | Comments
1 | Towns Water Inlet
2 | Cooling Fluid Outlet
3 | Cooling Fluid Inlet
Notes:
CHILLER