## Summary
Electrical Infrastructure Upgrade 2017
Department for Transport
June 2017
7.00 PRICING SCHEDULE
Item | Description |  |  | Quantity | Unit | Rate (£) | Total (£)
SUMMARY
A | Prelimiaries / General Conditions | [5 empty] | 0
B | LV DISTRIBUTION UPGRADE | [5 empty] | 0
|  | Basement Level - Strip Out |  |  |  |  | 0
|  | Basement Level - Proposed |  |  |  |  | 0
|  | Ground Floor - Strip Out |  |  |  |  | 0
|  | Ground Floor - Proposed |  |  |  |  | 0
|  | First Floor - Strip Out |  |  |  |  | 0
|  | First Floor - Proposed |  |  |  |  | 0
|  | Second Floor - Strip Out |  |  |  |  | 0
|  | Second Floor - Proposed |  |  |  |  | 0
|  | Third Floor - Strip Out |  |  |  |  | 0
|  | Third Floor - Proposed |  |  |  |  | 0
|  | Lift Isolator - Strip Out |  |  |  |  | 0
|  | Lift Isolator - Proposed |  |  |  |  | 0
C | EMERGENCY LIGHTING | [5 empty] | 0
|  | Basement Level |  |  |  |  | 0
|  | Ground Floor |  |  |  |  | 0
|  | First Floor |  |  |  |  | 0
|  | Second Floor |  |  |  |  | 0
|  | Third Floor |  |  |  |  | 0
|  | Fourth Floor |  |  |  |  | 0
|  | Fifth Floor |  |  |  |  | 0
|  | Sixth Floor |  |  |  |  | 0
|  | Seventh Floor |  |  |  |  | 0
|  | Eighth Floor |  |  |  |  | 0
D | CONTROL PANELS | [5 empty] | 0
|  | Second Floor - Strip Out |  |  |  |  | 0
|  | Second Floor - Proposed |  |  |  |  | 0
|  | Third Floor - Strip Out |  |  |  |  | 0
|  | Third Floor - Proposed |  |  |  |  | 0
|  | Seventh Floor - Strip Out |  |  |  |  | 0
|  | Seventh Floor - Proposed |  |  |  |  | 0
E | SUMP PUMPS | [5 empty] | 0
|  | Basement Level - Strip Out |  |  |  |  | 0
|  | Basement Level - Proposed |  |  |  |  | 0
|  | Ground Floor - Strip Out |  |  |  |  | 0
|  | Ground Floor - Proposed |  |  |  |  | 0
| Builders Works | [5 empty] | 0
|  | LV Distribution Upgrade |  |  |  |  | 0
|  | Emergency Lighting |  |  |  |  | 0
|  | Control Panels |  |  |  |  | 0
|  | Sump Pumps |  |  |  |  | 0
| Out of Hours Working | [5 empty] | 0
|  | LV Distribution Upgrade |  |  |  |  | 0
|  | Emergency Lighting |  |  |  |  | 0
|  | Control Panels |  |  |  |  | 0
|  | Sump Pumps |  |  |  |  | 0
| Generally | [5 empty] | 0
|  | LV Distribution Upgrade |  |  |  |  | 0
|  | Emergency Lighting |  |  |  |  | 0
|  | Control Panels |  |  |  |  | 0
|  | Sump Pumps |  |  |  |  | 0
|  |  | Carried to Form of Tender |  |  |  | 0

## A- Preliminaries
Electrical Infrastructure Works 2017
Department for Transport
June 2017
7.00 PRICING SCHEDULE
Item | Description |  | Quantity | Unit | Rate (£) | Total (£)
A | Prelimiaries / General Conditions |  |  |  |  | 0
i) | Preliminaries |  | 1 | item |  | 0
ii) | Overheads and profit |  | 1 | Item |  | 0
iii) | Scaffolding |  | 1 | Item |  | 0
iv) | Timber hoarding |  | 1 | Item |  | 0
v) | Skips |  | 1 | Item |  | 0
vi) | Management of waste and disposal |  | 1 | Item |  | 0
vii) | Attendance on named/specialist sub-contractors |  | 1 | Item |  | 0
viii) | Statutory signage |  | 1 | Item |  | 0
ix) | Testing, commissioning and labelling |  | 1 | Item |  | 0
x) | Operation and maintenance manuals |  | 1 | Item |  | 0
xi) | Record information (updates and new) |  | 1 | Item |  | 0
xii) | Training/instruction to the client staff |  | 1 | Item |  | 0
| Generally |  |  |  |  | 0
Add below any additional items to the above which is referred to in the Tender Specification or shown on the Drawings:
|  | Construction Total |  |  |  | 0

## B - LV Distribution
Electrical Infrastructure Works 2017
Department for Transport
June 2017
7.00 PRICING SCHEDULE
Item | Description |  | Quantity | Unit | Total (£)
B | LV DISTRIBUTION UPGRADE
| Basement Level - Strip Out [18080-DB-B-00] |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (SBTP1); including making safe and disconnection of the existing circuits for re-temination into the new panel as necessary |  | 1 | item | 0
2,3,4,5,6,7&9 | Make safe, disconnections, removal and disposal of the MICC cables associated with SBTP1, Control Panel B, and AHU20 - Extract Fan Isolator / Inverter, Supply Fan Isolator / Inverter, Light Switch |  | 1 | item | 0
8 | Make safe, disconnections, removal and disposal of the Light Switches in AHU20 |  | 1 | item | 0
10 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (MSBL1/P1) |  | 1 | item | 0
11 | Remove and retain circuit 5L1 to connect DB SB1TP1 (fan coil unit 19 and 20 circuit) |  | 1 | item | 0
12 | Make safe, disconnections, removal and disposal of the ELV circuits |  | 1 | item | 0
13 | Make safe, disconnections, removal and disposal of the existing 240 socket outlet cables |  | 1 | item | 0
14 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (MSBTP1); including making safe and disconnection of the existing circuits for re-temination into the new panel as necessary |  | 1 | item | 0
15 | Isolated circuits to be identified and stripped out if not in use |  | 1 | item | 0
16 | Make safe, disconnections, removal and disposal of the lights lamp post, Lambert Street Circuit |  | 1 | item | 0
17&18 | Make safe, disconnections, removal and disposal of the existing isolators, busbar chamber feeding BBP1 and BBL1 |  | 1 | item | 0
19 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (MBBTP1) |  | 1 | item | 0
20 | Make safe, disconnections, removal and disposal of FCU contactor |  | 1 | item | 0
21,22&23 | Make safe, disconnections, removal and disposal of the MICC cables associated with MBBTP1 feeding Car Park - Sump Pump, Extract Fan No 1, Extract Fan No 2 |  | 1 | item | 0
24 | Make safe, disconnections, removal and disposal of the isolator for Hydraulic Lift L8 |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
Basement Level - Strip Out [18080-DB-B-00]
25-26 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board and panel (BBTP1 (1 and 2) |  | 1 | item | 0
27 | N/A |  | 1 | item | 0
28&29 | Make safe, disconnections, removal and disposal of the SWA cables associated with BBTP1 to AHU25 Extract Fan |  | 1 | item | 0
30,32&33 | Make safe, disconnections, removal and disposal of the MICC cables associated with BBTP1 to Control Panel 01 Outstation; HWS Pump 1 Isolator; HWS Pump 2 Isolator |  | 1 | item | 0
31 | Make safe, disconnections, removal and disposal of the cable link from CP1 to AFP01 |  | 1 | item | 0
34 | Make safe, disconnections, removal and disposal of the existing isolators, busbar chamber feeding BCL1, BCP1 and BCL2 |  | 1 | item | 0
35 | Make safe, disconnections, removal and disposal of the existing 2 core 95.0mm2 SWA cable |  | 1 | item | 0
36 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (MSBTP2) |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Basement Level - Proposed [18080-DB-B-01] |  |  |  | 0
1A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (SBTP1); include for re-terminating the existing circuits in the new panel |  | 1 | item | 0
2A,7A&9A | Supply and install 2.5mm2 2 core SWA cable from SBTP1 to Control Panel 8; AHU20 - Light Switch, Heat Recovery Pump |  | 1 | item | 0
3A,4A,5A&6A | Supply and install 4.0mm2 4 core SWA cable from SBTP1 feeding AHU20 - Extract Fan Isolator / Inverter, Supply Fan Isolator / Inverter |  | 1 | item | 0
8A | Supply and install IP65 rated light switch in AHU20 |  | 1 | item | 0
10A | Supply and install Schneider Electric 18w 3ph Acti Isobar type B distrbution board (MSBL1/P1) |  | 1 | item | 0
11A | Relocate supply for fan coil units 19 and 20 to distribution board SBTP1 |  | 1 | item | 0
12A | N/A |  | 1 | item | 0
13A | Rewire socket outlets |  | 1 | item | 0
14A | Distribution board MSBTP1 to become part of MSBL1/P1; include for re-terminating the existing circuits in the new panel |  | 1 | item | 0
15A | Retain circuits still required |  | 1 | item | 0
16A | Relocate supply from DB SBTP1, existing to be extended |  | 1 | item | 0
16B | Install 2 separate 13A supplies to fused spurs, outlets from MSBTP1 distribution board in Water Tank Room |  | 1 | item | 0
17A / 18A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (BBL1/P1) |  | 1 | item | 0
19A | Supply and install Schneider Electric 18w 3ph Acti Isobar type B distrbution board (MBBTP1) |  | 1 | item | 0
20A | N/A |  | 1 | item | 0
21A,22A&23A | Supply and install 4.0mm2 4 core SWA cable from MBBTP1 feeding Car Park Sump Pump; Car Park Extract Fan No 1; Car Park Extract Fan No 2 |  | 1 | item | 0
24A | Supply and install 1No 200A TP&N fused switch (fused at 160A) |  | 1 | item | 0
25A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (BBTP1) |  | 1 | item | 0
26A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board () |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
Basement Level - Proposed [18080-DB-B-01]
27A | Relocate existing fluorescent luminaire above the new panel |  | 1 | item | 0
28A,30A&31A | Supply and install 2.5mm2 4 core SWA cable from BBTP1 (1 and 2) to AHU25 Supply Fan Isolator; CP01 Outstation; AFP01 |  | 1 | item | 0
29A,31A,32A&33A | Supply and install 4.0mm2 4 core SWA cable from BBTP1 (1 and 2) to AHU25 Extract Fan Isolator; HWS Pump 1 Isolator; HWS Pump 2 Isolator |  | 1 | item | 0
34A | All circuits to be moved over to new distrution panel BBTP1 (1 and 2) |  | 1 | item | 0
35A | 240.0mm2 4 core SWA cable for BBTP1/2 shal; be retained in new panel board with a 300A isolator |  | 1 | item | 0
36A | Supply and install 2No 4.0mm2 4 core SWA cable from BBTP1 (1 and 2) to Chilled Water Pump 5 and 6 Isolators |  | 1 | item | 0
37A | Move trace heating circuit to new BBTP1 distrbution board |  | 1 | item | 0
38A | Supply and install 95.0mm2 4 core SWA cable from switchboard to new BCL1 and P1 panel board |  | 1 | item | 0
39A | Supply and install Schneider Electric panel board with 200A isolator with 3No 63A fuse switches to feed independent distribution boards BCL1, BCP1 and BCL2 |  | 1 | item | 0
40A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (MBBTP2) |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Ground Floor - Strip Out [18080-DB-G-00] |  |  |  | 0
1 | Strip-out the existing 200A TP&N distribution panel, isolators and 2No distribution boards (Conference Hall); including making safe and disconnection of the existing circuits for re-temination into the new panel as necessary |  | 1 | item | 0
| Ground Floor - Proposed [18080-DB-B-01] |  |  |  | 0
1A | Supply and install Schneider Electric 1ph panel board (LV Panel Conference Hall) and associated isolators; include for re-terminating the existing circuits in the new panel |  | 1 | item | 0
2A | Supply and install Schneider Electric 18w 1ph Acti Isobar type B distrbution board (Conference Hall Miicellaneous Lighting CHL2) |  | 1 | item | 0
3A | Supply and install Schneider Electric 18w 1ph Acti Isobar type B distrbution board (Conference Hall General Purpose Power CHP2) |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| First Floor - Strip Out [18080-DB-01-00] |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (1BTP1) |  | 1 | item | 0
2,3,5,6,7,8,10 | Make safe, disconnections, removal and disposal of the MICC cables associated with 1BTP1 to Control Panel 2; AHU01 - Light Switch, Supply Fan Isolator, Foyer Extract Fan Isolator; AHU02 - Supply Fan Isolator, Light Switch; Toilet Extract Fan A; Toilet Extract Fan B |  | 1 | item | 0
4&9 | Make safe, disconnections, removal and disposal of the Light Switches in AHU01 and AHU02 |  | 1 | item | 0
12 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (1CTP1 1 and 2) |  | 1 | item | 0
13,14,15,17,18,19,21,22,23&24 | Make safe, disconnections, removal and disposal of the MICC cables associated with 1CTP1/2 to Control Panel 3; AHU05 Inverter Isolator; AHU04 Light Switch; AHU01 Supply Fan Isolator; Fan 04 Meeting Room Isolator; AHU03 - Light Switch, Supply Fan Isolator; Fan 03 Meeting Room Isolator; Toilet Extract Fan F05/a; Toilet Extract Fan F05/b |  | 1 | item | 0
16&20 | Make safe, disconnections, removal and disposal of the Light Switches in AHU03 and AHU04 |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| First Floor - Proposed [18080-DB-01-01] |  |  |  | 0
1A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (1BTP1) |  | 1 | item | 0
2A | Supply and install 2.5mm2 2 core SWA cable from 1BTP1 to Control Panel 8 |  | 1 | item | 0
3A&8A | Supply and install 1.5mm2 2 core SWA cable from 1BTP1 feeding Light Switches in AHU01 and AHU02 |  | 1 | item | 0
4A&9A | Supply and install IP65 rated Light Switches in AHU01 and AHU02 |  | 1 | item | 0
5A,6A,7A,10A&11A | Supply and install 4.0mm2 4 core SWA cable from 1BTP1 feeding AHU01 - Supply Fan Isolator, Extract Fan Isolator; AHU02 - Supply Fan Isolator; Toilet Extract Fan A; Toilet Extract Fan B |  | 1 | item | 0
12A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (1CTP1) |  | 1 | item | 0
13A | Supply and install 2.5mm2 2 core SWA cable from 1CTP2 to Control Panel 3 |  | 1 | item | 0
14A, 17A,18A,21A,22A,23A&24A | Supply and install 4.0mm2 4 core SWA cable from 1CTP1 feeding AHU05 - Inverter Isolator; AHU04 - Inverter Isolator; Fan 04 Meeting Room Isolator; Toilet Extract Fan F05/a; Toilet Extract Fan F05/b |  | 1 | item | 0
15A&19A | Supply and install 1.5mm2 2 core SWA cable from 1CTP1 feeding Light Switches in AHU03 and AHU04 |  | 1 | item | 0
16A&20A | Supply and install IP65 rated Light Switches in AHU03 and AHU04 |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Second Floor - Strip Out [18080-DB-02-00] |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (2BTP2) |  | 1 | item | 0
2,3,5,6,7,9&10 | Make safe, disconnections, removal and disposal of the associated MICC cables from 2CTP2 to Control Panel 4; AHU07 - Light Switch, Supply Fan Isolator, Extract Fan Isolator; AHU06 - Light Switch, Supply Fan Isolator, Extract Fan Isolator |  | 1 | item | 0
4&8 | Make safe, disconnections, removal and disposal of the existing Light Switches in AHU 06 and AHU07 |  | 1 | item | 0
11 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (CHTP2, 1 and 2) |  | 1 | item | 0
12,13,15,16,17,18,20,21&22 | Make safe, disconnections, removal and disposal of the associated MICC cables from CHTP2/2 to Control Panel 9; AHU22 - Light Switch, Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Islolator; AHU23 - Light Switch, Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Isolator |  | 1 | item | 0
14&19 | Make safe, disconnections, removal and disposal of the Light Switches in AHU22 and AHU23 |  | 1 | item | 0
23,25,26,27,28,29,30,31 | Make safe, disconnections, removal and disposal of the associated MICC cable from CHTP2/1 feeding AHU21 - Light Switch, Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Isolator; AHU24 - Light Switch, Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Isolator |  | 1 | item | 0
24&29 | Make safe, disconnections, removal and disposal of the existing AHU21 and AHU24 |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Second Floor - Proposed [18080-DB-02-01] |  |  |  | 0
1A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (2CTP2) |  | 1 | item | 0
2A | Supply and install 2.5mm2 2 core SWA cable from 2CTP2 to Control Panel 4 |  | 1 | item | 0
3A&7A | Supply and install 1.5mm2 2 core SWA cable from 2CTP2 feeding Light Switches in AHU06 and AHU07 |  | 1 | item | 0
4A&8A | Supply and install IP65 rated Light Switches in AHU07 and AHU07 |  | 1 | item | 0
5A | Supply and install 4.0mm2 4 core SWA cable from 2CTP2 feeding AHU07 - Supply Fan Isolator; AHU06 - Supply Fan Isolator, Extract Fan Isolator; |  | 1 | item | 0
6A,9A&10A | Supply and install 4.0mm2 4 core SWA cable from 2CTP2 feeding AHU07 Extract Fan isolator |  | 1 | item | 0
11A | Supply and install Schneider Electric 24w 3ph Acti Isobar type B distrbution board (CHTP2) |  | 1 | item | 0
12A | Supply and install 2.5mm2 2 core SWA cable from CHTP2 to Control Panel 9 |  | 1 | item | 0
13A,18A,23A&28A | Supply and install 1.5mm2 2 core SWA cable from CHTP2 feeding Light Switches in AHU21, AHU22, AHU23 and AHU24 |  | 1 | item | 0
14A,19A,24A&29A | Supply and install IP65 rated Light Switches in AHU21, AHU22, AHU23 and AHU24 |  | 1 | item | 0
15A,16A,17A,20A,21A,22A,25A,26A,27A,30A&31A | Supply and install 4.0mm2 4 core SWA cable from CHTP2 feeding AHU22 - Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Isolator; AHU24 - Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Isolator; AHU21 - Supply Fan Isolator, Extract Fan Isolator, Heat Recovery Pump Isolator; AHU24 - Supply Fan Isolator, Extract Fan Isolator |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Third Floor - Strip Out [18080-DB-03-00] |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (3BTP1, 1 & 2 ) |  | 1 | item | 0
2&3 | Make safe, disconnections, removal and disposal of the associated MICC cable from 3BTP1 feeding AHU10 - Extract Fan Isolator, Supply Fan Isolator |  | 1 | item | 0
4,5,6,8,9,11,12 | Make safe, disconnections, removal and disposal of the associated MICC cable from 3BTP1/1 feeding AHU08 - Extract Fan Isolator, Supply Fan Isolator, Light Switch, Toilet Extract Fan Standby Isolator, Heat Recovery Pump Isolator; AHU09 - Supply and Extract Starter Panel Isolator, Light Switch |  | 1 | item | 0
7&10 | Make safe, disconnections, removal and disposal of the Light Switches in AHU08 and AHU09 |  | 1 | item | 0
13 | Make safe, disconnections, removal and disposal of the associated MICC cable from 3BTP1/2 feeding the Plant Room Lighting |  | 1 | item | 0
14 | Make safe, disconnections, removal and disposal of the existing isolator and distribution board (3CTP2, 1 & 2 ) |  | 1 | item | 0
15.17,18,19,20,21,23,24,25&26 | Make safe, disconnections, removal and disposal of MICC cable from 3CTP2/1 feeding AHU11 - Light Switch, Supply Fan Isolator, Extract Fan Isolator, Control Panel 6, Heat Recovery Isolator; AHU12 - Light Switch, Supply Fan Isolator, Extract Fan Isolator; AHU13 - Light Switch, Supply Fan Isolator, Extract Fan Isolator |  | 1 | item | 0
16&22 | Make safe, disconnections, removal and disposal of Light Switches in AHU11, AHU12 and AHU13 |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Third Floor - Proposed [18080-DB-03-01] |  |  |  | 0
1A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distrbution board (3BTP1) |  | 1 | item | 0
2A,3A,4A,5A,8A,11A,12A | Supply and install 4.0mm2 4 core SWA cable from 3BTP1 feeding AHU10 - Extract Fan Isolator, Supply Fan Isolator; AHU08 - Supply Fan Isolator, Extract Fan Isolator, Toilet Extract Fan Standby Isolator, Heat Recovery Pump Isolator; AHU09 - Supply and Extract Starter Panel Isolator |  | 1 | item | 0
6A,9A | Supply and install 1.5mm2 2 core SWA cable from 3BTP1 feeding AHU08 light switch |  | 1 | item | 0
7A10A | Supply and install IP65 rated light switch to AHU08 |  | 1 | item | 0
8A | Supply and install 4.0mm2 2 core SWA cable from 3BTP1 feeding AHU09 Supply and Extract Starter Panel Isolator |  | 1 | item | 0
9A,15A | Supply and install 1.5mm2 2 core SWA cable from 3BTP1 feeding Light Switchs in AHU09 and AHU11 |  | 1 | item | 0
10A,16A | Supply and install IP65 rated Light Switches in AHU09 and AHU11 |  | 1 | item | 0
13A | Supply and install 1.5mm2 2 core SWA cable from 3BTP1/2 to Plant Room Lighting |  | 1 | item | 0
14A | Supply and install Schneider Electric 12w 3ph Acti Isobar type B distribution board (3CTP2) |  | 1 | item | 0
17A,18A | Supply and install 4.0mm2 4 core SWA cable from 3BTP2/1 feeding AHU11 - Supply Fan Isolator, Extract Fan Isolator |  | 1 | item | 0
19A | Supply and install 2.5mm2 4 core SWA cable from 3BTP2/2 feeding Control Panel 6 Outstation |  | 1 | item | 0
20A | Supply and install 4.0mm2 4 core SWA cable from 3BTP2/2 feeding AHU11 - Heat Recovery Pump Isolator |  | 1 | item | 0
21A | Supply and install 1.5mm2 2 core SWA cable from CHTP2 feeding Light Switches in AHU12 and AHU13 |  | 1 | item | 0
22A | Supply and install IP65 rated Light Switches in AHU12 and AHU13 |  | 1 | item | 0
23A | Supply and install 4.0mm2 4 core SWA cable from 3BTP2/1 feeding AHU12 supply fan isolator |  | 1 | item | 0
24A,25A | Supply and install 4.0mm2 4 core SWA cable from 3BTP2/1 feeding AHU12 - Extract Fan Isolator; AHU13 - Supply Fan Isolator |  | 1 | item | 0
26A | Supply and install 4.0mm2 4 core SWA cable from 3BTP2/2 feeding AHU14 Extract Fan Isolator |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Lift Isolators - Strip Out [18080-DB-08-00] |  |  |  | 0
1,2,8&9 | Make safe, disconnections, removal and disposal of the isolator and associated containment to Lift 1, Lift 2, Lift 6 and Lift 7 |  | 1 | item | 0
3 | Make safe, disconnections, removal and disposal of isolating switch from LV Switch Room |  | 1 | item | 0
4,5,6 | Make safe, disconnections, removal and disposal of the isolator, busbar chamber and its associated containment for Lift 3, Lift 4, Lift 5 |  | 1 | item | 0
7 | Make safe, disconnections, removal and disposal of the controls fuse switch, busbar chamber and its associated containment |  | 1 | item | 0
| Lift Isolators - Proposed [18080-DB-08-01] |  |  |  | 0
1A&8A | Supply and install 100A TP&N fused switch rated at 40Amps |  | 1 | item | 0
2A,4A,5A&6A | Supply and install 100A TP&N fused switch rated at 100Amps |  | 1 | item | 0
3A | Supply and install 300A TP&N isolating switch |  | 1 | item | 0
7A | Supply and install 100A TP&N fused switch rated at 63Amps |  | 1 | item | 0
8A | Supply and install 100A TP&N fused switch rated at 40Amps |  | 1 | item | 0
9A | Supply and install 60A TP&N fused switch rated at 16Amps |  | 1 | item | 0
B | LV DISTRIBUTION UPGRADE
| Builders Work |  |  |  | 0
1 | Builders work in connection associated with the above works |  | 1 | Item | 0
| Out of Hours Working |  |  |  | 0
2 | Out of hours working associated with the above works |  | 1 | Item | 0
| Generally |  |  |  | 0
Add below any additional items to the above which is referred to in the Tender Specification or shown on the Drawings:
|  | Sub-Total |  |  | 0

## C- Emergency Lighting
Electrical Infrastructure Works 2017
Department for Transport
June 2017
7.00 PRICING SCHEDULE
Item | Description |  | Quantity | Unit | Rate (£) | Total (£)
C | EMERGENCY LIGHTING
| Basement Level - [18080-EL-B-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Ground Floor - [18080-EL-G-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| First Floor - [18080-EL-01-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Second Floor - [18080-EL-02-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Third Floor - [18080-EL-03-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Fourth Floor - [18080-EL-04-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Fifth Floor - [18080-EL-05-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
C | EMERGENCY LIGHTING
| Sixth Floor - [18080-EL-06-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Seventh Floor - [18080-EL-07-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Eighth Floor - [18080-EL-08-01] |  |  |  |  | 0
1 | Supply and installation of luminaires c/w 3hr emergency battery pack, including all ancillaries and accessories; emergency test switches; wiring and secondary containment |  | 1 | item |  | 0
| Builders Work |  |  |  |  | 0
1 | Builders work in connection associated with the above works |  | 1 | Item |  | 0
| Out of Hours Working |  |  |  |  | 0
1 | Out of hours working associated with the above works |  | 1 | Item |  | 0
| Generally |  |  |  |  | 0
Add below any additional items to the above which is referred to in the Tender Specification or shown on the Drawings:
|  | Sub-Total |  |  |  | 0

## D - Control Panels
Electrical Infrastructure Works 2017
Department for Transport
June 2017
7.00 PRICING SCHEDULE
Item | Description |  | Quantity | Unit | Rate (£) | Total (£)
D | CONTROL PANELS
| Second Floor - Strip Out [18080-CP-02-00] |  |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing MICC supplies and feeder cabling (AHU21, 22 and 23) |  | 1 | item |  | 0
2 | Make safe, disconnections, removal and disposal of the Control Centre (AHU21, 22 and 23) |  | 1 | item |  | 0
| Second Floor - Proposed [18080-CP-02-01] |  |  |  |  | 0
3 | Supply and installation of ABB ACH550 15kW variable speed drive (Extract Fan - AHU21 , AHU22 and AHU23; Supply Fan - AHU21, AHU22 and AHU23) |  | 1 | item |  | 0
4 | Supply and installation of ABB ACH550 1.5kW variable speed drive (Heat Recovery - AHU21 , AHU22 and AHU23) |  | 1 | item |  | 0
5 | Supply and installation of rotary isolators (Extract Fan - AHU21 , AHU22 and AHU23; Supply Fan - AHU21, AHU22 and AHU23; Heat Recovery - AHU21 , AHU22 and AHU23) |  | 1 | item |  | 0
6 | Supply and install 6.0mm2 5 core SWA cable and terminations (Heat Recovery - AHU21 , AHU22 and AHU23) |  | 1 | item |  | 0
7 | Supply and install 10.0mm2 5 core SWA cable and terminations (Extract Fan - AHU21 , AHU22 and AHU23; Supply Fan - AHU21, AHU22 and AHU23) |  | 1 | item |  | 0
8 | Connection of the existing BMS to inverter and enable signal (Extract Fan - AHU21 , AHU22 and AHU23; Supply Fan - AHU21, AHU22 and AHU23; Heat Recovery - AHU21 , AHU22 and AHU23) |  | 1 | item |  | 0
D | CONTROL PANELS
| Third Floor - Strip Out [18080-CP-03-00] |  |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing MICC supplies and feeder cabling |  | 1 | item |  | 0
2 | Make safe, disconnections, removal and disposal of AHU09 Extract Fan Isolators |  | 2 | item |  | 0
3 | Relocation of the retained AHU09 supply fan inverter and re-cable and terminate (power and BMS) as necessary |  | 1 | item |  | 0
4 | Relocation of the retained AHU09 extract fan inverter and re-cable and terminate (power and BMS) as necessary |  | 1 | item |  | 0
| Third Floor - Proposed [18080-CP-03-01] |  |  |  |  | 0
5 | Relocation of the supply and extract variable speed drives to the existing AHU09 control panel |  | 1 | item |  | 0
6 | Supply and install 6.0mm2 5 core SWA cable and terminations |  | 1 | item |  | 0
7 | Supply and installation of rotary isolators (Extract Fan - AHU09) |  | 2 | item |  | 0
8 | Supply and install 4.0mm2 5 core SWA cable and terminations |  | 1 | item |  | 0
9 | Connection of the existing BMS to inverter and enable signal |  | 1 | item |  | 0
D | CONTROL PANELS
| Seventh Floor - Strip Out [18080-CP-07-00] |  |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing MICC supplies and feeder cabling |  | 1 | item |  | 0
2 | Make safe, disconnections, removal and disposal of the Supply Fan Motor Control Centre |  | 1 | item |  | 0
3 | Make safe, disconnections, removal and disposal of the Extract Fan Motor Control Centre |  | 1 | item |  | 0
| Seventh Floor - Proposed [18080-CP-07-01] |  |  |  |  | 0
4 | Supply and installation of ABB ACH550 15kW variable speed drive (Extract Fan - AHU16; Supply Fan - AHU16) |  | 1 | item |  | 0
5 | Supply and installation of rotary isolators (Extract Fan - AHU16; Supply Fan - AHU16) |  | 1 | item |  | 0
6 | Supply and install 10.0mm2 5 core SWA cable and terminations (Extract Fan - AHU16; Supply Fan - AHU16) |  | 1 | item |  | 0
7 | Connection of the existing BMS to inverter and enable signal (Extract Fan - AHU16; Supply Fan - AHU16) |  | 1 | item |  | 0
D | CONTROL PANELS
| Builders Work |  |  |  |  | 0
1 | Builders work in connection associated with the above works |  |  | Item |  | 0
| Out of Hours Working |  |  |  |  | 0
2 | Out of hours working associated with the above works |  |  | Item |  | 0
| Generally |  |  |  |  | 0
Add below any additional items to the above which is referred to in the Tender Specification or shown on the Drawings:
|  | Construction Total |  |  |  | 0

## E- Sump Pumps
Electrical Infrastructure Works 2017
Department for Transport
June 2017
7.00 PRICING SCHEDULE
Item | Description |  | Quantity | Unit | Rate (£) | Total (£)
E | SUMP PUMPS
| Basement Level - Strip Out [18080-SP-B-00] |  |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing pump and discharge pipework, to screwed coupling and retain for future use (Sump No 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
2 | Make safe, disconnections, removal and disposal of the control panel and all control wiring (Sump No 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
| Basement Level - Proposed [18080-SP-B-01] |  |  |  |  | 0
3 | Supply and installation of 400W sump pump, including non-return valve, complete with high level float and discharge pipework (Sump No 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
4 | Supply and installation of 750W sump pumps, including non-return valve, complete with high level float and discharge pipework (Sump No 15) |  | 1 | item |  | 0
5 | Supply and installation of new discharge pipework connection to existing cast iron pipework (Sump No 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
6 | Supply and installation of reed type float switch to suit new pipework arrangement (Sump No 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
7 | Supply and installation of pump controller complete with parts kit including floats and alarm level float switch and fixing (Sump No 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
8 | Supply and installation of isolator including supplies (4.0mm2 3 core SWA) (Sump No 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
9 | Supply and installation of new BMS connection (Sump No 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 13, 14, 15 and 16) |  | 1 | item |  | 0
10 | New central sump pump alarm and BMS panel, connected to network and BMS head end |  | 1 | item |  | 0
E | SUMP PUMPS
| Ground Floor - [18080-SP-G-00] |  |  |  |  | 0
1 | Make safe, disconnections, removal and disposal of the existing pump and discharge pipework, to screwed coupling and retain for future use (Sump No 12) |  | 1 | item |  | 0
2 | Make safe, disconnections, removal and disposal of the control panel and all control wiring (Sump No 12) |  | 1 | item |  | 0
| Ground Floor - [18080-SP-G-01] |  |  |  |  | 0
3 | Supply and installation of 400W sump pump, complete with high level float and discharge pipework (Sump No 12) |  | 1 | item |  | 0
4 | Supply and installation of new discharge pipework connection to existing cast iron pipework |  | 1 | item |  | 0
5 | Supply and installation of reed type float switch and non-return valve to suit new pipework arrangement |  | 1 | item |  | 0
6 | Supply and installation of pump controller complete with parts kit including floats and alarm level float switch and fixing |  | 1 | item |  | 0
7 | Supply and installation of isolator including supplies (4.0mm2 3 core SWA) |  | 1 | item |  | 0
8 | Supply and installation of new BMS connection |  | 1 | item |  | 0
E | SUMP PUMPS
| Builders Work |  |  |  |  | 0
1 | Builders work in connection associated with the above works |  | 1 | Item | 0 | 0
| Out of Hours Working |  |  |  |  | 0
2 | Out of hours working associated with the above works |  | 1 | Item | 0 | 0
| Generally |  |  |  |  | 0
Add below any additional items to the above which is referred to in the Tender Specification or shown on the Drawings:
|  | Construction Total |  |  |  | 0