The Maritime and Coastguard Agency (MCA) is an Executive Agency of the Department for Transport.  The MCA is responsible throughout the UK for implementing and developing the UK Government’s maritime safety and environmental protection policy.  That includes co-ordinating Search and Rescue at sea through Her Majesty’s Coastguard 24 hours a day, and checking that ships meet UK and international safety rules.  The MCA work to prevent the loss of lives at the coast and at sea, to ensure that ships are safe, and to prevent coastal pollution: Safer Lives, Safer Ships, Cleaner Seas.

The MCA provides a full range of search and rescue, counter pollution, survey, inspection and enforcement activities and has 12 major business activities:

| Survey | Seafarers’ Services |
| --- | --- |
| Inspection | Search and Rescue |
| Enforcement | Pollution Response and Salvage |
| Ship Registration | Stakeholder Communication |
| Navigation Services | Ministerial Services |
| Strategic Prevention Design/Development | Regulatory Process |

These activities are maintained by support services responsible for providing a range of administrative functions including infrastructure, MCA people, financial management and administration and corporate management.

In accordance with the 2010 Equality Act, our capacity as a public body means we have a statutory duty to eliminate unlawful discrimination, promote equality of opportunity and promote good relations between people of different backgrounds.  Contractors will be expected to ensure that the service they provide promotes good relations between the MCA and its customers and does not directly or indirectly discriminate on the grounds of any of the protected characteristics specified in the Act.

You are invited to submit a tender for the following project:

MCA REFERENCE:  TCA 3/7/1115

BOILER REPLACEMENT, MARINE HOUSE, BLAIKIES QUAY,

ABERDEEN

- The Works

1.1	You are invited to submit a tender for the works outlined below.

  - Quality of Workmanship.  All works should be completed to a high standard, fit for purpose and in accordance with current British Standards, industry best practice and relevant Regulations for each work element.  Any electrical work is to be undertaken by a NICEIC or equivalently accredited electrical engineer.

1.3	The contractor is to pay the necessary fees to all associated sub consultants/contractors, i.e. building control etc.

1.4	A viewing day for tenderers to visit site has been scheduled for 11.30 Thursday 3rd October 2019.

- Existing Installation.

  - Most of the existing heating installation equipment is at or beyond the recommended economic life as stated by CIBSE/HVCA guides.  Several elements of the plant are approximately 40 years old.  However, some components such as timeclocks, energy monitoring equipment and pump heads have been upgraded during the intervening period.  The main boiler plant currently consists of six Hamworthy Purewell 80 P/P natural gas fired cast iron atmospheric modular boilers.  The boilers are 88% efficient with a nett input of 90.9kw and overall output of 80kw per boiler, equating to a total of 480kw of total boiler plant power.

- Specification.  The tender must include all sundry items required to fully complete their installation.  All items are to be installed in accordance with manufacturer’s guidelines.  All disturbed surfaces must be made good.  All waste, including old boilers, arising from the works are to be disposed of by the contractor in accordance with relevant regulations.

3.1	Boilers.  Replace the current six gas fired boilers with four modular condensing boilers to achieve an equivalent output.  These new boilers to be a modern, efficient equivalent.

  - In addition to the six boilers mentioned above, there is a Vokera Mynute 20HE wall mounted high efficiency gas system boiler rated at 20KW.  This boiler provides the primary heating to the 210 litre hot water cylinder and was installed circa 2008 and appears to only feed a 210 litre indirect stainless steel hot water cylinder located adjacent to the main boilers in the plant room.  Installed possibly as a summer operation whereby the main heating plant could be turned off during the summer providing a more efficient operation.  We would ask tenderers to provide advice as to the necessity of this unit, i.e. our preference would be that this additional system is removed, and the hot water cylinder fed from the new replacement system.

  - Stainless Steel Flue.  Generally, in a good condition but would request the horizontal flue heads be replaced to suit the new boiler installation, utilising the existing vertical risers system.

  - General Isolation Valves.  Replace any passing valves or ones that are stuck in position.

  - Circulation Pump.  Replace the LPHW circulation pumps with inverter driven (variable speed) pumps

  - Pressurisation Unit.  Replace.

  - Automatic Controls.  Replace the Control Panel.

  - Automatic Controls.  Replace the Control Valves

  - Automatic Controls.  Replace the Control Valve Actuators

  - Automatic Controls.  Replace the Temperature Sensors

  - Air and Dirt Separator.  Install a new air and dirt separator into the LPHW heating system.

  - Individual Thermostat Controls.  As an optional extra we would like to consider the fitting of thermostatic controls to radiators throughout the building.

4.	Health and Safety.  The works to be undertaken under the full remit of the CDM Regulations 2015.  At this stage we do not anticipate that the project will be notifiable.

5.	Handover.  The contractor is to provide a handover file for the works, including copies of any Electrical Safety Test Certificates, maintenance/servicing information, building control certification, etc.

6.	Pricing

6.1	Recommendations from the Tenderer for any additional works, not already included in the price, would be greatly appreciated, with separate quotes as optional extras.

6.2	The Tenderer should submit the completed Pricing Schedule and Works Schedule (Appendix A) to supply and install new boilers at Marine House, Blaikies Quay, Aberdeen.

7.	Guarantee

7.1	We regard warranties as an important component of achieving overall best value for money.  Full details of any warranties on the tendered equipment is required, including the period of cover.  We would also like to know the length of the guarantee coverage and how much it would cost to extend the period, i.e. if the guarantee period is one year, please provide a cost to extend this to two years, three years and four years.  Details of response times would also be appreciated.

8.	Insurance

8.1	Tenders should provide evidence of all insurances held, i.e. Public liability, employer’s liability, etc.

9.	Delivery

9.1	Tenderers should state in their tender their lead time for commencing work and the expected time on site for completion of all works and handover to the MCA.

10.	Training

10.1	Tenders should allow for full training of at least two members of staff on the operation of the system.

11.	Payment

11.1	Payment shall be made upon completion of all works in accordance with the ‘General Conditions of Contract for the Supply of Goods and Associated Services’, and subject to the receipt of a valid and correctly submitted invoice.  The MCA pays undisputed invoices 30 days in arrears.

12.	Submission of Tenders

12.1	Tenders must be submitted by the deadline date stated in the Invitation to Tender letter, and in accordance with the Instructions to Tenderers.

12.2	Tenders are required to provide a full programme of work schedule, including start date, training, and time on site.

13.	Sustainability

13.1	The MCA is committed to sustainable procurement.  This means making the necessary decisions to protect our environment and to operate its procurement activity in an economically, socially and environmentally responsible way.  Tenderers should indicate ways in which their organisation promotes and practices sustainable development and how this can impact on this contract.

13.2	Consideration should be taken to account for the following areas;

Origin and recycled/recyclable content of materials

- Tenderers should detail the quantities used and recycle content of the product.

- Recyclability of product once it has reached its end of life.

- Type of paints and coverings used.

Transport mode selected for freight

- Tenderers should detail options to identify and promote measures to reduce emissions during transport of goods. Including rail freight or low emission/fuel efficient heavy goods vehicles

13.3	More information on the environmental consideration can be found at:

https://www.gov.uk/government/policies/making-sustainable-development-a-part-of-all-government-policy-and-operations

https://www.gov.uk/government/collections/sustainable-procurement-the-government-buying-standards-gbs

14.	Selection Process

Evaluation Criteria

Quality Score represents 60% of Total Scores	Weightings

Compliance with the Technical Requirement			50%

Flues, Isolation valves, Circulation Pumps,

Pressurisation Unit, Control Panel, Valves,

Sensors, Separator						15%

Guarantees								5%

Compliance with all relevant British Standards			5%

Details of any sub-contractors					5%

Evidence of insurance						5%

Works Schedule/Programme/Training				5%

Sustainability/Waste Disposal					5%

Estimated time for works						5%

Quality Points

0 – Inadequate response

1 – Major weaknesses in the response

3 – Minor weaknesses in the response or detail missing

5 – Satisfactory response that fully meets the requirement and includes all relevant supporting evidence

Each Bidder’s Quality Score

Quality Score = x Weightings

Highest Quality Score Possible for the Criterion

Price Score represents 40% of Total Scores	Weightings

Overall cost 						85%

Option for Thermostatic Radiator Valves		10%

Other Proposed Options				5%

Lowest Bid Cost

Cost Score = x Weightings

Each Bidder’s Cost

TOTAL SCORE = Total Quality Score + Total Cost Score

THE MCA INTENDS TO AWARD THE CONTRACT TO THE HIGHEST SCORING TENDERER

Appendix A

WORKS SCHEDULE

| Item + (Paragraph Ref) | Details, Type, Quantity, Size, Output, Etc |
| --- | --- |
| Boilers (3.1) |  |
| Water Cylinder Boiler / Removal (3.2) |  |
| Details of any sub-contractors (1.3) |  |
| Stainless Steel Flue (3.3) |  |
| Isolation Valves (3.4) |  |
| Circulation Pumps (3.5) |  |
| Pressurisation Unit (3.6) |  |
| Control Panel (3.7) |  |
| Control Valves (3.8) |  |
| Control Valve Actuators (3.9) |  |
| Temperature Sensors (3.10) |  |
| Air and Dirt Separator (3.11) |  |
| Insurance (8) |  |
| Optional Thermostatic Radiator Valves (3.12) |  |
| Guarantees (7) Year 1 |  |
| Year 2 |  |
| Year 3 |  |
| Year 4 |  |
| Delivery and Lead time (11.2) |  |
| Time on Site (9) |  |
| Training (10) |  |

**NOTE: Failure to supply the information requested in the above table could result in your tender submission

not being taken forward.