## Tender Clarification Schedule
Tender Questions and Answers Tracker dated: |  | 2023-03-23
Client: | Croydon College
Project Name: | FECTF Works
Clarification No. | Date Query Issued | Query | Response | Answered by | Date Answer Issued | Query Status (Open / Closed)
1 | 2023-03-10 | Are we required to remove Asbestos? If so in which rooms? | Yes. Asbestos Removal will be Contractor responsibility in relation to entire project scope. Please refer to College Asbestos Register in Appendix L of the tender documents. | Fusion | 2023-03-15 | Closed
2 | 2023-03-10 | We assume that there is no FF&E required. Is this correct? | Correct. | Woodley Coles | 2023-03-15 | Closed
3 | 2023-03-10 | Please forward a finishes schedule/specification. | Please refer to 'CC FECTF - Internal Refurbishment Works' documents included on the tender portal. | Fusion | 2023-03-23 | Closed
4 | 2023-03-10 | Is a fall arrest system for the roof required? | Please refer to Tender Addendum document '34754 - Croydon College Tender Addendum - AFI.pdf' | Baily Garner | 2023-03-15 | Closed
5 | 2023-03-10 | Please state the packages which are contractor design | This is a Design & Build contract. | Woodley Coles | 2023-03-15 | Closed
6 | 2023-03-10 | Pleased provide us with a drawing showing the extent of the new render within the courtyard. We are unable to do this with plan drawings. Also the specification reference 35_31_64_12 is referred to in the document, but is missing. | There are only 2 rendered bands therefore should be able to cost based on the linear meterage and photoschedule provided. | Baily Garner | 2023-03-15 | Closed
7 | 2023-03-10 | Is there a door and ironmongery schedule? | No, contractor to design and submit proposals | Baily Garner | 2023-03-15 | Closed
8 | 2023-03-10 | Is a window schedule available? | Provided, see breakdown within seciton 4 and Tender Drawings T08 and T09 | Baily Garner | 2023-03-15 | Closed
9 | 2023-03-10 | Are Layouts for electrical services available? | No, contractor to design and submit proposals. Layouts to match existing recently refurbished rooms are far as possible, | Fusion | 2023-03-15 | Closed
10 | 2023-03-10 | We Assume offices are shell only.Please confirm. | Scope of works is as per internal refurbishment schedule. Al internal spaces will be as existing, with FF&E remaining in situ. | Fusion | 2023-03-15 | Closed
11 | 2023-03-10 | Please clarify roof level access requirements | Roof access requirements will vary for each roof and will be discussed during site visits. Further information is to be provided by the College in due course. | Fusion | 2023-03-15 | Closed
12 | 2023-03-10 | Within Appendix A of tender documents, you have provided CSA. Can you please confirm that we are to ignore this document as there are various items within this CSA which does not form part of the tender. | No. Do not ignore the CSA. Revised CSA has been issued for clarity. | Woodley Coles | 2023-03-15 | Closed
13 | 2023-03-10 | You have provided two Preliminaries Documents. We have Section 2 – Preliminaries_Final and also Preliminaries in Bailey Garner Spec. We assume Section 2-Preliminaries_Final does not apply to this tender and to allow for the Prelims included within Bailey Garner Specification. | No. BG Prelims do not cover the full scope of the Works. See item 7K in the CSA. | Woodley Coles | 2023-03-15 | Closed
14 | 2023-03-10 | Schedule of works, page 4/8 and 4/9 makes reference to elevations 1,2,3,4 & 5. Can you please provide these elevation drawings so we can identify the windows/doors which are replaced. Can you also confirm that at this stage, we are to allow for the windows/doors quantities provided in the SOW items 4.19.6 to 4.20.8 inclusive. | Quants are as specified. Elevations as indicated on floor plans - no elevation drawings provided at this stage. BG to follow up on 14/03/23 | Baily Garner | 2023-03-15 | Closed
15 | 2023-03-10 | Making good decorations internally where new windows/doors are replaced – For clarity, can you please confirm that we are to paint window reveals only where disturbed during window/door replacement. | What you detail is what would be anticipated with colour matched accordingly. Should damage extend beyond the reveal then the full wall would need redecoration. Some rooms with window replacment are being fully redecorated under the internal refurbishment elements of the Works. | Woodley Coles | 2023-03-15 | Closed
16 | 2023-03-10 | SOW item 4.13.5, 4.24 & 4.25 – Can you please confirm that any making good of plaster/decorations disturbed during door and window replacement will be included in the provisional quantity provided. | 4.13.5 - No PQ deemed included within price. 4.24&4.25 where it can be demonstrated in the schedule of condition damage is existing prior to works then provisional quant will be expended for making good these areas. As per 4.22 contractor responsible for making good damage as a result of works. | Baily Garner | 2023-03-15 | Closed
17 | 2023-03-10 | SOW item 4.13.6 – Can you please provide provisional quantity for renewing(if any) wall tiles, cill tiles, render, etc | No provisional quant given, item deemed to be included witihn contractors priced return. | Baily Garner | 2023-03-15 | Closed
18 | 2023-03-13 | Can SME's tender for this project? Is there a minimum turnover? | SME's are able to tender for the opportunity and will be assessed in line with the cost of the tender return and the responses to the qualitative questions provided. | Fusion | 2023-03-22 | Closed
19 | 2023-03-15 | We were advised that works to roofing and internal refurbishment of class rooms shall be uploaded on the portal. Can you please advise when will these documents be available. We would also require extension to tender return date to incorporate these additional works. We will also require further site visit once the above documents are received. | Tender addendum information will be uploaded to the portal on 15/03/2023 with the internal refurbishment schedule and outline specification to follow on as soon as possible. Any extension to the tender period that is granted by the College will be communicated via the contracts finder portal. | Fusion | 2023-03-17 | Closed
20 | 2023-03-15 | Can you please advise when will we receive your answers to the questions raised on 10th March 2023 by email. | Responses to these queries are noted in this document. | Fusion | 2023-03-17 | Closed
21 | 2023-03-15 | Item 4.7.1 & 4.11.1 of SOW – Can you please provide provisional quantity of man days/hours to assist client to remove/relocate furniture and fittings. | Please allow for a provisional quantity of 2 man days to assist the College with the relocation of FF&E. This item may be omitted should the College have ample capacity undertake this task. | Fusion | 2023-03-22 | Closed
22 | 2023-03-15 | Item 4.9.1, 4.9.4 & 4.27 of SOW – Internal access to only few window openings was provided. Windows shown on site had no existing cables within the vicinity of the works. Can you please confirm that these would also apply to remainder openings or please provide either Provisional Sum or Quantity. | Contractors design, would expect no additional costs/variations if identified when on site | Baily Garner | 2023-03-17 | Closed
23 | 2023-03-15 | Item 4.9.2 & 4.27 of SOW – Areas shown to us yesterday did not have mechanical ducting of fans mounted to windows. We assume these item is not applicable. | Contractors design, would expect no additional costs/variations if identified when on site | Baily Garner | 2023-03-17 | Closed
24 | 2023-03-15 | Item 4.9.3 –During our site visit, we could not identify and roller shutters within the vicinity of the works. We assume these item is not applicable. | Contractors design, would expect no additional costs/variations if identified when on site | Baily Garner | 2023-03-17 | Closed
25 | 2023-03-15 | Item 4.10.1 of SOW; During our site visit, it was noted that some scaffold(or other means of access) would have to be erected off existing roofs/structure. At this stage, we will assume that the existing structure will able to take additional loading imposed. | Contractors design, would expect no additional costs/variations if identified when on site | Baily Garner | 2023-03-17 | Closed
26 | 2023-03-15 | It was also agreed that erection/dismantle of scaffold(or other means od access) can be carried out during normal working hours. | This is correct. | Fusion | 2023-03-17 | Closed
27 | 2023-03-15 | Permission/Licence from LA for access on to podium(South Elevation) will be obtained by the Client. | Scaffold design forms part of the Contractor's design/responsibility so this will need to be obtained by the Contractor. | Baily Garner | 2023-03-17 | Closed
28 | 2023-03-15 | Unobstructed access to the under croft car park will be provided and vehicles will not be parked where scaffold/other means of access is erected. | Access for College deliveries must be maintained at all times, plus any MOE maintained. | Woodley Coles | 2023-03-17 | Closed
29 | 2023-03-15 | Item 4.12.1 of SOW - Areas shown to us yesterday did not have any blinds or curtains. Can you please confirm that these applies the same to all other openings or please provide provisional quantity for the removal and reinstatement of blinds/curtains. | Contractors design, would expect no additional costs/variations if identified when on site | Baily Garner | 2023-03-17 | Closed
30 | 2023-03-15 | Item 4.13.2 of SOW – Can you please confirm that none of the window openers require winding gear. If required, can you please advise which type of winding gear as you have provided specification for three different types – i.e. Teleflex, Canstay folding openers and automated actuators. | Winding gear not required to our knowledge – windows to be top hung openers manually operated. | Baily Garner | 2023-03-17 | Closed
31 | 2023-03-15 | Item 4.13.6 of SOW – Hacking off and renewal of glazed wall or cill tiles is not applicable. | Contractors design, would expect no additional costs/variations if identified when on site | Baily Garner | 2023-03-17 | Closed
32 | 2023-03-15 | Item 4.14.6 & 4.14.7 of SOW – Can you please advise which concrete surfaces are required to be repaired. We need this information in order to calculate cost of hammer testing cover meter testing. | All concrete Cills and Lintels to be Hammer Tested | Baily Garner | 2023-03-17 | Closed
33 | 2023-03-15 | Item 4.15 of SOW – Can you please confirm that stone cleaning is to all elevations and to include window surrounds. | Yes this is correct. | Baily Garner | 2023-03-17 | Closed
34 | 2023-03-15 | Item 4.16.2 of SOW – Can you please provide provisional quantity for securing fascia boards to existing rafters as we are unable to quantify the extent at this stage. | Provisional quantity will not be provided - Contractors to quantify in tender returns. | Woodley Coles | 2023-03-17 | Closed
35 | 2023-03-15 | Item 4.17.1 of SOW – Do we allow to renew all existing render or only where missing?. Can you also please confirm that the works to the East Courtyard is limited to only render renewal as advised on site. | All existing render within East Courtyard. | Baily Garner | 2023-03-17 | Closed
36 | 2023-03-15 | East Elevation of College, adjacent new construction – As advised, we are to provide budget cost for carrying out specified works including access as these may not be carried out due to construction site. Can you please confirm your acceptance to allow a Provisional Sum of £10,000.00 for these. | Provisional quantity will not be provided - Contractors to quantify in tender returns. | Woodley Coles | 2023-03-17 | Closed
37 | 2023-03-16 | Items 4.14 & 4.26 - Q1 -Are we to assume that the Concrete repairs & pointing will be in the above window & render renewal areas only? – | Concrete is additional and separate to the window and render works – generally found a basement level in form of lintels and cills. | Baily Garner | 2023-03-17 | Closed
38 | 2023-03-16 | Item 4.15.2 Stone Cleaning, states DOFF wash to ALL elevations. Is this to the whole college? If not could you clarify areas please. | Whole college – ALL elevations. | Baily Garner | 2023-03-17 | Closed
39 | 2023-03-16 | Installation of TRV's to all existing radiators Please confirm which rooms this applies to? | To all existing radiators within the rooms undergoing refurbishment works. | Fusion | 2023-03-23 | Closed
40 | 2023-03-16 | Is there an incumbent data installer? | Data - Avente Ltd - keith.dodd@avente.co.uk - please refer to Section 2 - Preliminaries_Final_Revised | Woodley Coles | 2023-03-17 | Closed
41 | 2023-03-16 | Roof - do we include the extra over costs noted on Capital Roofing quotation for applying Moy Enkopur system to the total roof area. | You are welcome to include the cost noted in the Capital Roofing quotation, however you are not obliged to do so and may obtain your own quotations should you wish. | Fusion | 2023-03-17 | Closed
42 | 2023-03-16 | Specification for internal doors & ironmongery to be replaced required | See query 7. | Fusion | 2023-03-17 | Closed
43 | 2023-03-16 | Specification of new carpet tiles required | Please refer to 'CC FECTF - Internal Refurbishment Works' documents included on the tender portal. | Fusion | 2023-03-23 | Closed
44 | 2023-03-16 | Specification of new suspended ceiling required | Please refer to 'CC FECTF - Internal Refurbishment Works' documents included on the tender portal. | Fusion | 2023-03-23 | Closed
45 | 2023-03-16 | What rooms are to have new TRV's | To all existing radiators within the rooms undergoing refurbishment works. | Woodley Coles | 2023-03-17 | Closed
46 | 2023-03-16 | Specification for TRV's required | Pipework is imperial sized and is in steel/barrel pipe – so the TRVs need to be compatible and of the correct size – potentially 15mm or 20mm size valves will be required – the installation of TRVs will require some aspects of the heating system to be drained down and that will need the involvement of the incumbent PPM contractor (ASH) on site. Suggested TRV spec would be HERZ TS-90 Range, angle-pattern, (of correct size for each application), with ‘Herzcules’ Vandal Resistant Thermostatic Sensor – please refer to document 'TRV Specification Documents' on the contract notice. | Michael Jones & Associates | 2023-03-20 | Closed
47 | 2023-03-16 | Specification for new LED Lighting | To match the LED lighting recently installed into the T-Levels Classrooms at LGF south-west zone. MJA to be consulted to review Technical Submittals from the electrical contractor, showing lighting calcs, lighting levels, switching arrangements, fitting specification, emergency fitting spec and positions, and all as related to ensure that other LED Lighting works across the College are fully coordinated with this project. | Michael Jones & Associates | 2023-03-20 | Closed
48 | 2023-03-16 | What works are expected to be carried out for the Security Systems | All doors with access control, which are being replaced, to have access control reinstalled. Also any other elements of security disturbed by the refurbishment works e.g. new ceiling installations | Woodley Coles | 2023-03-17 | Closed
49 | 2023-03-17 | Can you provide room numbers for Ground floor where windows are being replaced. This is for decorating reference |  |  |  | Open
50 | 2023-03-17 | Where windows have been removed, is it only the affected wall to be decorated or is it the whole room. (Cannot guarantee to match colours) | See response query 15. | Woodley Coles | 2023-03-20 | Closed
51 | 2023-03-17 | Where windows are not being replaced on 2nd floor, are windows to be painted inetrnally & extenally | Existing windows are not to be painted internally or externally. Making good internally will be required where windows are being replaced. | Fusion | 2023-03-23 | Closed
52 | 2023-03-17 | The items below do not seem applicable to the works we are quoting for, could you confirm if they are or are not applicable? 2.G, 4.A, 5.A, 5.B, 5.C, 5.D, 5.E, 5.F, 5.G, 5.H, 5.J, 5.K, 5.L, 5.N, 6.A, 6.B, 6.C, 6.D | The CSA is clear in that works required to be priced are shown to be '1 item'. Notwithstanding this, should tenderers feel that any other elements of works are required under this D&B contract, they are to price accordingly. | Woodley Coles | 2023-03-17 | Closed
53 | 2023-03-17 | Where rooms are not having suspended ceilings, are these to be painted? | Ceilings to be painted as itemised in the CSA. | Woodley Coles | 2023-03-20 | Closed
54 | 2023-03-17 | All rooms on 2nd floor are having new power / data trunking. Under this clause, are we decorating all the rooms? Will this include only walls, or ceilings & woodwork too? | Localised making good and decoration unless full decoration as detailed in the CSA | Woodley Coles | 2023-03-20 | Closed
55 | 2023-03-20 | Please confirm whether an extension to the tender deadline will be granted. | A 2-week extension to the tender deadline has been granted by the College. The deadline for tender returns is now Monay 17th April 2023. No further extensions to this date will be issued. | Fusion | 2023-02-20 | Closed
56 | 2023-03-22 | Can you please confirm door and top panel colours. | This is to match existing colour. | Fusion | 2023-03-22 | Closed
57 | 2023-03-22 | Can you please confirm window colour. | This is co match existing colour. | Fusion | 2023-03-22 | Closed
58 | 2023-03-22 | Can you please confirm handle colour. | This is co match existing colour. | Fusion | 2023-03-22 | Closed
59 | 2023-03-22 | Can you please confirm any ventilation or trickle vent requirements. | Trickle vents required. | Baily Garner | 2023-03-22 | Closed
60 | 2023-03-22 | Is any obscured glazing required? | No obscured glazing is required. | Fusion | 2023-03-22 | Closed
61 | 2023-03-22 | Is any automation/AOV required? | No automation/AOV is required. | Baily Garner | 2023-03-22 | Closed
62 | 2023-03-22 | “Comar system or similar approved” specified, can we propose Smarts Eco-futural system of same or higher spec? | Contractor design. Tenderers are able to specify alternative solutions provided it meets the performance specification. | Baily Garner | 2023-03-22 | Closed
63 | 2023-03-22 | Item 4.19.22 specifies TYPE D but from the plans I believe this should be TYPE B | Agreed, this should be a Type B window not Type D. | Baily Garner | 2023-03-22 | Closed
64 | 2023-03-22 | A slightly different quantity of TYPE A & B stated on the window schedule: 18no A and 72no B. | As listed above we have just done a recount and have 19 Type A and 71 Type B. | Baily Garner | 2023-03-22 | Closed
65 | 2023-02-23 | Please provide clarity regarding scope of works on elevation to the east of the rotunda and far east elevation of the building. | No works to be undertaken on these elevations due to lack of access as a result of adjacent third-party construction works. | Fusion | 2023-03-23 | Closed