## App A - Schedule of Work
Appendix A
MCA - SCHEDULE OF WORKS
Site Address: |  | HM Coastguard Technical Training Centre, Daedalus Drive, Lee on Solent, Hampshire. PO13 9FL
Project Type: |  | Installation of a standby generator
Tenderers for the above contract should complete the tables below, indicating what they would charge for each required element. Prices must: • Be stated in Pounds Sterling; • Include all other charges and overheads associated with the element being priced.
|  | General Works, Site Conditions and Prelims: | Tender: £ | Tenderer Comments
Notes
** | Existing electrical systems are to be reviewed to ensure adequate knowledge is available to undertake the redesign appropriate to the desired outcome. |  | 0
** | Works are to be planned and scheduled to allow for controlled shutdowns for critical Search and Rescue communications equipment |  | 0
** | All works are to comply with all current legislative regulations and best practice guidance.
1 | Health, Safety & Environment
1.01 | Allow for the provision of all pre-construction safety file documentation including risk assessments, method statements, COSHH assessments, safety programs, lifting plans etc. & F10 submissions on behalf of the client (if appropriate). |  | 0
1.02 | Allow for all staff and operatives to undertake a site safety induction prior to starting work on the site. This is envisaged to last approximatly 20 minutes and can be conducted with a group of operatives if required. |  | 0
1.03 | Allow for all safety related equipment including such items as barriers, signage, confined space entry equipment, working at height access equipment and lifting equipment etc. to enable works to be carried out with minimal risk to operatives and building users. our aim is for a zero accident working environment and we encourage all staff and contractors to work toward this goal. |  | 0
1.04 | Allow for your own companies Safe Systems of Work to be utilised and provide the necessary Authorised Persons to issue work permits and safety documentation as required. |  | 0
1.05 | Allow for all approriate waste transportation licences and ensure all arrisings are removed from site and disposed of in an environmentally approved manner. Any spills are to be controlled and cleared immediately they occur, back up remediation plans / resources should be available in the event of a major spill or release of product. |  | 0
2 | Design Works
2.01 | Allow for all investigations of the existing equipment and layouts to enable modifications where necessary for the new system to function correctly on completion of the project. |  | 0
2.02 | Allow to act as the Principle Designer for all works on modification of the existing systems, installation of underground ductwork runs and to supply / install the new standby generator to support the operation of the connected load under full load for 72 hrs continuous running. |  | 0
2.03 | Allow for all local authority Planning Application requirements deemed necessary and any DNO costs in providing isolations etc. |  | 0
3 | Statement of Requirement
3.01 | Allow to supply and install an emergency Standby Generator to automatically maintain the equipment being fed from the Distribution Network Operators (DNO) 100A BS88 fuse cut-out in the event of a total power outage. The generator is to provide a SP&N supply having the capacity to run continuously for 72Hrs at full load before refuelling. The new unit is to be fully bunded, provide minimal noise disruption and comply with all legislative regulations and best practice. Alarm contacts for unit running, bund flood alarm, low fuel and unit fault conditions are to be provided, together with local tank overfill and fuel level gauge. The geographic location is considered to be local to the sea and therefore any metal or paint finishes shall be suitable for the prevailing weather conditions. |  | 0
3.02 | Allow to fill the new generator fuel tank with new red diesel oil to the recommended fill capacity. Also to provide a spill kit suitable for the capacity of the tank, which can be positioned adjacent to the generator in case of used in an emergency. |  | 0
3.03 | Allow to install a suitable earth system and lightning protection bonding conductors to ensure all items are adequately protected. |  | 0
3.04 | Allow to move the existing twin socket located on the internal east wall of the Radio Hut to make way for the new changeover switchgear. |  | 0
3.05 | Allow to supply and install a generator automatic changeover panel within the Radio Hut complete with all switchgear, also install an external load bank connection point, suitable for the prevailing weather conditions. Careful planning of this electrical shutdown is required to minimise disruption to this critical comms link. |  | 0
3.06 | Allow to install a new 40A SP&N electrical circuit from the existing Radio Hut distribution board complete with contactor operated from a new Emergency Push Off (EPO) switch to be positioned outside the Technical Training Centre (TTC) Comms Room. |  | 0
3.07 | Allow to set aside the any turf for reuse, excavate and install 3 x inspection chambers and 2 x 100mm ductwork routes between the Radio Hut and the existing inspection chamber ICBT1 , Provide sufficient segregation within the trench to prevent interference between the Comms ducts and the proposed electrical cables that are to be laid in the ground within the same trench. Allow for all bedding material and marker tapes as per best practice. Allow suitable cable entries into the Radio Hut and the TTC Server Room. |  | 0
3.08 | Allow to set aside any turf and continue the excavation and install an underground electrical supply cable and EPO control cable from the Radio Hut to the Technical Training Centre Comms Room. |  | 0
3.09 | Allow to install an EPO switch within the TTC outside the comms room adjacent to the door. Also to install a new 4 way SP&N DB at high level within the TTC Comms Room ready to provide supplies to the TTC Comms Rack and UPS. |  | 0
3.1 | Allow to disconnect and remove the existing electrical supplies feeding the TTC comms rack and UPS (DB1 Circuits 4L4 and 10L3). |  | 0
3.11 | Allow to connect the outgoing circuits from the new 4 way DB to the existing contactor at high level within the comms room. Careful planning of this electrical shutdown is required to minimise disruption to this critical comms link. |  | 0
3.12 | Allow to back fill the trench line, level the ground, replace grass where possible and re-sow areas using suitable grass seed where needed. Relay the turf set aside during excavation. |  | 0
3.13 | Allow to supply and install all warning signage appropriate to having a separate electrical supply within the TTC. |  | 0
4 | Completion
4.01 | Allow for the provision of 2 x electronic copies on CD Rom and one printed hard copy of all commsionning certification, test sheets, manufacturers information, user operation and engineers service and maintenance guides, suppliers contact information, disposal information etc. together with full layout and schematic drawings of the complete install in DWG. & PDF. formats. This information is to be presented in a post-construction health and safety file format. |  | 0
4.03 | On completion the Contractor to undertake deep clean of working areas and leave the premises clean and tidy, free from dirt, dust and any builders waste and plant. |  | 0
5 | Preliminaries & Overheads
5.01 | Prelims |  | 0
5.02 | Overheads & Profit |  | 0
| TENDER TOTAL |  | 0
| VAT |  | 0
| TOTAL INCLUSIVE OF VAT |  | 0
The nominated Procurement Manager is:
Kathy Monk
Finance & Contracts
Bay 3/19 – Spring Place
105 Commercial Road
Southampton
SO15 1EG
Tel:- 020 381 72328
Email: - Contracts@mcga.gov.uk
| Signed: | Name (Block Capitals):
in the capacity of:
duly authorised to sign tenders for and on behalf of (in BLOCK CAPITALS):
Postal Address:
| Telephone No: | Email:
Date: