CIVIL, ELECTRICAL & MECHANICAL

WORKS CONTRACT
DIO RD OS TRG (Kenya)

BATUK

BOOKLET 3

SPECIFICATION

LUMP SUM FIRM PRICE CONTRACT FOR KEN/GE/1901

PERIMETER SECURITY LIGHTS

&

CONSTRUCTION OF FUEL STORAGE FACILITY

CIVIL, ELECTRICAL AND MECHANICAL WORKS CONTRACT

References

- BS 7671: Requirement for electrical installations.  IET wiring regulations 18th Edition Amendment 1.

- JSP 375 MOD Health and Safety Handbook.

- UK Health and Safety at Work Act 1974 (HASAWA).

- Provision and Use of Work Equipment Regulations (PUWER) 1998.

- Construction (Design & Management) Regulations 2015 (CDM2015).

- BS EN 60947: Low-voltage switchgear and control gear assemblies.

- BS EN 60529:1992+A2:2013: Degrees of protection provided by enclosures (IP Code).

- BS 7430 Code of practice for protective earthing of electrical installations.

- Electricity at Work Regulations 1989, Third Edition, 2015.

- BS EN 61439-3: Low-voltage switchgear and control gear assemblies, distribution boards intended to be operated by ordinary persons.

- BS 5489-1:2013 Code of practice for the design of road lighting, Part 1: Lighting of roads and public amenity areas.

- PD CEN/TR 13201-1:2004 Road lighting – Part 1 Selection of lighting classes.

- BS 5489-1:2013 Code of practice for the design of road lighting, Part 1: Lighting of roads and public amenity areas.

- BS EN 13201-2:2003 Road lighting – Part 2: Performance requirements.

- CIBSE lighting guide (LG06).

- BS EN 40.  Part 1-5 – lighting columns.

- BS EN 1992-1-1:2004: Euro code 2.  Design of concrete structures general rules and rules of the buildings.

- BS 5950:2000(1990) - Structural use of steelwork in building.

- BS EN 1011 Series – Welding guidelines.

- BS EN 60529:1992+A2:2013: Degrees of protection provided by enclosures (IP Code)

- BS 5228_Code of practise for noise and vibration control on construction and open sites

- BS EN 858-2 Separators systems for light liquids- part 2: selection of nominal size, installation, operation and maintenance.

- Pollution Preventive Guide 03.

- JSP 317- Defence fuels policy, Organization and safety regulations part 2 Vol 1,3 and 4

- Design and maintenance guide 14.

- BS 8004:2015 Code of practice for foundations.

- BS EN 206:2013 Concrete - specification, performance, production and conformity.

- BS EN 62305-1:2011 Protection against lightning.

- British Standard 5228: Code of practice for noise and vibration control on construction.

- Asbestos Prohibitions Regulations 1985 and the Asbestos Products (Safety) Regulations 1985.

- JSP 375 part 2 volume 3 SSOW.

- BS EN 16907-1:2018 – earthwork principle and general rules.

- BS6031:2009 – code of practice for earthworks.

- BS EN 12620:2013 - Specification for aggregates from natural sources for concrete.

- BS EN 12390 – Testing hardened concrete and 12390-2 making and curing specimen for strengths tests.

- BS 4482-2005 - Steel wire for the reinforcement of concrete products.

- BS EN 12350-2:2009 Testing fresh concrete. Slump test.

CIVIL, ELECTRICAL AND MECHANICAL WORKS CONTRACT

Supporting documents

- The Drawing attached to this document is to be read in conjunction with this Performance Specification (PS).  It shall be noted that this Drawing is ‘Concept Only’ and the Contractor is to produce a full set of design documentation and confirm quantities and distances.

# Contractors design

- The Contractor is to advise the Project Manager (PM) of all design consultants / sub-contractors who will be employed on this Contract and the areas of their design responsibility.  Any works undertaken without prior issue of full information for the necessary approvals will be entirely at the Contractor’s own risk.

- The Contractor shall not commence any work in accordance with any Design Document until the PM has agreed the relevant Design Document.  The Contractor shall keep one copy of each Design Document on the Site, to which the PM or his representatives may have access at all reasonable times.

# Design responsibilities

- Contractors design responsibilities.  The Contractor is responsible for the design of all elements contained within the schedule of Works.  Where required, all designs are to be submitted to the Authority for concurrence and authorisation prior to implementation of Works.  Where the nature of works does not warrant full design, a descriptive proposal complete with proposal sketch must be submitted for concurrence.  The Contractor shall ensure all designs are in accordance with, and include the applicable requirements as contained within Refs A to II and all other design documents specified within this PS.  It shall be noted that these references are provided as guidance and minimum requirement only; the responsibility remains with the Contractor to ensure that all design and construction works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the works, geography, climate, environment and theatre of operations.  Where there are conflicts between the Contractor’s design Drawings and the PS (Booklet 3), the PS will take precedence in all cases.  Any queries shall always be addressed to the Authority in the first instance.  The references and specified British Standards (BS) / Euro Norms (EN), within this PS are to be used (or similar Authority approved standards) as a minimum standard, throughout the Works.

- UK Building Regulations.  All works shall comply with the latest UK Building Regulations.  Shall any variation be required, approval from the Authority shall be obtained in writing prior to the commencement of any Works.

- Health and Safety (H&S).  All works shall be carried out in accordance with the Health and Safety at Work Act 1974 (HASAWA).  The Contractor shall submit a Construction Health and Safety Plan (CHASP) to the Authority for approval, including but not limited to all risk assessments, method statements, and procedures for transport, storage, handling and disposal of hazardous materials.

- Construction Drawings.  All works shall be constructed in accordance with the final approved Contractor furnished construction Drawings (or written proposal in this case).  Where a conflict in design is found, authorisation shall be obtained in writing prior to any changes in design.  No construction shall commence prior to obtaining written approval of the final construction Drawings / proposal by the Authority.  All project changes will be conducted in accordance with Booklet 2 para 61, change control procedures.

- Design life.  The design life of all new electrical and structural components and assemblies to first major overhaul, repair or replacement shall be a minimum of several years as stated on each section project tasks.  The Contractor shall supply and install all components, elements and systems / structures to satisfy this requirement, and any additional Contractual requirements that may apply.

- Existing services.  The Contractor is responsible for ensuring all services on or adjacent to the site that will be affected by the works are identified, located and appropriate action taken to prevent damage before work commences.  The Contractor shall ensure that any existing services and concrete slabs are reinstated to a condition at least similar to existing, with the minimum of disruption to existing facilities and services during construction.  All works that could possibly influence existing services may only commence with written approval.  The Authority must be informed immediately if any unknown services are discovered that will have an impact on the works.  The Contractor shall ensure that any existing services and affecting Works – including all connections and services tied into – are of an acceptable standard to ensure the required performance over the life of the facility.  Shall it be found that one or more of the services (including but not limited to existing water, sewerage, drainage and electrical reticulation) is not considered acceptable to the requirements, the Contractor shall inform the Authority and obtain written approval / instruction prior to taking any actions to rectify or make good the pertinent unacceptable situation.

# Construction preliminaries

- Existing ground conditions.  The Contractor is responsible for confirming the existing ground conditions, which are to be taken into account whilst designing and compiling the CHASP.

- Obstructions.  As the proposed works are to be carried out around existing infrastructure and surrounding areas, there are obstructions in the form of fences and buildings etc, the Contractor is to review the site before commencing works.

- H&S restrictions, precautions and monitoring.  The Contractor shall implement the requirements described in the Health and Safety at Work Act 1974 (HASAWA) to protect members of the public and persons visiting the site from risks arising from the use of equipment, materials or substances defined therein.

- Control of noise and vibration.  The Contractor shall comply with the recommendations for practical measures to reduce noise set out in BS 5228: Parts 1, 2 and 4 - Code of practice for noise and vibration control on construction and open sites.

- Contractors laydown area.  It is expected that the Contractor will not require a forward resources area other than the site.  Shall one be required a location shall be made available, as agreed by the PM.

- Contractors logistics.  Packaging shall be to a good standard capable of withstanding transportation and handling loads.  The Contractor shall be solely responsible for storage and movement of all equipment to site.  The Contractor shall remain at all times responsible for the security of equipment including prevention of theft.

Section 1 Operating base perimeter security lights

# Proposed works

- Key project details.  The key project details are shown below:

| Contract title: Site location: | 1901 – Electrical and Mechanical Works. Operating Base (OB) Simba, OB Twiga, OB Swara. |
| --- | --- |
| Proposed start date: | 7 Oct 2019. |
| Proposed completion date: | 8 Jan 2020. |
| Retention: | 5% (reduced to 2.5% if completion achieved on planned date). |
| Defects liability period: | 12 Months – Note that an inspection must take place 3 – 4 weeks prior to the end of the defects liability period. The retention payment will not be paid until this, and any works arising from that inspection, have been completed. |
| Design life: | 15 years. |

Task description

- Decommissioning existing perimeter lighting and installation of new perimeter lighting system to comply with Ref A, B and C in the following location:

  - Operational Base (OB) Simba.

  - Operational Base (OB) Twiga.

  - Operational Base (OB) Swara.

Background information

- The security light fittings are installed by use of approximately 2.5 metres high 73mm diameter steel round poles, the columns are mounted on top of the HESCO and the light fittings are fitted on top of pole permanently on a square framework.  The entire perimeter fence security lights are linked together by means of non-Ingress Protection (IP) 2X feeder pillars.

- The proposed task location can be seen on Drawing (Dwg) No. DIO/KEN/SIM/G/001 Site plan, DIO/KEN/TWI/G/001 Site plan and DIO/KEN/SWA/G/002 Proposed perimeter security lights plan.  Exact building locations and orientation are to be confirmed with the Authority.

Requirements

- The requirement for the task is to decommission the existing perimeter lights and install new perimeter fence lighting systems to comply with Ref A, B and C in the following locations:

  - OB Simba perimeter lighting.  Design and build a new perimeter wall lighting system, including:

    - Concrete plinth for enclosures.

    - Concrete plinth for lighting columns.

    - Enclosure for distribution board.

    - Lowerable steel frame lighting columns that are easy to maintain.

    - White light LED lamp.

    - Timer control panel.

(7)	De-commissioning of existing Low Voltage (LV) cables, lighting columns and feeder pillars.

(8)	Installation of LV power underground to support perimeter lights in accordance with Ref A.

  - OB Twiga perimeter lighting.  Design and build a new perimeter wall lighting system, including:

    - Concrete plinth for enclosures.

    - Concrete plinth for lighting column.

    - Enclosure for distribution board.

    - Lowerable steel frame lighting columns that are easy to maintain.

    - White light LED lamp.

    - Timer control panel.

    - De-commissioning of existing LV cables, lighting columns and feeder pillars.

    - Installation of LV power underground to support perimeter lights in accordance with Ref A.

  - OB Swara perimeter lighting.  Design and build a new perimeter fence lighting system, including:

    - Concrete plinth for enclosures.

    - Concrete plinth for lighting column.

    - Enclosure for distribution board.

    - Lowerable steel frame lighting columns that are easy to maintain.

    - White light LED lamp.

    - Timer control panel.

    - De-commissioning of existing LV cables, lighting columns and feeder pillars.

    - Installation of LV power underground to support perimeter lights in accordance with Ref A.

Scope of works

- The following scope of work shall be carried out in conjunction with the related OBs:

  - Demolition of existing perimeter lights, poles, associated LV power and accessories.

  - Trench excavation.

  - Construction of sub base and casting of concrete plinth for enclosures including entry ducts.

  - Construction of sub base and casting of concrete plinth for lighting columns including entry ducts.

  - Installation of ductwork.

  - Installation of lighting cables in accordance with Ref A.

  - Erecting of lighting columns.

  - Installation of timer controller systems.

  - Testing and commissioning of the system in accordance with Ref A.

Performance specifications

- The following performance specifications are to be considered into the contractor’s design.

a.	Trenching.  All trenches for the ducting shall be 600mm deep.  A warning tape shall be placed above duct works.  Warning tape shall be laid at a depth of 300mm below the finished surface level.

b.	Ducting.  All underground armoured cables shall be installed inside 110mm, Unplasticised Polyvinyl Chloride (uPVC) heavy gauge ducting.  They shall be at least 150mm away from existing water pipes, drains, sewers and electrical plant.  Where services cross, the clearance between them shall be not less than 50mm.  On completion the ends of the ducts must be sealed with expanding foam to avoided ingress of unwanted foreign objects and insects.

c.	Cable.  The Contractor shall carry out calculation and size all conductors in accordance with Ref A (including earth cable).  All underground cables shall be XLPE insulated armoured cables and the earthing system shall be TN-S system i.e. separate earth conductor.  All necessary precautions shall be taken to prevent damage and ingress of moisture and impurities when terminating cables.  Cable ends must be free from moisture before jointing commences.  All cable types shall be BSEN compliant or similar and complies with new colour coding.

(1)	L1 - Brown

(2)	L2 - Black

(3)	L3 - Grey

(4)	Neutral - Blue

(5)	Earth - Yellow/green

d.	Inspection chamber.  All underground ductwork shall have a minimum of 400 x 400mm concrete inspection chambers (IC’s) at a distance span of 30 metres and at any direction change of the ductwork.

e.	Concrete plinths for feeder pillars and lighting columns.  The Contractor shall carry out load calculations for the concrete plinths for feeder pillars and lighting columns.  All feeder pillars and lighting columns shall be installed a distance of 2m away from the existing HESCO walls at OB Simba and Twiga and perimeter fence at OB Swara.  All concrete plinths shall protrude 50mm above the ground level and be adequately reinforced and cured.  Cube tests shall be carried out for each batch of concrete.  Anchor bolt shall be concreted in-situ and shall be designed to take a shear load imposed by the structure.  Concrete specification shall be read together with the general points in this document.

f.	Lighting column.  The Contractor shall carry out a lighting design in accordance with Ref A to P and identify the number of columns required and space out lighting columns as per their design in all OB’s.  All lighting columns shall be minimum 2m away from the existing HESCO walls at OB Simba and Twiga and perimeter fence at OB Swara and a maximum of 8m in height.  All lighting columns shall be constructed from hot dipped galvanised mild steel hollow sections cold and hot rolled steel sections or slotted angles, in accordance with Ref P.  All lighting columns shall be bolted in position with the anchor bolt concreted into the reinforced concrete plinths.  All lighting columns shall have a mechanism to lower the light fittings for maintenance, with all lowering equipment incorporated or provided.  All bolts, nuts, washer and screws used in the construction of the lighting columns and bases shall be hot dipped galvanised compatible with use in the local environment.  All lighting columns shall be with 2 No. outreach arms and 2 No. lighting units, one each side of the column to achieve a greater column span whilst still achieving even coverage and the minimum of 5 lux levels.  Each column shall be fitted with a protective device (Miniature Circuit Breaker (MCB) CB or BS 88 fuse) for the column lights, providing terminations adequate for running cables in parallel.  Covers giving access to fused cut-outs/termination block shall require a unique tool to open and shall have a rubber rings to avoid ingress of insects, dust and water.  All lighting columns shall be earth with the adequately sized earth cable.

g.	Luminaires.  The Contractor shall carry out a lighting design and identify the number and size of luminaries required for all OB’s.  All luminaries shall be White LED and IP rated 65.  A minimum horizontal illumination shall be 5 lux level operational at uniformity 5m away from the inside and 3m away from the outside of the existing HESCO walls at OB Simba and Twiga and perimeter fencing at OB Swara.  All entrances and emergency exit gates shall have a minimum of 150 lux level for the purpose of security check.  There shall not be any unlit areas around the perimeter less the shadow produced from the existing HESCO walling.

h.	Lighting control system.  All perimeter lights shall be controlled with a timer switch installed inside the enclosures.  There shall be a facility for one manual over ride switch that can be used to turn off all perimeter lights for Helicopter landing at night time.  The override switch shall be installed at the Operations room in each OB’s.  All MCB’s shall be double pole Schneider brand or similar approved.

i.	Enclosures and distribution board.  The Contractor shall carry out cable and lighting calculation and identify the number and size of distribution board (DB) required.  All DB shall be mounted inside IP44 rated enclosure that has sufficient space for cables termination and mounting the DB inside.  The enclosure shall be bolted in positioned with anchor bolt concreted in the reinforced concrete plinth.  All DB’s and enclosures shall be constructed from galvanised mild steel painted in grey.  All DB’s shall be minimum of IP 2X rated when doors are open and IP 44 when doors are closed, and it shall be lockable.  All enclosures shall be placed a minimum of 2m away from the existing HESCO walls at OB Simba and Twiga and perimeter fence in OB Swara inside the OB’s and it shall be earthed.

j.	Existing power supply.  There are numbers of existing Local Distribution Units (LDU) inside the OB’s.  The Contractor shall utilise the nearest existing power supply where possible.  On formal request from contractor, the duty Authorised Person (Electrical)/ Skilled person (Electrical) will isolate the power supply and the contractor shall carry out commissioning of the cables as required.

k.	Decommissioning existing perimeter lighting system.  All lighting columns at OB Simba and Twiga shall be cut down at the level of the top of the existing HESCO walling without damaging any HESCO wall and ground down, de-burred and capped to prevent a future injury hazard.  OB Swara lighting columns shall be fully decommissioned including removal of the base and making good to the ground.  All underground cables shall be cut down to 300mm below the surface level and left buried under the ground.  All surface laid ducting and cable shall be stripped out and disposed of.  All existing light fittings from all OB’s shall be handed over to the Authority.  Disposal of the existing perimeter lighting components shall be in accordance with NEMA regulation and or guidance.  The Contractor shall arrange for waste removal by a registeredcontractor for waste disposal in accordance with Ref W.  The Waste Transfer Note shall be handed to the Authority.  Additionally, hazardous waste is to be placed in suitable sealed containers.

Section 2a Operating base fuel storage facility – (POL point)

# Proposed works

- Key project details.  The key project details are shown below:

| Contract title: Site location: | 1901 – Fuel Works (Construction of fuel storage facility). Operating Base Simba (OB Simba). |
| --- | --- |
| Proposed start date: | 7 Oct 2019. |
| Proposed completion date: | 9 Dec 2019. |
| Retention: | 5% (reduced to 2.5% if completion achieved on planned date). |
| Defects liability period: | 12 Months – Note that an inspection must take place 3 – 4 weeks prior to the end of the defects liability period. The retention payment will not be paid until this, and any works arising from that inspection, have been completed. |
| Design life: | 15 years. |

Task description

- OB Simba Proposed works consist of the following:

  - Decommissioning, demolition and disposal of existing fuel storage cage size 11.2 m (L) x 2.8 m (W) 2.7 m (H) with the existing concrete slab staying in situ.

  - Decommissioning, demolition and disposal of existing Oil Water Interceptor (OWI) size 1.92 m (L) x1.10 m (W) x1.71 m (H).

  - Construction of new fuel storage cage size 11.2 m (L) x 2.8 m (W) 2.7 m (H).

  - Construction of new OWI.

- The proposed task location can be seen on Dwg No.  DIO/KEN/SIM/G/001 Site plan.  Exact building locations and orientation are to be confirmed with the Authority.

Requirements

- The task requires the demolition of an existing underground RC concrete OWI, fuel cage and construction of a new OWI and fuel storage cage.  Based on following requirements.

  - Decommissioning of fuel storage cage that includes:

    - Decommissioning and disposal of alarm and Lightning Protection System (LPS).

    - Demolition and disposal of roof and side frame structure.

    - Cleaning and making good all affected areas.

  - Demolition and disposal of existing OWI:

    - Obtain required permits to decommission OWI.

    - Decommissioning and disposal of interceptor contents.

    - Decommissioning and disposal of interceptor furniture and alarms.

    - Demolition of the concrete structure and covers.

    - Backfilling the open excavation.

    - Levelling and making good to match existing surrounding.

  - Construction of fuel storage cage that involves:

    - New fuel storage cage to be size 11.2 m (L) x 2.8 m (W) 2.7 m (H) with four equal chambers to be fixed on existing ground slab.

    - Steel metal frames with heavy gauge mesh wire infill sidewalls.

    - Steel metal frame roof structure with gauge 28 CGI roof cover.

    - Extension of concrete drainage with wrought iron cover grating.

    - Installation of lightening protection system.

  - Construction of new OWI that includes:

    - Construction of concrete underground oil water interceptor.

    - Steel metal covers.

    - Installation of solar powered alarm systems with battery pack.

    - Drainage to be connected to existing drainage systems.

    - Installation of MS steel bollards.

Scope of works for OB SIMBA

- Project is to be completed in 2 phases:

  - Construction of new facility indicated on Dwg No.  DIO/KEN/SIM/G/001 that can be found in Booklet 4:

    - Sub-structure to include but not limited to:

      - Groundwork.

      - Drainage below ground.

      - Foundations and concrete works.

    - Cage structure to include but not limited to:

      - Construction of steel framed structure.

      - Construction of steel framed roof with CGI cladding.

      - Installation of doors similar to the steel structure.

      - Finishes to concrete and steel surfaces.

      - Lightning protection.

    - OWI with devices:

      - Concrete chambers.

      - Connection of inlet and outlet pipe work.

      - Fixing of steel covers.

      - Finishes to concrete and steel surfaces.

      - Fixing of signage.

      - Installation of alarm detection system.

      - Installation of steel bollards for protection.

    - Testing and commissioning of alarm and LPS to Ref AA.

  - Decommissioning of existing OWI and fuel cage:

    - Inspection.  Test contents of OWI.

    - Decommissioning.  Isolate services.

    - Demolition.  Demolish Roof, side and OWI.

    - Disposal.  Dispose of different materials appropriately as per NEMA.

    - Backfilling.  Backfill in open holes.

    - Making good.  Level affected areas and clean off.

Performance specification

- In conjunction with Dwg No.DIO/KEN/SIM/G/001.  The following is to be considered into the contractor’s design:

  - Groundwork.  The contractor is to inspect the ground, check level and soil condition where necessary excavations are to be carried out carefully and excavated materials set aside for disposal.  The excavation shall be kept free of water and fallen materials, where the excavated sides are not firm extra shoring shall be used to contain the soil.  Open excavation shall shall be protected, suitable signage erected, and a banks man employed when vehicles are manoeuvring.  Backfilling shall be completed utilising suitable materials and compacted in 75mm layers to achieve the bearing strength enough to safely carry the imposed loads without settling.

  - Earthworks.  All earthworks to be governed by Ref. FF and GG.  Excavation for any foundation works shall be a minimum of 1m below ground depending on different ground conditions and  allow for safe working space.  Filling shall be compacted in layers not more than 75 mm depending on the type of equipment and number of passes.  Shaping of the fill shall be checked continuously to ensure an accurate profile.

  - Drainage below ground.  Drainage shall be completed in a manner that compliments the existing drainage system and in accordance with Ref W.  The drainage shall be able to contain the spillage flow of fuel stored within the cage plus storm water as a result of rainfall.  An extension of approximately 10m length to match the existing drainage system is to be constructed to the kerb line.  The existing drain is of concrete construction with heavy gauge wrought iron grating, the size is 300x250mm.

  - Foundations and concrete works.  The Contractor is to design a foundation to suit the structural design load of the building and geology of the site.  All foundations and concrete works shall be carried out in accordance with Ref D, Q, Z and AA.

  - Construction of steel framed structure.  The steel structure is to be fabricated and erected to match the existing structure using the existing location.  The structure is to be made of steel sections, and wire mesh infill, the structure shall be designed to withstand all self-imposed loads and external wind loads.  All steel is to be as per Ref R and S.  Supply and install Mild Steel (MS) Hollow Section (HS) fixed to existing concrete base preferably bolted with a base plate, vertical members to be of enough size to carry the roof members/own imposed weight.  The vertical members are to be strengthened with horizontal members and braced with diagonal members to provide a rigid structure, the structure is to be enclosed with heavy duty wire mesh with an openable double leaf gate for each of the four compartments.

  - Construction of steel framed roof with CGI cladding.  The roof structure is to consist of steel girder trusses, purlins strengthened firmly to prevent sag.  The roof cover is to be pre-painted corrugated sheets, gauge 28 fixed with J bolts and a matching ridge cap.  Provide steel plate fascia with steel gutters and down pipes sized sufficiently to contain water from the gutters.  Gable sides are to be fitted with heavy gauge mesh wire all the way to the ridge to match the bottom mesh wire.  The steel used is to be as per Ref R and S

  - Installation of doors.  Doors shall be of similar material as per the steel structure described at Paragraph 28 d.  The door shall be a double door opening to the outside and large enough to allow the movement of a folk lift with pallets containing up to 21 containers of fuel each 20 litres.

  - Finishes to concrete and steel surfaces.  The steel structure is to be free from any sharp edges; all metalwork is to be free from rust before priming with a grey primer and finished with 3 layers of black metal paint.  All welds to be welded in a continuous line as per Ref R.  All concrete surfaces must be finished smooth with steel trowel.

  - Lightning protection.  A LPS risk assessment is to be undertaken to determine the LPS classification required.  A LPS is to be installed that satisfies the risk assessment in accordance with Ref BB.

  - OWI concrete chambers.  To be designed to meet the following criteria:

    - The OWI shall be designed to be a class 1 separator.  Class 1 separators are designed to achieve a discharge concentration of less than 5 mg/litre of oil under standard test conditions.  These separators are required for discharges to surface water drains.  The oil water interceptor is to be designed to a Forecourt separator type as per Ref V.

    - The OWI is to be large enough to take all spillage from the storage cage stored fuel, the cage has a maximum storage of 13440 litres of oil.

    - A correct size vent pipe shall be installed minimum 2.4 m high with none return valve and a bend at top facing downwards.

  - Connection of inlet and outlet pipe work.  A new pipework connection shall be made properly to the existing drainage with no leakages and an inspection chambers easily accessible for maintenance.

  - Fixing of steel covers.  Steel covers shall be lockable and easily opened by hand, strong enough to bear imposed loads by accidental stepping or driving on.  Steel works to be as per Ref R and S.

  - Fixing of signage.  The OWI is to be marked with a visible label that is durable containing the following information:

    - Manufacturer’s reference number and year of manufacture.

    - Oil storage capacity.

    - Volume of separator.

    - Type of separator.

  - Alarm detection system.  The following devices shall be fitted:

    - The interceptor shall be fitted with an automatic closure device that will prevent flow passing through the separator when the quantity of the oil in the separator exceeds the oil storage volume.

    - The interceptor shall be fitted with a robust device to provide a visual warning when the oil level reaches 90% of the oil storage volume under static liquid level conditions.  All electrical devices used to be ATEX rated.

  - Bollards.  Bollards are to be designed and installed to meet the following criteria:

    - Strong enough to resist impact of 10 tonne moving vehicle at a speed of 20km/h.

    - High enough such that they cannot be run over by vehicles.

    - Spaced at intervals such that no vehicle (pick up size) can pass through the gap.

    - Painted with highly visible contrasting in yellow and black.

  - Test contents of OWI.  Contents of the existing OWI shall be tested for the presence of any oil pollutants.  Test results shall be analysed for proper disposal as per the NEMA regulations.

  - Isolation of services.  Isolate all services including but not limited to, drainage, lightning protection, and power.  Authority permission is to be acquired prior to isolating any services.

  - Demolition.  Demolish all parts of the cage and OWI.  Demolition shall be done carefully and systematically starting from top to bottom.  Measures to control noise and dust shall be in place in accordance Ref BB.

  - Backfill in open holes.  Exposed holes after demolition shall be back filled.  Backfilling shall be carried out with selected suitable materials and compacted to achieve the bearing strength enough to safely carry the imposed loads without settling.

  - Level affected areas and clean off.  All affected areas after completion of the work shall be made good.  This shall include but not limited to levelling the site, sweeping debris and disposal, reinstating any planted maintained vegetation, reinstating affected existing building.

Section 2b Operating base fuel storage facility – (POL Point)

# Proposed works

- Key project details:  The key project details are shown below:

| Contract title: Site location: | 1901 – Fuel Works (Construction of fuel storage facility). Operating Base Twiga (OB Twiga ). |
| --- | --- |
| Proposed start date: | 7 Oct 2019. |
| Proposed completion date: | 8 Jan 2020. |
| Retention: | 5% (reduced to 2.5% if completion achieved on planned date). |
| Defects liability period: | 12 Months – Note that an inspection must take place 3 – 4 weeks prior to the end of the defect’s liability period. The retention payment will not be paid until this, and any works arising from that inspection, have been completed. |
| Design life: | 15 years. |

Task description

- The proposed works consist of the following:

  - Decommissioning, demolition and disposal of existing underground RC concrete fuel storage cage size 3.93 m (L) x 2.65 m (W) x 2.5 m (H) with the existing concrete slab staying in site.

  - Decommissioning, demolition and disposal of existing OWI size 1.92 m (L) x 1.10 m (B) x 1.71 m (H).

  - Construction of new fuel storage cage size 11.2 m (L) x 2.8 m (W) 2.7 m (H)

  - Construction of new OWI.

- The proposed task location can be seen on Dwg No.  DIO/KEN/TWI/G/001 Site plan.  Exact building locations and orientation are to be confirmed with the Authority.

Requirements

- Task requires the demolition of existing OWI, fuel cage and construction of new OWI and fuel storage cage.  Based on following requirements.

  - Decommissioning of fuel storage cage includes the following:

    - Decommissioning and disposal of alarm and LPS.

    - Demolition and disposal of roof and side frame structure.

    - Cleaning and making good all affected areas.

  - Demolition and disposal of existing OWI includes the following:

    - Obtain required permits to decommission OWI.

    - Decommissioning and disposal of interceptor contents.

    - Decommissioning and disposal of interceptor furniture and alarms.

    - Demolition of the concrete structure and covers.

    - Backfilling the open excavation.

    - Levelling and making good to match existing surrounding.

  - Construction of fuel storage cage is to be as follows:

    - Construction of the new concrete slab to accommodate the cage and a circulation area for offloading and loading and drainage system to connect with the OWI.  The circulation area to accommodate one 20 tonne truck being loaded or offloaded.  This area shall be designed such that any spillage will flow to the drain connected to the OWI.

    - New fuel storage cage to be size 11.2 m (L) x 2.8 m (W) x 2.7 m (H) with four equal chambers to be fixed on the newly constructed ground slab serial 1.

    - Steel metal frames with heavy gauge mesh wire infill sidewalls.

    - Steel metal frame roof structure with gauge 28 CGI roof cover.

    - Extension of concrete drainage with wrought iron cover grating.

    - Installation of lightning protection system.

  - Construction of new OWI is to include the following:

    - Construction of concrete underground oil water interceptor.

    - Steel metal covers.

    - Installation of solar powered alarm systems with battery pack.

    - Drainage to be connected to existing drainage systems.

    - Installation of steel bollards.

Scope of works for OB TWIGA

- Project is to be completed in 2 phases:

  - Construction of new facility indicated on Dwg No.  DIO/KEN/TWI/G/001 Site plan

    - Sub-structure to include but not limited to:

      - Groundwork.

      - Drainage below ground.

      - Foundations and concrete works.

    - Cage structure to include but not limited to:

      - Construction of steel framed structure.

      - Construction of steel framed roof with CGI cladding.

      - Installation of doors similar to the steel structure.

      - Finishes to concrete and steel surfaces.

      - Lightning protection.

    - OWI with devices:

      - Concrete chambers.

      - Connection of inlet and outlet pipe work.

      - Fixing of steel covers.

      - Finishes to concrete and steel surfaces.

      - Fixing of signage.

      - Installation of alarm detection system.

      - Steel bollard for protection.

    - Testing and commissioning of alarm and LPS to Ref. BB.

  - Decommissioning of existing OWI and fuel cage:

    - Inspection. Test contents of OWI.

    - Decommissioning.  Isolate services.

    - Demolition.  Demolish Roof, side and OWI.

    - Disposal.  Dispose of different materials appropriately as per NEMA.

    - Backfilling.  Backfill in open holes.

    - Making good.  Level affected areas and clean off.

Performance specifications

- In conjunction with Dwg No.  DIO/KEN/TWI/G/001 Site plan.  The following data will need to be considered into the contractor’s design.

  - Groundwork.  The contractor is to inspect the ground, check level and soil condition where necessary.  Excavations to be carried out carefully and excavated materials set aside for disposal.  Excavation shall be kept free of water and fallen materials, where the excavated sides are not firm extra strutting shall be used to contain the soil.  All the time the open excavation shall be protected and proper signage erected.  Backfilling shall be carried out with selected suitable materials and compacted to achieve the bearing strength enough to safely carry the imposed loads without settling.

  - Drainage below ground.  The extension of drainage system shall be in a manner to fit in with the existing drainage system and shall comply to Ref W.  The drainage shall be able to contain spillage of fuel stored within the cage plus storm water as a result of rainfall.  An extension of existing drainage matching same specification is to be constructed up to existing kerb line approximately of 10m length.  The existing drain is concrete drain with heavy gauge wrought iron grating, the size is 300 mm x 250 mm.

  - Foundations and concrete works.  The Contractor is to design a foundation to suit the structural design loadings of the building and geology of the site.  All foundations and concrete works shall be carried out in accordance with Ref D, Q, Z and AA.

  - Construction of steel framed structure.  Steel structure is to be fabricated and erected to match the existing structure and in the same location as the existing one.  The structure is to be made of steel sections, and wire mesh infill, the structure shall be designed to withstand all self-imposed loads and external wind loads.  Steel to be as per Ref R and S.  Supply and install Mild Steel (MS) Hollow Section (HS) fixed to existing concrete base preferably bolted with a base plate, vertical members to be of enough size to carry the roof members/own imposed weight.  The vertical members to be strengthened with horizontal members and braced with diagonal members to provide a rigid structure, the structure to be enclosed with heavy duty wire mesh with an open able double leaf gate for each of the four compartments.

  - Construction of steel framed roof with CGI cladding.  Roof structure to consist of steel girder trusses, purlins strengthened firmly with, bracers, anti-sag rods etc. roof cover to be pre-painted corrugated sheets, gauge 28 fixed with J bolts and a matching ridge cap.  Provide steel plate fascia with steel gutters and down pipes sized enough to contain water from the gutters.  Gable sides to be fitted with heavy gauge mesh wire all the way to the ridge to match the bottom mesh wire.  Steel to be as per Ref R and S.

  - Installation of doors.  Doors shall be of similar material as per the other steel structure described above Paragraph 34 d.  The door shall be double door opening to the outside and big enough to allow movement of loading forklift the pallets to be loaded take up to 21 containers of fuel each 20litres.

  - Finishes to concrete and steel surfaces.  Steel structure to be free from any sharp edges; all metalwork is to be free from rust before priming with a grey primer and finished with 3 layers of black metal paint.  All welds to be welded in a continuous line as per Ref R.  All concrete surfaces must be finished smooth with steel trowel.

  - Lightning protection.  A LPS risk assessment is to be undertaken to determine the LPS classification required.  A LPS is to be installed that satisfies the risk assessment in accordance with Ref BB.

  - OWI concrete chambers.  To be designed to meet the following criteria.

    - The oil water interceptor designed to be a class 1 separator.  Class 1 separators are designed to achieve a discharge concentration of less than 5 mg/litre of oil under standard test conditions.  These separators are required for discharges to surface water drains.  The oil water interceptor is to be designed to a Forecourt separator type as per Ref V.

    - To be big enough to take all spillage from the storage cage stored fuel, the cage has a maximum storage of 13440 litres of oil.

    - A correct size vent pipe shall be installed minimum 2.4 m high with none return valve and a bend at top facing downwards.

  - Connection of inlet and outlet pipe work.  New pipework connecting to the existing drainage shall be well connected to the new to with no leakages and an inspection chambers easily accessible for maintenance.

  - Fixing of steel covers.  Steel covers shall be lockable easily opened by hand, strong enough to bear imposed loads by accidental stepping or driving on.  Steel works to be as per Ref R and S.

  - Fixing of signage.  Interceptor to be marked with a visibly label that is durable containing below information;

    - Manufacturer’s reference number and year of manufacture.

    - Oil storage capacity.

    - Volume of separator.

    - Type of separator.

  - Alarm detection system.  The following devices shall be fitted:

    - The interceptor shall be fitted with an automatic closure device that will prevent flow passing through the separator when the quantity of the oil in the separator exceeds the oil storage volume.

    - The interceptor shall be fitted with a robust device to provide a visual warning when the oil level reaches 90% of the oil storage volume under static liquid level conditions.

  - Bollards.  The bollards are to be designed to meet the following criteria.

    - Strong enough to resist impact of medium weigh 10 tonne moving vehicle at speed of 20km/h.

    - High enough such that they cannot be run over by vehicles.

    - Spaced at intervals such that no vehicle (pick up size) can drive in between.

    - Painted with highly visible colours.

  - Test contents of OWI.  Contents of OWI shall be tested for the presence of any oil pollutants.  Test results shall be analysed for proper disposal.

  - Isolate services.  Isolate all life services this includes but not limited to, drainage, lightening protection, power.  Authority permission shall be acquired prior to isolation of any services.

  - Demolition.  Demolish all parts of the cage and OWI.  Demolition shall be carried out carefully and systematically starting from above to bottom.  Measures to control noise and dust shall be in place as per Ref BB.

  - Backfill in open holes.  Exposed holes after demolition shall be back filled.  Backfilling shall be carried out with selected suitable materials and compacted to achieve the bearing strength enough to safely carry the imposed loads without settling.

  - Level affected areas and clean off.  All affected areas after completion of the work shall be made good.  This shall include and not limited to levelling the site, sweeping debris and disposal, reinstating any planted maintained vegetation, reinstating affected existing building.

General points for all tasks

Civil works

- Concrete materials and mix design.  The contractor shall submit to the Authority the proposed concrete mix designs for all concrete works.  The size of the aggregate used is not to exceed the nominal 20mm and will comply with BS EN 12670 at Reference HH.  The contractor is to notify the Authority 48 hours prior to pouring of concrete.  Cubes are to be taken from structural concrete with 7 and 28 day crushing results passed to the Authority by the contractor QC representative. PQC is to be used for all concrete works associated with the 2No surface drainage on the AOS.  Concrete works carried out in accordance with Reference AA and II.

- Formwork.  The formwork will be checked for rigidity and shape by the contractor prior to any concrete being placed.  Levels will be checked, and any adjustment made to ensure that the finished concrete is as per the design.

- Aggregate grading.  Crushed aggregate is to be used as Type 1 and is to conform to the grading requirement illustrated in Table 1.  The optimum Moisture content of the Type 1 aggregate is to be maintained within a range of 8 - 12%, to aid the compaction process:

| BS EN Sieve Size | Percentage by Mass Passing |  |
| --- | --- | --- |
|  | Minimum | Maximum |
| 63 mm | 100 | 100 |
| 31.5 mm | 75 | 100 |
| 16 mm | 43 | 81 |
| 8 mm | 23 | 66 |
| 4 mm | 12 | 53 |
| 2 mm | 6 | 42 |
| 1 mm | 3 | 32 |
| 63 micron | 0 | 9 |
| The particle size shall be determined by washing and sieving method as stated in BS 933. |  |  |

Table 1:  Type 1 Aggregate grading requirements.

- Concrete strength.  The minimum strength for all concrete shall be 25 N/mm2 after 28 days. The strength of the concrete shall be measured by crush testing 150 mm cubes.  A minimum of 2 concrete cubes shall be produced on-site for each batch of concrete.  Once produced on-site they are to remain in-situ for 24hrs before being removed from site and introduced into a water bath for curing.  Cubes are to be tested at 7 days to provide a projected 28-day strength.  Concrete work shall be in accordance with Ref. HH.  The site representation from the Garrison Engineer (GE) department is to be notified if the projected concrete strength at day testing for the 28-day strength is below if below 25 N/mm2.

- Water.   Water used in the mixing of the concrete shall be clean, potable and non-saline.  The contractor is required to check any water sources used for salinity.  The Authority reserves the right to check water salinity on site.  Concrete made using saline water will be rejected and replaced by the Contractor.

- Reinforcement.  Reinforcing steel are to be deformed steel bars, reinforcement must be free from oil, dirty, loose rust and scale when placed.  Reinforcement bars shall be placed and fixed on supports or preformed spacers at 500 mm centres but not exceeding 1000 mm and staggered for individual bars.  For welded fabric mesh, spacing shall not exceed 500 mm.  Cool water shall be sprinkled on steel and forms prior to placing concrete.  There must always be a minimum of 50 mm cover over steel reinforcement in all directions.  Concrete works in accordance with Reference JJ.

- Concrete workability.  Workability shall be constant and if necessary plasticizing or retarding admixtures may be used to suit local or weather conditions.  The slump of concrete will be tested prior to pouring in accordance with Reference KK to ensure that the mix is not too stiff.  Workability is not to be increased by adding water.

- Placing and compacting concrete.  At the time of placing concrete, the Contractor shall ensure that all surfaces on which concrete is to be placed are clean and free from debris, organic material and free water.  The concrete shall be placed in 150 mm layers; to avoid trapping air, their thickness should be regulated.  Do not add water or re-temper mixes.  Compact to full depth (and into previous layers if sufficiently plastic) for full compaction and into corners of formwork.  Vibration of the concrete shall be by means of mechanical vibration only, inserted vertically and shall be controlled to regulate the degree of compaction and compaction to prevent segregation.  A spare mechanical vibration unit shall be at hand in the event of break down during the concrete pour.

- Concrete finish.  The contractor is to carry out all finishing operations at optimum times in relation to the setting and hardening of the concrete.  Wetting of surfaces of concrete to assist surface working or sprinkling cement on to the surface is to be avoided.  The surface of the concrete shall receive no special treatment other than finishing operations required to produce the specified degree of accuracy of the surface level.  Any exposed concrete edges are to have a 25 x 25 mm chamfered finish applied to prevent damage when striking formwork.  The surface of the slab after final regulation shall be brush textured in a direction away from the tank sump.  The surface texture must be applied evenly across the slab with a stiff brush with the minimum texture depth of the less than 1mm.

- Concrete curing.  The ideal conditions for concrete curing are between 10 – 30ºC.  It is essential to provide adequate protection from evaporation and heat loss or gain by radiation to allow the concrete to attain its designed strength.  The Contractor shall prevent surface evaporation during the curing process.  It is the Contractors responsibility to ensure the concrete is cured correctly.  The fresh concrete shall not be subjected to the weight of any traffic or equipment for a period of 14 days after the pour.  Where further pours are required on to the concrete, a period of 2 days curing is to pass before further formwork and pouring is introduced.

- Joints.  Expansion joints allow expansion and contraction of a concrete slab without generating potentially damaging forces within the slab itself or the surrounding structures.  There shall be a definite break in the concrete and any reinforcing steel that may be present. Where adjacent bays are 'tied' together by means of dowel bars, these dowels shall be sleeved in one of the bays to allow expansion to take place without generating stresses within the slab.  Joints are to be constructed after every individual slab to allow for expansion and extraction.  The dowels shall be 600mm long and manufactured from mild steel (Grade 250). In expansion joints, the dowels are 25mm diameter at 300mm centres.  Expansion joints shall consist of a flexible piece of compressible board, topped with a waterproof sealant.  The sealant is to be petroleum resistant and sandwiched between adjacent bays or between the concrete slab and another fixed object.

Electrical works

- Conduit.  Conduit is to be surface mounted on to a suitable structure.  Conduits shall have screw threads for jointing length to length and for the attachment of accessories.  Conduits and fittings shall be fixed to structures and to other components with bolts or screws unless otherwise indicated or approved by the Authority.  High impact areas shall have hot dipped galvanised steel conduit and all other areas shall be uPVC that is highly resistant to UV light.  Adequate protection against corrosion shall be provided to steel conduit.

- Supports.  Junction boxes and back boxes installed in conduit runs need be separately fixed to the underlying supporting structure so as not to rely solely on the saddling of conduits for their support.  A spacer bar saddle shall be fixed 150mm adjacent to any junction or back box.  Fixing saddles shall be positioned at a maximum of 1200mm apart or 300mm from conduit outlet boxes or changes in direction.

- Bends.  Steel conduit shall be bent on site to the required shape to allow the conduit to run around obstacles and corners.  All conduit bends shall be achieved without distorting the diameter of the conduit.  Conduit bending shall be by means of good quality conduit bending machine in good condition and poor or damaged conduit bends shall be rejected.

- Couplers, bushes and glands.  Bushes and glands used in conjunction with conduit and conduit accessories shall be appropriate to the type used.  Conduit connected galvanized steel trunking, back boxes and fluorescent fittings shall utilise a coupler and male brass bush.  The male bush is to be fitted from within the fitting, securing the coupler outside the equipment.

- Saddles.  Spacer bar saddles shall be used for fixing conduits to surface walls, ceilings, and roof trusses.  In all cases the conduit is to run parallel to the building lines and shall be fixed in position at intervals of not more than 1200 mm by means of spacer bar saddles.

- Access and covers.  Covers for conduit boxes shall be appropriate to the type used.  Gaskets shall be used with conduit box covers within roof space to prevent insects, debris and moisture entering the conduit runs.

- Cable routes.  Cables are to be buried below ground where practical, and shall, as far as reasonably practicable, follow the features of the site such as roadways and building lines.  Ducts at roads shall normally be at right angles to the line of the road.  Cables that are directly fixed to surfaces shall be neatly run and securely fixed at suitable intervals, in accordance with the recommendations of the cable manufacturer.

- Inspection and test procedure.  The inspection and testing of the new installation shall include the following:

  - Prior to energising.  Before the supply is connected the following procedure is to take place:

    - Visual inspection as laid down within the current edition of Ref A.

    - Continuity of protective conductors, including main and supplementary bonding.

    - Continuity of ring final circuit conductors, including protective conductors.

    - Insulation resistance.

    - Polarity (by continuity method).

    - Earth electrode resistance measurement (clean earth).

  - During energising.  With the supply connected and energised the following procedure is to take place:

    - Check polarity of the supply, using an approved voltage indicator.

    - Earth electrode resistance, using a loop impedance tester.

    - Earth fault loop impedance.

    - Prospective fault current measurement.

- Trenching.  No work shall commence until the Authority has provided a Statement of Known Services (SoKS) and the Contractor has taken all reasonable steps to ensure that the area is free of all cables, drains and other services.  Cable Avoidance Tool (CAT) and Signal Generator (Genny) or any other equivalent cable detector tools shall be used to detect services.  Unless otherwise indicated the following is required.

  - Excavations within 600 mm of existing services shall be dug by hand.  Any damage to services shall be reported immediately to the Authority.  No repair or replacement shall be carried out unless the Authority gives approval.  All works will be at the Contractor’s expense.

  - Cables shall be buried at a sufficient depth to avoid being damaged by any disturbance of the ground reasonably likely to occur.  Trenches shall be excavated to a 600 mm depth.

  - All cable enclosed within trenches are to be installed in accordance with Ref A.  The Contractor shall ensure an accurate record of the location is made and passed to the Authority.

- Warning tapes and covers.  A traceable warning tape shall be placed above each cable that is laid direct in the ground and above each cable duct.  The following will be required:

  - The tape shall be laid at a depth of 300 mm below the finished surface level except where the depth of roadway or paved area base exceeds 300 mm in which case the tape shall be laid immediately below the base.

  - Warning tapes shall be traceable and be not less than 150 mm wide and 0.1 mm thick.  They shall be yellow in colour and bear the continuously repeated legend “CAUTION ELECTRIC CABLE BELOW”, or similar, in black letters not less than 30 mm high.

- Commissioning.  The Contractor shall be responsible for carrying out all inspection and testing of the electrical installation and equipment as prescribed at Ref A.  The Contractor is to complete the required sections of the commissioning form and present them to the Authority for verification.

- Regulatory compliance.  All work shall be carried-out whilst maintaining a Safe System of Work (SSoW) as per Ref B and all the electrical installation shall be in accordance with Ref A.

- Inspection chambers and termination.  All underground ductwork shall have a 400 x 
400 mm concrete Inspection Chamber (IC) at a maximum spacing of 30 metres plus; changes of direction, changes of height, junctions and maximum runs (in accordance with building regulations) along the ductwork.

- Existing services and facilities.  It is the Contractor’s responsibility to conform to the following:

  - The Contractor is responsible for ensuring all services or facilities on or adjacent to the site including public roads approaching the site, that may be affected by the works are identified and that appropriate action is taken to prevent damage occurring before work commences.  Liaison between adjacent areas of activity or other work sites is essential where any activities on the site or on an adjacent site are identified which may impact on the project.  The Authority is to be informed in writing at the earliest opportunity (e.g. services requiring redirection).  If damage is incurred, it will be the sole responsibility of the Contractor to rectify to the Authority’s given standard.

  - Any work that could possibly impact on existing services may only commence upon receipt of appropriate written documentation (e.g. Statement of known services), a copy of which must be provided to the Authority.  The Contractor must discuss in advance with the Authority which specific agencies it will need to obtain approvals and documentation from (e.g. Facilities Manager, Communications, etc.).  Obtaining any such approvals and documentation is the Contractor’s responsibility.

  - Upon request, and subject to security caveats, the Contractor may have access to all relevant existing Drawings relating to the contracted works on the site, held by the Authority.  During the tender stage, the Contractor shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

  - The Contractor shall conduct a detailed site investigation and ensure that any existing services, which are to be connected to, are of an acceptable standard to ensure the required performance over the life of the new facility.  Where it is found that an existing services (including, but not limited to water, sewerage, drainage and electrical power) are not adequate the Contractor shall inform the Authority and obtain written instruction prior to taking remedial action.

  - Where the proposed work interacts with any existing facilities where defects are found this shall be reported to the Authority without delay.  Instructions must be obtained from the Authority before proceeding with work, which may cover up, or otherwise hinder access to the defective construction, or be rendered abortive by the carrying out of subsequent remedial work.

- Setting out.  The Contractor is responsible for all setting out and for all ongoing monitoring of line, level and accuracy as works progress.

- Communication.  Communication will be key in planning and conducting concrete works, excavation works, design works, final connection, and new connections to the existing systems, electrical installation and during commissioning.  Therefore, the contractor must communicate with the Authority in a timely manner.

- Competence.  All personnel employed to work on the above tasks shall be suitably qualified and experienced, with their CV submitted to the Authority.  They may also be interviewed by the Authority to confirm their competence.

- Risk Assessment and Method Statement.  Before any work is performed, pertinent risk assessments and method statements shall be issued to the Authority.  The Authority will then issue the appropriate permits to work if required.  The contractor must have been issued a Statement of known hazards from the Authority prior to starting each task or part thereof and excavation on site.

- Design Data.  All detailed design Drawings, lighting designs and calculations, cable-sizing calculations, pipes sizing calculations, drainage sizing, concrete mixing ratios, materials data safety sheets and samples for materials are to be submitted to the Authority for approval before relevant work proceeds.

- Access.  The Authority will issue the necessary documentation for the transportation of goods to and from BATUK camps or barracks upon request e.g. gate passes.

- Equipment.  Any working at height equipment to be used in the task/s are to be serviceable and where required presented to the Authority for inspection and permission to use.

- Permit to Work.  Any electrical works (final connection of the cables to the existing system) work will be carried out as per Ref B (Permit to work).

- Statement of Known Services.  Under no circumstances are trench digging works are to be carried-out without gaining a Statement of Known Hazards (SoKH) from the Authority.

Restrictions and constraints

- Access to the site.  This is to be agreed and coordinated with the PM prior to start on site.  Passes may be required, and the contractor shall submit the details and Identification Document (ID) of any technicians that will be working on the contract within the tender return.

- Notice.  The contractor is to provide notice to the Authority in writing (or through email) of a minimum of 3 working days prior to work starting on site.  The notice must include the date and expected time of arrival, name and ID No of the workforce, and contact telephone number for both the contract manager and the workforce.

- Working hours.  The contractor may choose to work in his/her suitable hours; however, assistance from the Authority will only be available 0800-1600 hrs Mon – Fri.  For any assistance from the Authority, the contractor must submit request with a minimum of 24hrs notice.

- Welfare facilities.  The Contractor is to provide suitable welfare facilities for their workforce including washing and toilet facilities and for break and meal times.

- Emergency and first aid.  The Contractor is to request a site specific 4Cs brief prior to working at each facility.  The Contractor is to ensure that a medical plan is in place to deal with accidents.  A first aid kit is to be at each site with a nominated first aider located at all times at each site when work is ongoing.

- Permit to work.  Permit to work applicable for this task are as follows:

  - Statement of Known Services.

  - Electrical Works.

  - Working at Height.

  - Confined Spaces.

Annexes:

A.	Generic Points - Pre-contract

B.	Generic Points - Pre-construction.

C.	Generic Points - During construction.

D.	Generic Points - Post construction.

Annex A to

ITT/KEN/GE/1901/BK/3/Spec

Dated 12 November 2019

Generic Points - Pre-Contract

#### Designers

- General.  This project is a Design and Build contract, meaning the contractor must fulfil the role of both the designer, and the Principle contractor.  The design work must be carried out by a qualified and competent person.  The contractor shall ensure that all designs are in accordance with, and all applicable requirements contained within references and all other design documents specified within this Performance Specification.  If the contractor is not competent to carry out some aspects of the design work, a qualified person or consultancy firm shall be sub-contracted to carry out that portion of the work.  The Contractor is to inform the PM of all design consultants/sub-contractors who will be employed in this project and the areas of their responsibility.

- Competency.  Where design work is required to be carried out by a professionally qualified person, details of their qualifications and experience, registration with the Engineers Board of Kenya and copy of their professional liability insurance needs to be submitted to the Authority.

- Pre-Construction Information Pack (PCIP).  All pre-construction information is contained within this Booklet 3.  If any additional information is required, the contractor is to request a copy in sufficient time to allow any changes prior to tender submission.

Contractors design

- Design parameters.  The contractor is to ensure that their design meets the parameters outlined within this PS.

- Site visit.  The Contractor shall acquaint himself completely with the exact conditions relating to access and site environment, along with the layout, conditions and positions of the existing services, the full extent of the works required, and the supply and conditions affecting labour, carriage, carting, unloading, storage, tools, scaffolding etc. as well as any security and access constraints.

- Existing ground levels.  The Contractor shall confirm or identify all existing site levels required prior to any construction works.

- Ground water level.  The ground water level has not been established but it is not expected to impact on any of the works.  However, it remains the Contractor’s responsibility to consider the ground water levels when submitting technical and commercial proposals.

- Existing record Drawings.  The Contractor will upon request, be supplied with copies of all available and relevant as built Drawings.  The Contractor during tender stages shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

- Compliance.  The responsibility remains with the Contractor to ensure that all design and construction works comply with the latest methods, requirements and guides, and generally accepted practice as related to the works, geography, climate, and environment.  Where there are conflicts between the design Drawings and detailed specification the detailed specification will take precedence in all cases.  Any queries shall always be addressed to the Authority in the first instance.

#### Use of design codes and specifications

- Conformity.  All designs must conform to the most current editions of British Standards (BS) or Euro Norms (EN).  Other design codes may, on occasion, be used provided that they meet the minimum requirements and the Contractor shall submit proof of equivalency to the Authority for approval of use.  The Authority can be approached for clarification of the relevant BS if required.  On no account is the contractor to use any design information other than that stated or approved by the Authority.  All Contractors will be required to certify their designs for conformity to the specification and to the relevant BS/EN.  Only appropriately qualified and experienced engineers are to certify the designs.

  - Letter of conformation.  The design engineer is to produce a letter to state that the design conforms to all applicable legislation, most current editions of BS or EN, and best practices.  The letter is to have the company header (of the design agency if sub-contracted) and to be signed by the lead designer with his name, contact details and qualifications detailed in the signature block.

  - Construction Inspections.  Prior to the start of construction, the contractor, designer and Authority shall agree key stages at which the works are to be inspected by the designer for compliance with the design.

  - Build Conformity.  At the end of the project, the lead designer is to confirm in writing that the works have been built correctly, in accordance with his design.

- Design Life.  The design life of all new works and structural components and assemblies to first major overhaul, repair or replacement is to be the minimum stated on each section project task.  The Contractor shall supply and install all components, elements and systems/structures to satisfy this requirement and provide documentary evidence.

Annex B to

ITT/KEN/GE/1901/BK/3/Spec

Dated 12 November 2019

Generic Points - Pre Construction

Detailed design and planning

- Additional design information.  The Contractor is to submit any additional design information to the Authority prior to commencement of the construction phase.  The PM will examine design documentation and shall be entitled to reject a design as unsatisfactory where it is not in accordance with the specification, statutory regulations or if it would be unfit for purpose.

- A copy of all construction Drawings are to be provided by the Contractor to the PM prior to commencing Works.  Amended or updated Drawings are to be provided as necessary.  The minimum design information to be provided by the Contractor shall include the following:

  - Any additional design calculations for the works.

  - Any additional general layout plans for the site and the structures.

  - Any additional detailed structural design, calculations and Drawings.

  - Any additional foundation plans shall (as a minimum) indicate: all footing locations and dimensions, screeds and / or ground slabs or plinths, as applicable.

  - Any additional services layouts and calculations.

  - Any additional detailed Electrical, Mechanical Drawings and calculations.

  - Manufacturer’s product details including safety data sheets.

  - Designer’s risk register.

  - Project programme is to be regularly updated and, upon request by the Authority, provided electronically on Microsoft Project or equivalent.

#### Design Responsibilities under CDM 2015)

- The designer has the following responsibilities under Ref E.

  - Eliminate hazards and risks during design.  Designers are to analyse the risks posed during the construction, daily use, maintenance and ultimate demolition of the facility.  Once identified, these risks shall, where practicable, be designed out.

  - Provide information on remaining risks.  Remaining risks after the design process are to be compiled onto a designer’s risk register and submitted with the final design.

Provision of information

- Unless otherwise specified the following is to be provided:

  - Documentation.  Three copies of all information, including valid certification, in respect to work, goods and materials proposed by the Contractor, shall be supplied to the Authority.  Where the original document is written in a language other than English, it shall be accompanied by an English translation.

  - Time.  Information and certificates shall be provided at least 2 days prior to the work commencing or supply of goods or materials.

  - Drawing and Calculations.  Three copies of detailed working and fabrication Drawings and calculations shall be submitted to the Authority for reference purposes.  Such submittal shall in no way relieve the Contractor of his responsibilities for the work under the contract.

- The Authority reserves the right to request copies of all calculations and Drawings for analysis prior to the commencement of any construction on site.  The contractor will provide copies of all calculations and ‘As Built Drawings’ for the Health and Safety File.

- The signed and approved Drawings shall be used as the construction Drawings on site for all work purposes and to satisfy the requirements as specified by the Ref E and appropriate Approved Code of Practice (ACoP).

Construction phase plan

- Under the requirements of Ref E, the contractor is to prepare a construction phase plan detailing how they will safely conduct the works.  Risk assessments are to be included for all elements of work and method statements are required for any works that are out of the ordinary or high risk.  The Construction Phase Plan must cover the following area’s (where applicable):

  - Safety Risks

    - Protecting the public.  The public is any persons not involved in the works.  Particular attention shall be paid to areas where children are likely to have access to the site outside of working hours.

    - Traffic routes.  Traffic routes for delivery of stores and equipment shall be clearly highlighted and controlled.  Movement of plant and machinery on site shall be organised in a way that minimises risks to the workforce and any visitors to site.  Care must also be taken to minimise risk from existing traffic routes.

    - Existing buried and overhead services.  Some of these may be identified in the permit to dig process, however care must be taken to identify and avoid any damages on existing services.

    - Adjacent land use.  The use of adjacent land and properties will affect the level of protection for noise and dust suppression etc.

    - Stability of nearby structures.  Care must be taken that works do not affect the stability of nearby structures.

    - Demolition works.  Demolition work is a particularly dangerous task and careful planning must be conducted.  Method statements for all aspects of demolition will be required by the Authority.

    - Work equipment.  Work equipment must be inspected and in a suitable condition not to cause a hazard on site.

    - Electrical safety.  Electrical works will be conducted in accordance with the JSP and CDM recommendations.

    - Preventing falls.  Falling from height is one of the biggest causes of accidents in the construction industry.  Even when not working under a permit, it is expected that the correct equipment and management methods are utilised to prevent falls.

    - Working with or near fragile materials.  Fragile materials shall be identified prior to work commencing and appropriate action must be taken.

    - Control of lifting operations.  Lifting operations are to be carefully planned and controlled on site.

    - Excavations / confined spaces.  All excavations inside buildings where work is to be conducted are to have the appropriate level of shoring / protection.  Where an area is deemed a confined space, a permit may need to be issued to control the works.  If permit is not issued, the contractor is to have a suitable system in place with appropriate document i.e. risk assessment and method statements associated to the work being carried out.

    - Working on or near water.  If working on or near water the contractor is to plan the works to minimise the risk drowning.

  - Health risks

    - Temperature and weather.  Protection from the weather conditions for the workforce.

    - Substance misuse.  Assurance mechanism to prevent the workforce from working under influence of drugs or alcohol.

    - Manual handling.  Assurance mechanism for correct lifting techniques, lifting equipment etc.

    - Dust.  Provision of dust suppression and removal.

    - Noise.  Reduction and suppression of noise.  Management of timings for noisy activities etc.

    - Control of Substances Hazardous to Health (COSHH) Regulations 2002.  The correct storage and use of hazardous substances.  Appropriate protective equipment must be worn when handling COSHH materials.  Safety data sheets must be available on site at all time.

    - Asbestos.  Identification and appropriate management of Asbestos in accordance with Ref DD.

  - Provision of

    - Welfare facilities.  Water, food, shade, toilet facilities etc.

    - First aid.  There shall be at least one qualified first aider with appropriate medical equipment on site at all times.

    - Emergency procedures.  Procedures for response to incidents such as Fire, major and minor injuries, security incident etc.

    - Reporting of accidents, incidents or near misses.  Procedure for reporting and follow-on actions to prevent re-occurrence.

    - Waste management.  Management, storage and disposal of waste and arising from the site.

    - Fire prevention, detection and firefighting.  Methods to prevent the start and spread of fire, and to identify any fire that does start.  There must also be appropriate firefighting equipment available and access to the site for firefighting services.

Pre-start meeting

- Prior to the commencement of any works, a Pre-Start meeting is to be held with the contractor, lead designer and chaired by a representative from the Authority.  The following topics are to be discussed as a minimum:

  - Mobilisation plan.

  - Site setup.

  - Health and safety.

  - Required permits.

  - Access and security.

  - Programme.

Annex C to

ITT/KEN/GE/1901/BK/3/Spec

Dated 12 November 2019

Generic Points - During Construction

#### Facilities and temporary works and services

- Locations.  The Contractor is to agree with the PM of the intended siting of all spoil heaps, temporary works and services in advance.  The Authority shall verify with the Contractor which site features are to be removed and protected during construction works.

- Survey and setting out.  The Contractor will be responsible for all setting out and levelling during construction.  The Contractor shall keep updated schedules and Drawings of all bench marks used in setting out of the site; these must be made available to the Authority when required.  A minimum of 2 survey control stations are to be constructed, one visible from the site at a distance of 50 m and the other 200 m away from the first but in line of site.

- Record Drawings.  The Contractor shall record details of all grid lines, setting out stations, bench-marks and profiles on the site setting out Drawing.  Retain on site throughout the contract and hand to PM on Completion.

- Signage.  The Contractor shall supply and erect all applicable and appropriate signage to the site.  This shall include as a minimum all H&S signage, directions and location of site office and emergency contact details of the Contractor’s representative on site.  Temporary warning signs and careful demarcation of works areas must be undertaken with care to ensure compliance with any and all requirements.

- Lighting and power.  The Contractor shall provide all lighting and power for this work.  No facility will exist on site from the general base infrastructure.

- Communications.  The Contractor shall provide his workforce with adequate means of communications throughout the duration of the Contract period in order to carry out the work specified.

- Temporary services.  The Contractor shall provide temporary service connections to both mechanical and electrical systems.  All temporary service connections are to be in accordance with current UK regulations.

- Use of the site.  The Site shall not be used for any purpose other than undertaking the specified works.  The Contractor may erect the site office and storage compound in a location agreed with the Authority.  No storage of materials, parking of vehicles, temporary accommodation or any other use of areas beyond the boundaries shall be permitted.  Under no circumstances shall it be permissible for the Contractor to cause an obstruction to normal pedestrian or vehicular movements within the vicinity of the site.

- Restrictions to the works.  The Works are to be undertaken without interfering with every day running of the Authority’s operations within the area.  The demarcation of the Site boundary is to be obvious and clearly marked to restrict access to the Site whilst the Works are being undertaken.

Project management

- The Authority.  The Project Support Officer (PSO) has overall Authority on this project.  For the purpose of this specification, the PM is the only person from within the Authority acting on behalf of the PSO, or Superintending Officer (SO) in most cases.  The Contractor shall not commence any work in accordance with any Design Document until the PM has agreed the relevant Design Document.

- Buried Services.  Prior to carrying out any excavation work, the Contractor must:

  - Obtain a Permit to Dig (Statement of Known Services) and all Drawings relating to existing services that may interfere with the proposed works.  A copy of the Permit to Dig must be given to the Authority prior to any works commencing.

  - Identify all local services and take adequate precautions to protect such services from damage for the duration of the works.

  - Inform the Authority immediately if any unknown services are discovered that will impact on the works.

- Supervision.  The Contractor shall accept responsibility for delivery, co-ordination, supervision and administration of the Works, including all subcontracts.  They shall arrange and monitor a programme with each subcontractor, supplier, local Employer and any statutory undertaker, and obtain and supply information as necessary for co-ordination of the work.

- Site diary.  The Contractor shall keep an up to date daily site diary.  This document is to be used to record all decisions made on site both verbally and written.  The document is also to be used to record visits to site and note anything, which has a direct effect on the project in terms of cost and extensions to time, or any other occurrence that affects the project programme.  This document will be used as the audit trail in light of any disputes, concerning the project.

- Contractor’s site meetings.  The Contractor is to hold meetings with appropriate subcontractors and suppliers shortly before site meetings with the Authority to facilitate accurate reporting of progress.

- Site meetings.  The PM, or his representative will hold regular site meetings to review progress and other matters arising from the administration of the Contract.  It will be the Contractors responsibility to ensure the availability of accommodation and attend all such meetings.

- Liaison with the Authority.  The Contractor shall designate a site manager from within his organisation who will be responsible for liaising with the PM, PSO or his representative (SO) on a day to day basis and as the need arises.  At all times the Contractor shall ensure that the Site Manager presents on site that has the capability of reading, writing, speaking and receiving instructions in the English Language, including being able to understand and interpret technical Drawings and specifications.  The Site Manager must be able to explain the work operations to person performing the work in a language that those performing the work are capable of understanding.  The PM shall have the right to determine, whether the proposed representative has sufficient technical and linguistic capabilities.

- Approvals.  Where products or works are specified to be approved or the PM instructs or requires that they are to be approved, the same must be supplied and executed to comply with all requirements.

- Access.  The Contractor shall provide at all reasonable times, access to the Works.  The Contractor shall supply the PM or his representative with copies of any documentation and drawings, which may reasonably be required for the purposes of monitoring the work performed under this or any sub-contract.

- Regulations.  It is the Contractor’s responsibility to be fully conversant with all local/MOD regulations and requirements in respect of fire, safety, security and occupational health, etc.  These are to be fully complied with throughout the contract period.

Health and Safety

- Health and Safety (H&S).  All works shall be carried out in accordance with Ref C.

- JSP 375.  The contractor shall comply with the Client’s permit to work system and the JSP 375, Volume 3, (details of which are obtainable from the Authority SO), including the provision of method statements, risk assessments, switching/isolating safety programmes, permit to dig, etc.

Permit to work

- Permit to dig.  If any excavation or breaking of ground is to be carried out, the contractor must request a permit to dig at the Pre-Start meeting.  Shall any excavation be conducted without a permit, the contractor may be removed from site.

- Hot works permit.  The contractor is to establish at the Pre-Start meeting if hot work permits will be required for his location of work.

- Authorised Persons (AP).  The following table shows details of APs in their respective discipline.

| Discipline | CAP | Contact No |
| --- | --- | --- |
| Electrical | Mr Ezekiel / SSgt Ringjali | 0719197643/0704405046 |
| Mechanical | WO2 Hattingh | 0702659971 |
| Petroleum | Mr Ezekiel | 0719197643 |
| Confined Spaces | Mr Mbilo/Mr Julius | 0720015852/0719197599 |
| Working at Height | Mr Mbilo | 0720015852 |

- Skilled persons & Persons in Charge (PIC).  Any works required to be completed under a JSP 375 permit must have a dedicated PIC and the work carried out by registered skilled persons.  At the Pre-Start meeting the contractor must establish if any of his works require a permit, and if so arrange for currently registered personnel to conduct the works, or registration of the contractor’s personnel.

- CDM 2015.  The Contractor shall submit a pre-construction H&S file to the Authority for approval, including all risk assessments, method statements, hazardous material procedures etc to comply fully with Construction, Ref E & appropriate ACOP.

Quality of work

- Quality standards and control.  The contractor will provide evidence to the PM of his quality standards and controls and will produce a plan detailing Quality Control (QC) activities in order for the PM to plan for witnessing of critical activities.

  - General quality of products.  All products shall conform to the following subparagraphs:

    - Products to be new unless otherwise specified by the Authority.

    - For products specified to a BS or EN obtain certificates of compliance from manufacturers when requested.

    - Where a choice of manufacturer or source is allowed for any particular product, the whole quantity required must be of the same type, manufacture and/or source unless otherwise approved.  Produce written evidence of sources of supply when requested by PM.

    - Ensure that the whole quantity of each product required to complete the work is of consistent kind, size, quality and overall appearance.

    - Where consistency of appearance is desirable ensure consistency of supply from the same source.  Do not use different colour batches where they can be seen together.

    - If products are prone to deterioration or have a limited shelf life, order in suitable quantities to a programme and use in appropriate sequence.  Do not use if there are any signs of deterioration, setting or other unsatisfactory condition.

  - Proprietary products.  All products shall conform to the followings:

    - Handle, store, prepare and use or fix each product in accordance with its manufacturer’s current printed or written recommendations/instructions.  Inform PM if these recommendations/instructions conflict with any other specified requirement.  Submit copies to PM when requested.

    - The tender will be deemed to be based on the products specified and recommendations on their use given in the manufacturer’s literature current at the date of tender.

  - Product Quality.  Obtain confirmation from manufacturers that the products specified and recommendations on their use have not been changed since that time.  Where such change has occurred inform PM and do not place orders for or use the affected products without further instructions.

  - Checking compliance of products.  The Contractor shall check all delivery tickets, labels, identification marks and where appropriate the products themselves to ensure that all products comply with the project documents.  In particular, check that the products comply with the following sub-paragraphs.

    - The sources, types, qualities, finishes and colours are correct, and match any approved samples.

    - All accessories and fixings that shall be supplied with the products have been supplied.

    - Sizes are correct.  Where tolerances are critical, measure a sufficient quantity to ensure compliance.

    - The delivered quantities are correct, to ensure that shortages do not cause delays in the work.

    - The products are clean, undamaged and otherwise in good condition.

    - Any products with a limited shelf life are not out of date.

  - Protection of products.  All products shall be protected to ensure that they remain in the condition they are required.  In particular the contractor is to ensure that products are to be prevented from overstressing, kept clean, protected from the elements and kept in original wrappings until required for the project.

- Prohibited products.  The Contractor shall not employ on or incorporate in the Works any of the following products and shall impose a like obligation upon all Sub-Contractors.

  - Asbestos materials as described in the Asbestos Prohibitions Regulations 1985 and the Asbestos Products (Safety) Regulations 1985.

  - Lead or any products containing lead for use in connection with drinking water.

  - Materials that are generally composed of mineral fibres either manmade or naturally occurring which have a diameter of 3 microns or less and a length of 200 microns or less or which contain any fibres not scaled or otherwise stabilised to ensure that fibre migration is prevented.

  - Other products or substances generally known to be deleterious to health and safety at the time of use or to the durability of the property in the particular circumstances in which they are being used.

- Hazardous, aggressive or unstable materials.  The Contractor is not to import or use fill materials that either would in themselves or in combination with other material or ground water, give rise to health hazards, damage buildings or structures.  The construction materials shall not include any finishes that may lead to shedding of particles.

- Defects in existing construction/services.  This shall be reported to the PM without delay.  Obtain instructions before proceeding with work which may be covered up or otherwise hinder access to the defective construction or be rendered abortive by the carrying out of remedial work.  This is particularly relevant in relation to the expansion of the existing service runs.

- Proposals for rectification of defective work/products.  As soon as possible after any part(s) of the work or any products are known to be not in accordance with the Contract, or appear that they may not be in accordance, the Contractor is to submit proposals to the PM for opening up, inspection, testing, making good, or removal and re-execution.  Such proposals may be unacceptable to the PM and he may issue contrary instructions.

- Quality control.  The Contractor is to establish and maintain procedures to ensure that the works, including the work of all Subcontractors, comply with specified requirements.  This is to include all testing of materials that are to be incorporated into the project (e.g. concrete).  The Contractor is to maintain full records, keep copies on site for inspection by the PM, and submit copies of particular parts of the records on request.  The records must include the following:

  - Identification of the element, item, batch or lot including location in the works.

  - The nature and dates of inspections by the Contractor or PM, tests and approvals.

  - The nature and extent of any non-conforming work found.

  - Details of any corrective action.

- Materials testing.  It is the Contractor’s responsibility to carry out all materials testing and present all test results to the Authority on request and within the H&S file.  The Authority will carry out concurrence quality control material tests at regular intervals.

- Notification.  The Authority requires to be informed in writing at least 10 days in advance of any tests and commissioning being carried out.  Access must be available to the Authority to carry out testing as deemed necessary by the Authority.

Annex D to

ITT/KEN/GE/1901/BK/3/Spec

Dated 12 November 2019

Generic Points - Post Construction

Completion / Handover

- Commissioning period.  Within the tender submission the Contractor shall submit a Works Commissioning Plan, setting out his commissioning proposals including the preparation of handover documentation.

- Notice of completion.  The Contractor is to provide the PM at least five days’ notice of the anticipated date of Practical Completion of the whole or parts of the works.

- Mechanical and electrical services.  Mechanical and Electrical Services must have final tests and commissioning carried out by the Contractor so that they are in full working order at Practical Completion.  This includes buried but not connected cables and pipelines.

- Timing of tests and inspections.  The Contractor is to agree dates and times of tests and inspections with PM 10 days in advance, to enable the PM and other affected parties to be present.  On the previous working day to each such test or inspection the Contractor is to confirm to the PM that the work or sample in question will be ready or, if not ready, agree a new date and time.

- Test certificates.  The Contractor is to submit a copy of each certificate to PM as soon as practicable and keep copies of all certificates on site.  Copies shall be included in the Health and Safety File on handover of the works.

- Work at or after completion.  The Contractor is required to undertake the following works prior to handover.

  - Make good all damage consequent upon the work.

  - Remove all temporary markings, coverings and protective wrappings unless otherwise instructed.

  - Clean the works thoroughly inside and out including all accessible ducts and voids; remove all splashes, deposits, efflorescence, rubbish and surplus materials consequent upon the execution of the work.

  - Cleaning materials and methods to be as recommended by manufacturers of products being cleaned, and to be such that there is no damage or disfigurement to other materials.

- Security at completion.  The Contractor is to leave the Works secure with all accesses locked.  Account for and adequately label all keys and hand over to PM with itemised schedule, retaining duplicate schedule signed by PM as a receipt.

- Making good defects.  The Contractor is to make arrangements with the PM and give reasonable notice of the precise dates for access to the various parts of the Works for purposes of making good defects.  The PM is to be informed by the Contractor when remedial works to the various parts of the Works are completed and ready for approval.

- Inspection, testing and commissioning.  The installations shall be tested and inspected in accordance with but not limited to the current CIBSE Codes, Ref A, amendment where appropriate, etc.  Advance notice of tests shall be given (minimum of 10 days prior to notification).

- Test and inspection certificates.  Test and inspection certificates are to be approved by the Authority, preferred document templates will be provided by the Authority on request.  Test certificates shall serve as a record that the item referred to has been shown under test to meet the requirements of the specifications and of British Standards as applicable and shall be dated, numbered and clearly referenced to the item tested by means of serial, chassis or other manufactures reference number permanently marked in a conspicuous position.

- Equipment calibration.  The calibration certificates for the testing of the equipment are to be available on request to be shown to the Authority for scrutiny.  The Contractor shall ensure all calibrations are in date.  The Authority reserves the right to have an independent electrician available during the test and inspection phase.

- Defects.  Any defects of workmanship, materials or non-compliance with the specifications or other irregularities that become apparent during the tests shall be rectified by the Contractor, at his own expense, until the whole work is free from defects and in full working order to the complete satisfaction of the Supervising Officer.

- Material data sheets.  All materials used for construction of permanent works shall have suppliers’ specifications and/or testing certificates available.  Where materials are used as part of a whole or in conjunction with other materials, and in any case where site testing is required by best practice, verification of quality and specifications shall be allowed for the parts / items / products (suppliers’ specification) as well as the whole (site testing).

- Defects Liability Period (DLP).  A defects liability period shall apply for the works as detailed above.  The Contractor will be responsible for making good at his own expense any defects in the works arising within that period.  The contractor is to ensure that a defects inspection is conducted 2-4 weeks prior to the end of the liability period in order to release the contract retention.

- Operations and maintenance documentation.  Upon completion of the works the Contractor shall forward all manufacturers’ details relating to equipment/materials used to the Authority for inclusion into the O&M Manual/H&S File.  Refer also to Construction, (Design and Management) Regulations 2015 (CDM 2015) & appropriate ACOP, this documentation less ‘As Built Drawings’ is to be made available at the Pre-Board of Officers not less than 10 days before the due project handover date.  A full list of snagging items shall be produced and presented to the Authority with a rectification programme at this very same board.

#### Health and Safety File

- Presentation of health and safety file.  Upon project completion the H&S file shall be presented to the Authority before the Board of Officers is convened and in compliance with Ref E & appropriate ACOP.  The Contractor is to provide the PM with an electronic and hard copy of the H&S File.  The Manual is to be contained in a series of A4 size, plastic covered, loose leaf, four ring binders with hard covers, each indexed, divided and appropriately cover titled.  Selected Drawings needed to illustrate or locate items mentioned in the Manual, where larger than A4, are to be folded and accommodated in the binders so that they may be unfolded without being detached from the rings.  The main set(s) of as-built Drawings will form Annex (es) to the Manual.

- Health and safety file.  The Contractor is required to complete the Project Health and Safety File on completion of the works, three copies of which will be provided to the Authority at handover.  Advice can be sought from the Authority if required.  The H&S File provides information required for future construction work, which includes cleaning, maintenance, alterations, refurbishment and demolition.  The Manual is to consist of the following parts, sub-sectioned as appropriate.

  - Section 1: H&S.  The Contractor is to provide a description of the site and the buildings thereon.  This is to include details of construction methods and materials, which may present significant residual hazards in the future.

  - Section 2: Certificates.  The Contractor is to provide a copy of all Test Certificates (including but not limited to electrical circuit tests, start and commissioning tests) for the installations and plant, equipment, valves, etc, used in the installations.  Warranty Certificates and guarantees are also to be included in this section.

  - Section 3: As-built Drawings.  The Contractor is to provide as-built Drawings recording details of all construction, electrical and mechanical work.  A fire strategy for the site shall also be included with Drawings showing emergency escape routes, location of emergency and firefighting systems, services shut-off valves, switches, etc.

  - Section 4: Operation & Maintenance (O&M) schedules.  The Contractor is to provide recommendations as to the preventative maintenance, frequency and procedures to be adopted to ensure the most efficient operation of the systems.  Manufacturer’s O&M schedules are to be included.  Diagrammatic Drawings of each system indicating principal items of plant, equipment, and valves are also to be included.

  - Section 5: O&M manuals.  The Contractor is to provide copies of manufacturers’ current literature for all products for which the particular proprietary brand has been chosen by the Contractor, including COSHH data sheets, catalogue list numbers and manufacturers recommendations for cleaning and maintenance.  The mechanical and electrical systems section shall contain a full description of each of the systems installed, written to ensure that the client fully understands the scope and facilities provided.  All manufacturers technical literature for items of plant and equipment, assembled specifically for the project, including detailed Drawings, electrical circuit details and operating and maintenance instructions are to be included.

- Draft health and safety file.  A complete draft of the Manual must be submitted by the Contractor, not less than 2 weeks before the date for submission of the final copy of the Manual.  This is to be amended in the light of any comments and resubmitted to the PM.  Do not proceed with production of the final copy of the Manual until authorised to do so by the PM.

DIO RD OS Trg (K) is the Authority for this Contract.

Contractor to provide NEMA certificate to the Authority.