## Sheet1
Caledonian |  |  | Buckton Fields | [5 empty] | Opening Up Investigations & Assessment
Revision | 01
Item | Element / Aspect | Purpose | Concern / Focus | Haygrove | Buckton | SFG | Priority | No. / Frequency | Comments | Opening up Scope | £
1 | External wall - Rainscreen | H+S | Panel/rail fixings | n/a | Y | n/a | Aecom | n/a
2 | External wall - Rainscreen | Quality | Panel/rail fixings | n/a | Y | Y | P2 | 2-4No |  | 1) Photograph and/or mark up existing locations of cladding panels prior to removal 2) Remove cladding from within the identified panel up to a natural break without the need for any cutting. Initially full horizontal panel at ground to first floor junction and first to second floor junction. 3) Locate joint in VCL and fold back VCL and temporarily secure in place. Where natural joint cannot be located ensure suitable taping material is available for reinstatement 4) Set aside removed sections of timber cladding with fixings retained for inspection/reuse 5) Remove and Set aside for inspection timber battens and counter battens inclusive of fixings 6) Remove any drip details to head of masonry panel where masonry panels are located below 7) Upon completion, allow to reinstate as existing Note: Please refer to dwg FS0620-HLM-MB-SE-DR-A-25-2501 External detail wall sections Sheet 1 for details (please note this is a contractor proposal drawing and not an as-built drawing so actual constructional build up may vary)
3 | External wall - Rainscreen | Fire | Cavity fire barriers | Y | Y | Y | P1 | 2-4No |  | 1) During the removal of item 02 (above) locate position of vertical and horizontal cavity barriers. 2) Cavity barriers to remain insitu unless required to removed under instruction of engineer. should not be cut for removal unless manufacturers literature can be identified to confirm acceptance. Existing fixing arrangements to be determined prior to any removal 3) Upon completion, allow to reinstate as existing
4 | External wall - Rainscreen | Quality | Drainage/air voids | n/a | Y | Y | P1 | as item 1 | Clearance / airflow. | As per item 02
5 | External wall - Rainscreen | Quality | Buildup of barriers/linings | n/a | Y | Y | P1 | as item 1 | Placement of vapour barrier, etc inc. insect mesh. | As per item 02
6 | External wall | Quality | DPC placement | Y | Y | Y | P1 | as item 1 |  | 1) Locate assumed position of DPC and drill/chisel/cut out mortar bed to full depth of brick to confirm Prescence of DPC 2) Repoint full depth of brick with mortar to closely match the colour of the existing
7 | External wall | Quality | Cavity - debris | Y | Y | Y | P1 | 2-4No | Borescope prefered | 1) Cavity behind masonry panels to be viewed from above following removal of cladding panels and drip detail
8 | External wall | H+S | Wall ties - Density / Frequency | Y | Y | Y | P1 | 2-4No | Borescope prefered | 1) Cavity & wall ties behind masonry panels to be viewed from above following removal of cladding panels and drip detail. 2) 10mm inspection hole to be drilled through mortar bed at lower levels of masonry panels adjacent window / door opening to allow borescope inspection 3) Repoint inspection holes upon completion
9 | External wall | H+S | Wall ties - Restraint to SFS | Y | Y | Y | P1 | as item 7 +1 | Borescope prefered | 1) Where cladding removed above brick panel as per item 02 above check fixing length of wall tie by removing top most fixing at the head of the wall. 2) Should insufient space be available follow removal of cladding, remove bricks from top course down of masonry panel to allow enough room to remove and check fixing length of wall tie fixing. 3) Allow to reinstate as existing upon completion
10 | External wall | Quality | Window frame cavity cover | Y | Y | Y | P1 | 2-4No |  | 1) Cavity closer should be visible following removal of timber cladding and limited areas of brickwork as per the above. Where additional inspection locations require, use borescope via 10mm inspection hole drilled within mortar bed. 2) Allow to reinstate to match as existing upon completion
11 | External wall | H+S | Window operator restraint | - | - | Y | Aecom | n/a | AECOM PROGRESSING.
12 | External wall | Quality | Cavity tray/weephole | Y | Y | Y | P1 | as item 7 + 1 |  | 1) Cavity tray should be visible following removal of cladding and limited areas of brickwork as per the above. Where additional inspection locations require, use borescope via 10mm inspection hole drilled within mortar bed. 2) Allow to reinstate to match as existing upon completion
13 | External wall | Fire | External columns (mid room) | Y | Y | Y | P1 | 2-3No |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
14 | External wall | Fire | External columns (corner) | Y | Y | Y | P1 | 2-3No |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
15 | External wall | Fire | Suspended floor lab level GF to F1 | Y | Y | Y | P1 | 2-3No |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
16 | External wall | Fire | Suspended floor lab level F1 to F2 | Y | n/a | Y | P1 | 2-3No |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
17 | Structural | Quality | Foundation / GF Slab | Y | Y | Y | P1 | 1No | SE review re: scope required as to foundation type. | 1) Locate pad foundation grid line within area of soft landscaping (where possible) 2) Complete all necessary pre excavation checks for services etc 3) Remove and set aside for re-use any turf, planting, mulch and top soil 4) Excavate trial pit to top of foundation and bottom of foundation. Expose pad to frame connection and also perimeter strip foundation either side of pad to limited width 5) Allow to back fill and reinstate as existing A) Where exposing GF slab internally, locate module to module bay joint and locally remove floor finish and set aside for reuse B) Breakout and remove 3mm C20/25 concrete infill, 12mm CP board infill & 2 No. 18mm OSB3 board infill to expose floor construction. C) Alternatively allow for 100mm core hole sample. D) Reinstate to match existing
18 | Structural | H+S | Steel connections - floor beam to floor beam | Y | Y | Y | P1 | 4-6No |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: For internal inspection of same refer to items 36 & 38
19 | Structural | H+S | Steel connections - soffit beams | Y | Y | Y | P1 | as item 17
20 | Structural | H+S | Steel connections - columns | Y | Y | Y | P1 | as item 17 |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: For internal inspection of same refer to items 36 & 38
21 | Structural | H+S | Steel - diagonal bracing | Y | Y | Y | P1 | 1-2No |  | 1) Complete removal of cladding as per item 2. 2) Cut out section of insulation and set aside for re-use 3) Cut out section of Sinat Weather Defence board and/or Cement Particle board to expose structure below. Set aside for reuse 4) Allow to reinstate to match as existing upon completion Note: For internal inspection of same refer to items 36 & 38
22 | Roof | Quality | Parapet / fascia - fixings | Y | Y | Y | P1 | 1No
23 | Roof | Quality | Single ply - instalation | Y | Y | Y | Aecom |  | Hasan action.
24 | Roof | Quality | Single ply - integrity (electronic) | Y | Y | Y | Aecom | as item 23 | as 23
25 | Roof | Quality | Standing seam - integrity/weatherporofing | n/a | n/a | Y | Aecom |  | Dan action with Vertec.
26 | Roof - RW | Quality | RW outlet - Fall | Y | Y | Y | Aecom | as item 23 | as 23
27 | Roof - RW | Quality | RW oultet - Leaf guard | Y | Y | Y | Aecom | as item 23 | as 23
28 | Roof - RW | Quality | RWP system - Debris | Y | Y | Y | P1 | 2-4No
29 | Floor | Quality | DPM placement | Y | Y | Y | P1 | as item 16 |  | As per item 17
30 | Floor | Quality | GF below floor ventilation (air bricks, internal walls, void depth) | Y | Y | Y | P1 | 1No |  | 1) complete exposure of foundation as per item 17 2) Directly below position of above ground air brick, breakout and set aside brickwork from top of foundation to expose periscopic air vent penetration through to sub-floor void. 3) Where possible dislocate periscopic air vent to allow visibility through to subfloor void. 4) Where not possible to dislocate air vent, cut out section of sheathing board to allow visibility into sub floor void. 5)Allow to reinstate to match existing upon completion
31 | Floor | Fire | Fire stopping - unit junctions | Y | Y | Y | P1 | 2-4No | Ceiling through to FFL. | 1) Refer to drawing FS0620-CAL-MB-01-DR-W-00-0801 Internal Cavity Barrier Setting Out. 2) Within specified location locally remove floor finish to expose module unit junction 3 )Breakout and remove 3mm C20/25 concrete infill, 12mm CP board infill & 2 No. 18mm OSB3 board infill to expose floor construction. 4) Use borescope to check for linear ventilated cavity barrier 5) Allow to reinstate to match existing upon completion
32 | Floor | Fire | Fire stopping - shafts/risers | Y | Y | Y | P1 | 2-4No |  | 1) Within located risers cut out and remove existing fire stopping to confirm build-up. Existing firestopping generally consisting of ablative coated batt and intumescent mastic or cured fire rated compound 2) Allow to reinstate to match existing upon completion
33 | Floor | Fire | Fire stopping - shafts/risers | Y | Y | Y | P1 | 2-4No
34 | Wall internal (etc) | Fire | Buildup determination | Y | Y | Y | P1 | 1No | Each FR wall type. | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Section of wall element to be removed to be cut at natural joints or stud centres. I.e. 600mmc/c wide to allow for easier reinstatement. 4) Allow to reinstate to match existing upon completion
35 | Wall internal (etc) | Fire | Buildup determination Staircase | Y | Y | Y | P1 | 2-4No |  | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Section of wall element to be removed to be cut at natural joints or stud centres. I.e. 600mmc/c wide to allow for easier reinstatement. 4) Allow to reinstate to match existing upon completion
36 | Wall internal (etc) | Fire | External columns (mid room) | Y | Y | Y | P1 | 2-4No |  | 1) Within specified location, cut out and remove 9mm MR MDF board cover strip to full height 2) Remove 15mm GTEC Megadeco board fixed with Tremco SP525 adhesive and 32mm SDS screws 3) Neatly cut back section of VCL membrane to expose module columns. 4) Allow to reinstate to match existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
37 | Wall internal (etc) | Fire | External columns (corner) | Y | Y | Y | P1 | 2-4No |  | 1) Within specified location, cut out and remove 9mm MR MDF board cover strip to full height 2) Remove 15mm GTEC Megadeco board fixed with Tremco SP525 adhesive and 32mm SDS screws 3) Neatly cut back section of VCL membrane to expose module columns. 4) Allow to reinstate to match existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
38 | Wall internal (etc) | Fire | External columns (internal columns) | Y | Y | Y | P1 | 2-4No |  | 1) Within specified location, cut out and remove 9mm MR MDF board cover strip to feull height 2) Remove 15mm GTEC Megadeco board fixed with Tremco SP525 adhesive and 32mm SDS screws to expose internal module columns 4) Allow to reinstate to match existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
39 | Wall internal (etc) | Fire | External columns (diagonal bracing) | Y | Y | Y | P1 | 1-2No |  | 1) Within specified location, cut out and remove 9mm MR MDF board cover strip 2) Remove 15mm GTEC Megadeco board fixed with Tremco SP525 adhesive and 32mm SDS screws 3) Neatly cut back section of VCL membrane to expose module columns. 4) Allow to reinstate to match existing upon completion Note: Please refer to dwg FS0620-CAL-MB-ZZ-DR-W-00-2100 Typical module details for designed build up.
40 | Wall internal (etc) | Quality | Damp - Areas of occurance | Y | Y | Y | P2 | all instances |  | Location specific
41 | Wall internal (etc) | Fire | Electrical outlets | Y | Y | Y | P1 | 6-10No |  | 1) Identify and isolate electrical circuit prior to removing electrical face plates 2) Unscrew and pull forward electrical accessory faceplate to expose backbox and Prescence of putty pad without disconnecting electrical connections. 3) Where presence or absence of putty pad is not obvious, full disconnection of electrical accessory may be required. 4) Allow to reinstate to match existing upon completion
42 | Wall internal (etc) | Fire | Plant room | Y | Y | Y | P1 | 1-2No |  | 1) Within specified location, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
43 | Wall internal (etc) | Fire | PE Store / Caretakers Store | Y | Y | Y | P1 | 1-2No |  | 1) Within specified location, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
44 | Wall internal (etc) | Fire | FD frame to partition abutment | Y | Y | Y | P1 | 4-6No |  | 1) Within specified location gently pry off architrave from full perimeter of door to both faces 2) Allow to reinstate to match existing upon completion including decorations and mastic.
45 | Wall internal (etc) | Fire | FD Ironmongery bedding / intumescent / seals | Y | Y | Y | P1 | 4-6No |  | 1) Within specific location remove hinge one at a time to check for interdens behind hinge. 2) Remove and replace hinges one at a time to prevent need for full removal and re-hanging of door 3) Remove all other ironmongery from door including, handles, locks and latches from frame to check for specification and installation of interdens
46 | Ceilings (inc. H/L) | Quality | Damp - Areas of occurance | Y | Y | Y | P2 | all instances |  | Location specific
47 | Ceilings (inc. H/L) | Fire | Corridor cross doors (both sides) | Y | Y | Y | P1 | 4-6No |  | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
48 | Ceilings (inc. H/L) | Fire | Corridor dead end | Y | Y | Y | P1 | 4-6No | Widespread tile removal. | 1) Within specified location widespread removal of ceiling tiles to enable check of compartmentation. 2) Above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
49 | Ceilings (inc. H/L) | Fire | Kitchen | Y | Y | Y | P1 | 1-2No | Enclosure, both sides. | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
50 | Ceilings (inc. H/L) | Fire | Plant room | Y | Y | Y | P1 | 1-2No |  | Cut out of ceiling?
51 | Ceilings (inc. H/L) | Fire | PE Store / Caretakers Store | Y | Y | Y | P1 | 1-2No |  | Cut out of ceiling?
52 | Ceilings (inc. H/L) | Fire | Damper framing deconstruction | Y | Y | Y | P1 | 1-2No | Through framing of opening. | 1) Within specified location, remove and set aside ceiling tiles 2) Depending on installation detail cut out fire stopping around penetration to confirm build up of damper framing. 3) Allow to reinstate to match existing upon completion
53 | Ceilings (inc. H/L) | Fire | Compartment lines (ad hoc) | Y | Y | Y | P1 | 4-6No |  | 1) Within specified location above ceiling void, cut out and set aside each element of wall build up as noted on the Internal Wall Compartmentation GA's 2) To be complete on both sides of wall to ascertain full section build up. 3) Allow to reinstate to match existing upon completion
54 | External | Quality | Below Gnd drainage - CCTV and Report (dia, fall, connection, etc) | Y | Y | Y | Aecom |  | Dan action.
55 | External | H+S | Soil / GI - Playing Fields | Y | Y | Y | Aecom |  | Hasan action.
56 | External | H+S | Tarmac - Access zones | Y | Y | Y | P1 + Aecom | as item 16 | DR/CB/HS Aecom access strategy review.
57 | Wall internal (etc) | Quality | MDF joint panel cover strips. | Y | n/a | Y | P1 | 2-4No |  | Covered under item 36

## Sheet2
Buckton
Haygrove
SFG
All