## Sheet1
Reference number | Questions | Yes/No
General
Section | Scope of the Contract
A1.4 | The magnets, as manufactured, will comprise yokes, coils, water cooling circuits, electrical termination blocks, coil interconnections, insulated protective covers, support feet and all other mechanical brackets and fittings required for their full assembly.
A1.5 | The contract will be complete when all magnets have been delivered to STFC’s Daresbury Laboratory, Warrington, UK, when acceptance tests have been completed and all specified documentation, including magnetic measurement data has been received by STFC.
A1.6 | The manufacturer shall guarantee the delivered equipment against defects due to either faulty components or faulty manufacture for a period of 18 months after delivery of the equipment.
A2 | Contract Management and Quality Assurance
A2.1 | At the start of the contract the manufacturer shall nominate a Contract Engineer who will be responsible for all reporting and contact with the nominated STFC point of contact.
A2.2 | Within two weeks of the commencement of the contract, the manufacturer shall issue a detailed programme covering the design, procurement, manufacturing, testing and assembly phases in sufficient detail to allow regular progress monitoring. Thereafter, and throughout the contract, the Contract Engineer shall supply a written report to STFC every month, detailing progress with respect to this programme.
A2.4 | The manufacturer shall ensure that all subcontractors have a similar QA system and shall take all the necessary actions to guarantee the quality of the subcontractor’s delivery.
A2.5 | Within two weeks of the start of the contract, the Supplier shall provide a QA plan for STFC’s approval, listing all certification, supporting documentation and procedures that will be implemented within the contract, and which will form the basis of the final QA dossier.
A2.6 | Before completion of the contract the Supplier will provide a PDF format copy of the QA dossier, certifying that the equipment conforms to the specification and the supplied engineering drawings, and containing all certificates, relevant documents and results of test procedures.
A2.7 | The QA dossier will include full support documentation including operation and maintenance manuals and all relevant safety issues, as appropriate.
A2.8 | All documentation will be in English.
A2.9 | No acceptance or approval by STFC of quality assurance document, procedure or test result shall release the Supplier from his responsibilities in fulfilling the terms of this contract.
A3 | General Description of the Magnets
A3.1 | The magnets will all be excited by direct current (D.C.).
A3.2 | The 20 quadrupoles are all identical.
A3.3 | The 11 correctors are all identical, and will all be combined vertical and horizontal correctors.
A3.4 | The magnet yokes shall be assembled from solid or laminated steel, as specified in Section D. All types of magnet should be able to be split to allow the vacuum chamber to be introduced from above.
A3.5 | Provision for mounting survey monuments is required on the top surface of the magnets. These are detailed in the appropriate drawings.
A3.6 | The quadrupoles shall be mounted on a plate that provides a method of location with respect to the beam, as described in the specification drawings.
A4 | Quantities of the Contract
A4.1 | Bidders are to confirm that they can deliver the following items: • 20 quadrupoles, • 10 corrector magnets, • one spare quadrupole coil, and • one spare corrector coil.
A4.2 | The Contract will include: - The magnetic design of magnets to meet the performance specification - Mechanical, thermal and electrical designs, carried out in collaboration with STFC - The provision of all tools, jigs and fixtures, - The procurement of all materials for the production of the magnets - Manufacture, testing, magnetic measurement and delivery of the items
A4.3 | All designs, tools and materials obtained during the contract shall remain the property of STFC, and shall be surrendered to STFC at any time during the contract, within one month of the receipt of written notification. The manufacturer will be required to hold the tooling in a satisfactory storage area for a period of 5 years from the completion of the contract.
A4.4 | The design and all measurements shall become the property of STFC with the exception of any clearly defined prior-art which is and shall remain the property of the manufacturer.
A5 | Programme and Delivery
A5.2 | The delivery of all magnets shall be to the Daresbury Laboratory, Warrington, WA4 4AD, U.K., carriage paid by the manufacturer. Package weights should be clearly indicated on the outer cover.
A5.3 | During the contract, and particularly during the design phase, Design Review Meetings shall be held between STFC and the manufacturer. These shall alternate between STFC's Daresbury Laboratory and the manufacturer's premises.
A5.4 | All magnets shall be protected during transport from damage due to dirt, weather and rough handling. Tenderers should state, in their offer, their proposed package and delivery arrangements.
A6 | Magnetic Design
A6.1 | The design of the pole profiles and pole ends to achieve the required field configuration of the magnets will be the responsibility of the manufacturer.
A6.2 | The control of quality for the magnets will be by magnetic measurements, mechanical, electrical and thermal tests.
A7 | Engineering Design
A7.1 | Whilst the magnetic, electrical, mechanical and thermal design of the magnets, including the yokes and coils attachments, shall be the responsibility of the manufacturer, STFC has carried out preliminary work to enable the design of power supplies and other associated engineering systems to proceed. To maintain compatibility with this work, the specification of the magnets and the attached drawings define limits for some of the engineering parameters, or will indicate fixed values for certain parameters; these are mandatory, and will be contractually binding.
A7.2 | The engineering design of the magnets will include the following details: - Features for the mounting of survey monuments - A footplate to interface with STFC's girder arrangement - The position of power and water connections. These details need to comply with STFC's layout and planning and arrangements will be jointly agreed early during the design phase of the contract
A7.3 | Before the manufacture of any tools or dies commences, the manufacturer shall communicate the final conclusions of the magnetic modelling, mechanical, electrical, and thermal designs to STFC. This will take the form of CAD files in STEP/DXF format, summary papers giving numerical data and drawings of the resulting design.
A7.4 | Each individual coil, yoke and each complete magnet will be identified and numbered. The identification number will be stencilled onto the component at an agreed position, as shown on manufacturer’s drawings approved by STFC. The manufacturer shall utilise a numbering system with the following identifying format for both quality control records and the item identification: • Characters 1 to 5: ‘CLARA’ (Compact Linear Accelerator for Research and Applications); • Character 6: ‘Q’ (Quadrupole); or ‘C’ (Corrector); • Character 7: ‘C’ (Coil); or ‘Y’ (Yoke); or ‘M’ (Complete Magnet) • Characters 8 and 9: ‘nn’ (integer number starting at 09 for quadrupoles and 07 for correctors). These number sequences will be used for all manufacturing and test records and in all communications when reference is made to specific components or magnets
A7.5 | The magnets shall be designed with lifting brackets that are adequate for the support of the complete magnet.
A7.6 | The design shall ensure that the upper and lower halves of magnets correctly mate and align on reassembly after separation to insert the vacuum vessel.
A7.7 | Preliminary designs for the structures needed to support and align the bases of the magnets have been carried out by STFC and these are shown in the attached drawings. These are to be included in the manufacture of the magnets.
A8 | Drawings
A8.1 | The drawings listed in Appendix A are supplied as part of this request to tender and are an integral part of the Specification.
A10 | Testing and Magnetic Measurement of the Magnets
A10.1 | The manufacturer shall be responsible for the electrical, thermal, and mechanical testing of the magnets as specified in the appropriate sections. This shall include the provision of all test gear and measuring apparatus needed to carry out the tests as detailed.
A10.3 | Magnetic measurement of all magnets will be carried out at the manufacturer’s premises after the conclusion of all electrical and mechanical tests that are specified at works. The magnetic tests will be the responsibility of the manufacturer, and will be made on equipment supplied by the manufacturer, as described in the appropriate sections. STFC reserves the right to be represented at all such tests and measurements
A10.5 | The nature and technical capabilities of the magnet measuring equipment to be made available by the manufacturer for these tests and measurements should be fully described in the quotation.
A12 | Manufacturer's Design Drawings
A12.4 | STFC will provide a batch of drawing numbers for all design and manufacturing drawings, so that these drawings can be incorporated into the STFC registry.
A13 | Engineering Standards
A13.1 | All labelling, manuals, drawings and other documentation shall be in English.
A13.3 | All exposed conductors shall be shielded against contact to IP2X.
A13.4 | The magnets shall be built using Metric fittings and fasteners.
A13.5 | Asbestos or asbestos-type insulation, and insulation containing PCBs shall not be used. Where a choice of materials is available (e.g. cables, support hardware), preference shall be given to materials or equipment exhibiting a higher level of fire resistance.
Section B | Quadrupole Magnet Details
B1 | Description of the Quadrupole Magnets
B1.1 | Twenty identical quadrupole magnets are required.
B1.2 | All of the quadrupole magnets will be formed from a completely symmetric magnetic yoke which can be split along the horizontal centre line. The yoke and poles may be of either a laminated or solid construction. The magnets will be excited by four identical coils connected in series and mounted on the poles clear of the beam pipe. STFC require that all the magnets be water cooled (via internal or external cooling channels). The thermal and cooling parameters given in E1.3 are mandatory.
B1.3 | To generate the pure quadrupole field required in the magnets, the pole faces shall be sections of hyperbolas, with appropriate termination. The form of this termination shall be the responsibility of the manufacturer.
B1.4 | The ends of the magnets will be square with chamfering if necessary to achieve the required integrated gradient quality.
B1.5 | Details of survey monument mounts, which are required on the top face of the quadrupoles are shown in the specification drawings.
B2 | Parameters for Quadrupoles
B2.1 | The following quadrupole magnet parameters are mandatory (Please see table to the side). The magnetic parameters (strength, field quality and linearity) are scored in a separate question (PROJ1.5). |  | B2.1 Quadrupole magnet parameters | Value | Units
B3 | Magnetic Measurements of Quadrupoles |  | Number of magnets required | 20
B3.2 | The linearity of each quadrupole shall be tested as follows. The magnet shall be degaussed by powering to the nominal current in each polarity twice and then reducing the excitation to zero. The quadrupole component of the magnet shall then be measured at 5% intervals from 0 to 110% of the nominal current. |  | Number of spare coils required | 1
B3.3 | The magnet shall be rejected if any of the following conditions are met: • the integrated horizontal gradient variation at nominal current in the good gradient region is greater than the specified value; • the integrated gradient strength at nominal current is less than that specified; • the linearity is less than 98%. |  | Minimum bore radius | 20 | mm
B3.4 | The manufacturer shall assemble comprehensive documentation in PDF format relating to the tests and measurements carried out on each quadrupole. This shall record the number of the quadrupole together with details of all test results and measurement data obtained for that magnet. This will provide a long-term record of the quadrupole’s magnetic performance which is of major operational significance to STFC. |  | Maximum length outer coil edge to outer coil edge | 250 | mm
B3.5 | The manufacturer shall provide measurement data for each magnet in spreadsheet format. |  | Maximum height of magnet (excluding baseplate) | 360 | mm
Section C | Corrector Magnet Details |  | Maximum width of magnet | 360 | mm
C1 | Description of the Corrector Magnets
C1.1 | The corrector magnets must generate a combination of vertical (By) and horizontal (Bx) dipole field, independently controllable using two sets of coils.
C1.2 | The coils should be air convection cooled where possible, and water cooled if this is impractical
C1.3 | Holes must be provided for survey mounts above the beam centre.
C2 | Parameters for Correctors
C2.1 | Bidders are to confirm that they can deliver the quantities for correctors (see table to the side for further guidance). The magnetic parameters (strength, field quality, residual field and linearity) are scored in a separate question (PROJ1.6). |  | C2.1 Corrector parameters
C2.2 | Bidders are to confirm that they can meet the mechanical parameters for correctors (see table to the side for further guidance). |  | Parameter | Type 4 | Type 5 | Type 6
C2.4 | The magnets must all be able to be disassembled into two parts to enable reassembly around the vacuum chamber. |  |  | Straight 3-6 | VBC centre | Straight 7, after linac 4
C3 | Magnetic Measurements of Correctors |  | Number of magnets required | 6 | 1 | 4
C3.1 | After all electrical and mechanical tests have been completed, the correctors will be magnetically measured.
C3.2 | STFC requires the correctors to be measured using a point-by-point Hall probe (or equivalent) system. |  | C2.2 Corrector mechanical parameters
C3.3 | The first corrector will be measured in detail with the Hall probe or an equivalent system to confirm the integrated field strength over the full range of the good field region, the linearity performance, and the residual central field after cycling to nominal current and back to zero. |  | Parameter | Value | Units
C3.4 | If the first corrector successfully meets the specification then the subsequent correctors will be subject to a reduced set of magnetic tests which will confirm the integrated field strength on axis at nominal current only. |  | Minimum magnet gap (at centre) – clear aperture for circular beam pipe | Æ 40 | mm
C3.5 | The detailed test schedules of all the magnets will be agreed between STFC and the manufacturer prior to commencement of the tests. |  | Maximum allowed length of magnet | 100 | mm
C3.6 | If any magnet fails to meet the magnet specification then it shall normally be rejected by STFC. |  | Maximum allowed height of magnet | 200 | mm
C3.7 | The manufacturer shall assemble comprehensive documentation in PDF format relating to the tests and measurements carried out on each corrector. This shall record the number of the corrector together with details of all test results and measurement data obtained for that magnet. This will provide a record of the corrector’s magnetic performance which is of major operational significance to STFC. |  | Maximum allowed width of magnet | 200 | mm
C3.8 | The manufacturer shall provide measurement data for each magnet in spreadsheet format.
Section D | Magnet Yokes
D1 | Yoke Assembly - General
D1.1 | It must be possible to split the quadrupole and corrector magnets, to introduce the vacuum vessels from above.
D1.2 | Taking due account of the coil dimensions and the space required to introduce the coils onto the magnet, the manufacturer shall propose the number and nature of individual yoke sub-assemblies (blocks) from which the completed magnets will be assembled. This will be part of the engineering design, and subject to agreement by STFC. Tenderers should indicate, in their quotation, the recommended division of the yoke for the magnets.
D1.3 | Tenderers are free to propose the use of either solid or laminated yokes.
D1.4 | If laminated yokes are proposed, the tenderers should determine and indicate in their tender document the method of stacking and securing the laminations they intend to use. These methods shall be proposed as part of the engineering design, and subject to STFC’s approval.
D1.5 | Where laminated yokes are proposed, tenderers should give a clear explanation of how, by machining, they intend to ensure that the specified dimensions and angles required on the completed block will be achieved.
D2 | Steel
D2.1 | This section defines the steel quality that is to be used for the magnet yokes.
D2.2 | The magnetic performance of the magnets is the responsibility of the manufacturer, who must choose steel of the correct grade to meet the required performance. However, the material used in the magnet yokes shall comply with the following magnetic properties: (Please see table to the side) The material’s coercivity should not exceed 100 A/m. |  | D2.2 Steel properties
D3 | Dimensional Control |  | Field H (A/m) | Minimum Induction B (T) | Minimum relative permeability µr
D3.1 | The acceptance of the yokes will be determined by measuring all dimensions shown on the specification drawings or within this specification as mandatory. No further dimensional measurements are required, as acceptance is based on magnetic performance. |  | 150 | 0.5 | 2650
D4 | Painting the Yokes |  | 320 | 1 | 2480
D4.1 | After assembly and control, the yokes will be protected against rusting by coating the appropriate surfaces by means of a powder coating system of minimum thickness 0.2mm. The following faces will not be painted: - Reference and mating faces - The survey monument supports |  | 1000 | 1.5 | 1190
D4.2 | The unpainted areas shall be protected by a light oil or other rust preventative measures. The colours to be used for the magnets will be specified by STFC at an early stage of the contract.
Section E | Coils
E1 | Construction Method
E1.1 | The coils shall be constructed using solid copper conductor, or hollow conductor with a water cooling channel where necessary.
E1.5 | The coils shall be terminated on suitably mounted, insulated, connection panels.
E2 | Conductor
E2.1 | The conductor shall use oxygen-free high conductivity (OFHC) copper with a maximum volume resistivity of 17.3 nΩm at 20˚C, and its properties shall be as specified in DIN 1787 OF-Cu (DE), or BS 6017:1981 Cu-OF (UK), or A 53-100 Cu-c1 (France).
E2.2 | The material shall be in the fully-annealed condition prior to winding, and the coil fabrication method must be such as to minimise work hardening during the winding operation
E2.3 | The dimensions of the conductor shall be as determined by the manufacturer’s design, as approved by STFC.
E2.4 | The uniformity of the conductor shall be such that the resistance of all coils constructed from it shall be equal to within ±5%.
E2.5 | The use of joints within the coils will not be permitted.
E3 | Bonding and Outer-insulation System
E3.1 | No material, other than those detailed in this section shall be included in the coil without the written permission of STFC or its authorised representative. All materials must be suitable for use in a high radiation environment.
E3.6 | The coil terminals, the connection posts and all metallic parts connected to them will be insulated from the yoke and able to sustain 5 kV DC without any electrical breakdown and with an insulation resistance greater than 10 MΩ.
E3.7 | The coil terminals, the connection posts and all metallic parts connected to them will be protected against accidental contact by an insulating, transparent cover, shielded against contact to IP2X, which can only be removed by the use of tools; the tenderer’s proposals for this cover shall be described in the offer.
E3.8 | A single terminal connection post able to receive a 10 mm² cable shall be provided for earthing the yoke and other components. This shall be connected to all laminations (if used) in each block comprising the yoke by means of a single, resistive, conducting strip painted along the yoke block. This shall be designed so as not to create a shorted turn around the yoke laminations.
E4 | Water Connections
E4.2 | All hoses and pipes located on the magnet should be metric Swagelok. Swagelok American Standard Pipe Thread (NPT) is NOT to be used.
E4.3 | The manufacturer shall, during initial design, avoid locating any organic based material in the median plane of the magnet centre where it would be subject to long-term radiation damage from the electron beam. Water connections to the manifolds should be well above and below the beam-line. Where water conduits cross the beam-line horizontal plane, pipe work should be metallic.
E4.4 | The manufacturer shall ensure that there is adequate electrical connection between the earthing post, the manifolds and other components so that all the exposed metallic parts of the magnet are safely earthed by this terminal post.
E5 | Inspection and Tests of Coils at Works
E5.2 | Inspection and approval shall not release the manufacturer from any responsibilities under the terms of the contract.
E5.3 | All coils shall bear an identification number stencilled in a position as shown on manufacturer's drawings approved by STFC, as described in A7.4 above.
E5.4 | The programme of tests to be carried out shall be as specified in Section E6 below.
E5.5 | All tests shall be undertaken using equipment and procedures which have been agreed by STFC. The tenderer must specify the methods which it is proposed to use to carry out the test programme.
E5.6 | STFC reserves the right to reject any material or coil not fulfilling the conditions laid down in this specification.
E5.7 | No conductor or coil failing any test shall be used or repaired without the written permission of STFC or its authorised representative.
E6 | Test Schedule for Coils at Works
E6.1 | Test certificates shall be available relating to tests undertaken by the copper manufacturer, to include dimensions, resistivity and Brinell hardness.
E6.2 | All coils shall be visually inspected, and must be free from cracking, voids and other flaws or defects. The bonding insulation must not exhibit resin-rich areas, and the thickness of resin on the coil surface must not exceed 0.5 mm. Coils failing to satisfy any of these criteria shall not normally be accepted.
E6.3 | The electrical resistance of all coils shall be measured with a DC bridge. The values shall be corrected to 20˚C, and must be within ±5% of the mean value for all coils.
E6.4 | Each coil shall be energised until the coil temperature increases to 55˚C, as measured by the change in electrical resistance. On attaining the required temperature the current shall be interrupted and the coil allowed to cool until the conductor again assumes the ambient temperature, as measured by the conductor resistance. This cycle shall be repeated ten (10) times. Any coil exhibiting evidence of cracking or delamination shall be rejected. The manufacturer may wish to undertake this procedure on a number of coils simultaneously.
Section F | Mechanical and Electrical Tests
F1 | Mechanical Test and Measurement Programme
F1.1 | The manufacturer shall give details of their normal test procedure for routine mechanical tests during manufacture with the tender. Details of the specific tests which will be used in this contract shall be agreed at the Design Review.
F2 | Electrical Test and Measurement Programme
F2.3 | The inductance of each magnet should be measured and recorded.
F3 | Acceptance Tests after Delivery
F3.1 | After delivery, each magnet will be visually inspected for mechanical damage suffered in transit. Any such damage will be reported to the manufacturer. Possible repair will be the subject to the agreement of STFC. Where the damage has resulted in alteration to the magnet iron geometry or to the soundness or shape of coil conductor, insulation or terminals, the magnet shall normally be rejected.
F3.2 | Electrical tests shall be carried out by STFC staff at Daresbury Laboratory after delivery. The manufacturer has the right to be represented during these tests but shall notify STFC in writing if this right is to be exercised. Likewise, STFC will endeavour to provide the manufacturer with adequate notice concerning the timing of such test sequences.
F3.3 | A direct voltage of 2 kV will be applied between the terminals of each coil and its magnet yoke for one minute. Any coil showing evidence of breakdown, indicated by a leakage resistance of less than 10 MΩ, shall be rejected.
F3.4 | Each magnet will be energised with a direct current of value equal to the nominal current specified in the appropriate magnet parameters, for a period of at least two hours. Any coil showing evidence of breakdown, local hot spots or other faults during this period shall be rejected.
Section G | Fiducials for Magnets
G1.1 | Each quadrupole will be magnetically measured as described in section B3. The contractor will be required to measure, adjust and record the position of the magnetic centre from four survey fiducials equi-spaced about the magnetic centre for each magnet.
G1.2 | For each quadrupole magnet the distance between the magnetic centre and the survey fiducials must be set equal to an accuracy of ±50 µm.
G1.3 | For correctors, four survey fiducials are required on the top face of the magnet as specified on the drawing.
G1.4 | A circular area 50 mm in diameter should be left unpainted around each fiducial hole.
Section H | Tender Presentation
H1 | General
H1.1 | The tenderer must consider each clause of the specification in turn, and comment on any with which they do not propose to comply, providing in such cases a detailed explanation of any departures from the conditions defined in this specification.
H1.2 | The tenderer should indicate the proposed method of undertaking each of the required tests and measurements, including brief details of the equipment that is to be used.
H2 | Compliance and Adjudication
H2.1 | In order to allow STFC to judge the compliance and suitability of the quotation, the tenderer is asked to provide the following items of information: • the design facilities available to the tenderer in-factory; • the manufacturing facilities available to the tenderer in-factory or through a sub-contractor; • the experience of the manufacturer in the design and construction of electro-magnets for use in particle accelerators or other precision application.
H3 | Timescales and Price
H3.1 | The tenderer shall provide a programme showing the following milestones for the delivery schedule requested in section A5.1: • the placement of contract; • the commencement of design; • the completion of design and the submission of all drawings and design calculations; • the approval of the design by STFC following the Design Review meeting; • the ordering of materials; • the delivery of materials; • the completion of tooling and fixtures; • the commencement of manufacture of magnets; • the commencement of magnetic measurement of the magnets; • the delivery of the magnets.
H3.3 | The tenderer should provide information relating to the packing that would be used for delivery of the magnets.
H4 | Magnet and Engineering Design
H4.1 | An indication of the solutions or parameters for major design features should be given.
H4.2 | The tenderer should give a brief indication of the proposed method of mounting the coils on each of the magnets.
H4.3 | The tenderer should provide details of any difficulties in achieving the tolerances defined in the specification or attached drawings.
H5 | Magnetic Steel and Yoke
H5.1 | The tenderer shall indicate the proposed source of supply of the steel that will be used in the magnet yokes.
H5.2 | Technical information required for the proposed steel should include: • type of the proposed steel and whether solid or laminated steel is proposed; • thickness of laminations (if proposed); • proposed nature of bonding and insulated coating (if laminations are proposed); • quoted permeability as a function of flux density; • quoted coercivity.
H5.3 | The tenderer should indicate the test and measurement methods that are proposed for quality control of the magnetic, electrical and physical properties of the magnet steel.
H5.4 | The tenderer should indicate the method to be used to accurately measure the pole profiles.
H6 | Coil Production and Testing
H6.1 | The tenderer should indicate the expected source of supply for copper conductor.
H6.2 | The tenderer should give details of the proposed conductor sizes and cross-section, inter-turn insulation and coil winding operation for all magnets.
H6.3 | The tenderer should indicate the proposed source of supply of the epoxy resin chemical system proposed for the impregnation or bonding process, together with details of its expected mechanical, thermal and radiation properties.
H6.4 | Details of the method of mechanically binding and providing an external ground insulation to the coils should be provided. Where an epoxy resin system is proposed, the tenderer should indicate the proposed source of supply of that chemical system, together with details of its expected mechanical, thermal and radiation properties.
H6.5 | A brief description should be given of the equipment which is proposed for the various tests listed in the coil test schedule.
H6.6 | Details of the proposed direct or indirect cooling scheme should be given. Expected coolant flow, pressure drops and resulting coil temperature should be indicated.
H6.7 | The tenderer should indicate, with justification, whether coil over-temperature switches are required. Details of coil over-temperature switches should be given if they are proposed.
H7 | Electrical Connections
H7.1 | The tenderer should indicate what types of connections are proposed for the cables as well as the proposed layout of terminal boards and protective covers.
H7.2 | The tenderer should indicate the proposed method of coil electrical interconnection.
H8 | Magnetic Measurements
H8.1 | The tenderer should confirm that they propose to carry out the full sequence of magnetic tests as specified.
H8.2 | The tenderer should indicate the techniques that are proposed for the magnetic tests and, where these differ from those specified, should give a detailed explanation of how the proposed techniques will provide the measurement data required to the resolution and accuracy specified.
H8.3 | The tenderer should give a full description of the proposed equipment for carrying out the magnet measurements, together with its location if not at the factory of the manufacturer.