REFURBISHMENT WORKS to rooms

K311, K312, & K313, K207 & K208, K103 & formation of

entrance foyer interview pods

RATIONALISATION OF POWER & DATa TO ROOMS k308 & k309

# AT

CITY COLLEGE PLYMOUTH

king’s road campus

ON BEHALF OF

CITY COLLEGE PLYMOUTH

DEVONPORT

PLYMOUTH

PL1 5QG

## SPW/spw/71609

June 2017

CONTENTS

| SECTION |  | PAGE NO. |
| --- | --- | --- |
| 1 | Phase IV Works | 1-18 |
| ### COLLECTION SHEET |  |  |

|  | PHASE IV WORKS |  |
| --- | --- | --- |
|  | GENERAL INTENTIONS AND REQUIRED STANDARDS |  |
| 1.0 | DATA & POWER |  |
| 1.1 | Unless stated otherwise, data and power are to run around the perimeter of rooms affected by these works. As far as practically possible, existing installations shall be amended and existing trunking, sockets and data points shall be re-used and amended as economically as possible – generally, it is not the intention to strip out existing installations to replace with new trunking. The latter is to be a last resort in the event of obsolescence of the existing installations. |  |
| 1.2 | Where excess power and data provision exists, this is to remain in place. On no account are power and data points in any room to be removed/reduced. Amended and new installations shall be in accordance with the City College furniture layout drawings. |  |
| 1.3 | New trunking shall be Marshall Tufflex Monoplus 20 trunking or equivalent approved, colour white, with Krone CAT5e data points or equivalent approved, colour white. All sockets shall be standard model as manufactured by MK, MEM, Schneider or equivalent approved. See Appendix “Structured Cabling Infrastructure Specification Category 5e and 6a” document for reference. Where an alternative manufacturer is proposed, a sample of the product proposed shall be deposited in the Plymouth office of Vickery Holman and the CA shall seek the approval of the client prior to ordering. |  |
| 1.4 | Where power and data are already situated within existing walls and new trunking is being installed to the perimeter of the room, these installations shall be brought forward and mounted within the new dado trunking as required to form one homogenous installation. |  |
| 1.5 | A workstation is defined as 2 No Double Socket Outlets (DSO) and 1 No Cat5e data point. Where this requirement needs to be augmented, this is noted under the specific room below. |  |
| 1.6 | Please see the CCP standard specification for teaching walls, the provision of which will be required in each of the classrooms (but not the offices) affected by the works. Amend, adjust and add to existing installations to meet the specification. |  |
| 2.0 | NEW INTERNAL DOORS |  |
| 2.1 | It is the intention to match the newer style of self-finished door at the Kings Road site where new doors are installed. Veneer shall be the closest available match to the newer, existing doors on site. For the purposes of pricing, assume Beech. Where necessary, a sample of the veneer shall be provided to the CA for client approval prior to ordering. All new doors will be FD30S fire doors. Doors to classrooms and offices shall be fitted with 1 No push plate 300 x 15 x 1.5mm (H x W x D) and 1 No matching kick plate minimum 300mm height and for the full width of the door, minimum 150 x 800 x 1.5mm (H x W x D) to the external face of the door. Kick plate and push plate to be satin anodised aluminium finish. Check with CA prior to ordering. Doors shall be fitted with 1 No heavy-duty door closer suitable for use on a fire door, eg Briton 2003EN SES Silver or equivalent approved. Doors shall have long vision panel (for the purposes of pricing, assume 200 x 1200mm (W x L) set 600mm FFL and in from the leading-edge rail 160mm. Fire doors shall have 3 No new fire door hinges to new door, with 2 No fixed to the top of the door and one to the bottom: top and bottom hinges shall be 200mm from the head and the bottom of the door respectively and the third hinge shall be set 200mm down from the top hinge. Hinges shall be a standard twin ball bearing 100 x 75 x 3mm (L x W x D) grade 201 stainless steel. |  |
|  | NB - rubber blade type fire door seals will not be adequate for this application and new seals shall be brush type 10mm rebated fire door seals, colour brown. Seals shall be fitted to the head and rails of the door and the new door shall have a 2-4mm gap between the head and rails and the frame with a 3mm gap between the floor and the foot of the door. |  |
| 2.2 | New doors shall be fitted with 1 No pair of good quality lever door handles with backplate suitable for use with KABA locks and with SAA finish to match the other new door furniture. The preferred style and design is to match the existing door handles and configuration to room K716 (there is a mix of handle type and designs to the tower block). Check with CA prior to ordering. |  |
| 2.3 | Where doors are replaced, ensure that all existing signs are salvaged from existing doors prior to disposal and re-use/re-mount signs to new doors unless instructed otherwise. |  |
| 3.0 | LOCKS |  |
| 3.1 | The College uses a KABA suited lock system across the King’s Road Site. No such lock shall be disposed of and all “spare” locks arising shall be handed back to the Estates Department for recycling. Where new locks are required, these shall be KABA 20 System, KABA 22mm cylinder, round profile with thumb turn and new KABA lock case, profile cylinder mortice sash lock (76mm). Supply 5 No keys for each new lock to be handed to the client at completion. To habitable rooms (ie not cupboards), a thumb turn release to facilitate emergency escape will be required. |  |
| 4.0 | DECORATION |  |
| 4.1 | Double height rooms (eg KW032A) shall be decorated to a height of 2.0m FFL only. |  |
| 4.2 | Paint used in decoration shall be Johnstone’s, Crown, Dulux or equivalent and shall be used in accordance with manufacturer’s most recent instructions. For the purposes of pricing, assume Dulux colours: Walls: 1 No undercoat, 2 No topcoats vinyl matt, colour “Tuscan Treasure 6”, code 25YY83103 Woodwork: 1 No primer coat, 1 No undercoat, 2 No topcoats Paint Mixing Eggshell, colour “Stonewashed Blue”, code 70BG28169 |  |
| 5.0 | CARPET TILES |  |
| 5.1 | Carpet tiles installed shall be new Forbo Tessura Teviot loop pile floor tiles or equivalent approved, colour “Nightsky” or nearest equivalent. Supply and fix all necessary threshold coverings/strips where required to leave no trip hazard (for the purposes of pricing assume threshold strips colour black, check with CA prior to ordering). |  |
| 6.0 | SKIRTINGS |  |
| 6.1 | Skirtings shall be of FSC softwood and shall match the profile found in each room and shall be nailed and glued securely in each location as required. Similarly, where piecing-in with new timber/skirting is required, the profile of the new timber shall match the existing timber skirtings. Where in doubt, contact the CA. |  |
| 7.0 | ROOM DESIGNATIONS |  |
| 7.1 | Room numbers stated refer to the room designations shown on the CCP furniture layouts and on site some designations are currently different to the proposed albeit that room numbers remain generally consistent. |  |
| 8.0 | power & data only to rooms k308 & K309 |  |
| 8.1 | See City College Plymouth furniture layout for KR Tower Block 3rd Floor. It is the intention to recycle as much of the existing trunking complete with DSO and Cat 5e points as possible and existing installations should be left in situ where they will accommodate the required room layout. Amend, adjust, add to (supply and fix) new trunking and 2 No DSO and 1 No Cat 5e data point to accommodate 10 No workstations within each room (ie 20 No DSO and 10 No Cat 5e data points per room; 40 No DSO and 20 No Cat 5e in total). |  |
| 8.2 | No other works are required to this room. |  |
| 9.0 | EXISTING rooms K311, K312 and K313 |  |
| 9.1 | The three existing rooms are to be merged to form two classrooms of 40m². classrooms). Carefully remove ceilings to the existing rooms K312 and K313 complete – it is the intention to retain/ adapt/ extend the suspended ceiling to existing room K311. |  |
| 9.2 | Having isolated, disconnected and capped off any services within walls prior to commencement, carefully take down and dispose from site of all stud walls forming rooms K312 and K313 and the free-standing stud partition to room K311. Make good all surfaces disturbed. Carefully separate the existing installations for power and data to each room and amend the existing power and data and trunking as required. |  |
| 9.3 | Using softwood carcassing and polythene as required, ensure that both sides of the new door aperture are screened off across the corridor to minimise the spread of dust prior to proceeding. Propping and shoring as required and prior to the installation of the new demountable partition (see below), carefully cut a new door aperture to the northern/ paradise road side classroom ready to receive the new door. Supply and fix 1 No suitably sized concrete or steel lintel over the door and make good using proprietary finishing plaster prior to decoration. |  |
| 9.4 | Carefully take up the existing carpets to former rooms K311, K312 &K313 complete and dispose of from site. Allow for 10m2 of concrete repairs using Fosroc Nitomortar PE (or similar approved) as per manufacturer’s recommendations (Fosroc Ltd, Drayton Manor Business Park, Coleshill Road, Tamworth, Staffordshire, B78 3XN, tel: 01827 262222, www.fosroc.com, email: enquiryuk@fosroc.com . Leave levels as flush as possible ready to receive self-levelling latex. To the whole of the floor to both new classroom spaces and the floor to extend under the floor, apply self-levelling latex such as Arditex by Ardex or equivalent approved (Ardex UK Ltd, Homefield Road, Haverhill, Suffolk, CB9 8QP, tel: 01440 714939, www.ardex.co.uk). |  |
| 9.5 | To the location shown in drawing 71609/402 Supply and fix 1 No. new proprietary demountable partition to achieve not less than 45dB sound reduction between rooms to the underside of the concrete soffit (no windows/ vision panels within, vinyl finish, eg Slimline Executive 100mm partitioning by Avon Paritioning Solutions, tel: 0333 772 0912, www.avonpartitioningsolutions.co.uk, email: enquiries@avonpartitioning.co.uk). The wall shall be acoustically attenuated using Knauf Earthwool Acoustic Roll (widely available) or equivalent approved at the ceiling soffit so that transfer of sound between rooms is minimised. |  |
| 9.6 | Carefully amend, adjust and reinstate the existing suspended ceiling remaining from the previous configuration of the former rooms to meet the new partition wall. To the classroom with no remaining ceiling, install new white metal framed suspended ceiling, 600 x 600mm fissured ceiling tile such as Ecophon Focus A or equivalent approved (Saint-Gobain Ecophon, Old Brick Kiln, Monk, Sherbourne Road, Ramsdell, Tadley, RG26 5PP, Telephone: 01256 855213 |  |
| 9.7 | In accordance with the Fitzgerald lighting specification or equivalent approved, in each of rooms K311 & K312 and re-using the existing light switches in each room, supply and fix 6 No Fitzgerald Spectrum 66w LED surface mounted luminaires (ie 12 No in total) connected into the existing light switch. Lighting shall achieve a minimum of 300 lux at desk level in both rooms. |  |
| 9.8 | To both new classroom areas, supply and fix new Forbo Tessura Teviot loop pile floor tiles or equivalent approved, colour “Nightsky” to both floors complete. www.forbo.com/flooring/en-uk/ Where an alternative product is proposed, a sample will be required to be delivered to the Plymouth office of Vickery Holman for client approval prior to ordering. |  |
| 9.9 | As described in the standard specification above, to new door opening to room K314, supply and fix 1 new door with long vision panel, door lining and architraves etc as required and all door furniture previously described. Supply and fix new door closer suitable for a fire door and as previously described. |  |
| 9.10 | Decorate rooms K312 and K314 throughout as described above. |  |
| 10.0 | Merging of Existing Rooms K207 (Quality Improvement Team) & K208 (Head of Library/ Learning Resources) to Form 1 No 40m2 Classroom |  |
| 10.1 | Protect the carpet to room K207 complete prior to commencing works. The carpet is to remain (it is relatively new) and shall be extended into the newly merged room. Take up and dispose of from site the carpet to Room K208 (red in colour) complete. Make good the existing floor using Fosroc Nitomortar PE or equivalent approved – for the purposes of pricing, assume 1.5m2 of repairs will be required prior to laying new latex. Include to use the same compound along the whole of the line of the wall to be removed. |  |
| 10.2 | To the whole of former room K207 complete (including the line of the removed masonry partition) lay self-levelling latex taking care to protect the carpet to the former room K208. |  |
| 10.3 | Following demolition, to the whole room K208 lay new Forbo carpet tiles or equivalent approved as previously described. Ensure no trip hazard where laying up to the existing carpet to the former room K207. Supply and fix all necessary threshold strips. |  |
| 10.4 | Carefully amend and support the plasterboard ceilings to rooms K207 & K208 to reveal the partition between the rooms to facilitate demolition of the existing masonry partition wall. Reinstate the ceiling with new plasterboard securely fixed as required to leave all at one continuous level across the whole (newly integrated) room. All joints shall be scrim taped and the entire ceiling skimmed with plaster prior to decoration. Include to decorate the ceiling complete, 1 No undercoat and 2 No topcoats vinyl Matt, colour white. |  |
| 10.5 | Having first disconnected all services within the partition to be removed, carefully take down the masonry partition between rooms K207 & K208 to floor level and dispose of all masonry, debris and arisings from site. Make good floor using proprietary concrete flooring screed and leave all levels flush ready to receive new self-levelling floor screed. Piece-in new timber skirtings where partition formerly stood as needed and as previously described prior to decoration. |  |
| 10.6 | Remove and cap-off the light switch to former room K207 and remove the light switch to former room K208. Replace that to K208 with 1 No new white plastic faced triple gang 2 way light switch (MK, MEM, Schneider or equivalent approved) linked into newly configured lighting (see below). Reconfigure switching to facilitate economic use of lighting in day-to-day teaching (ie to have the facility to switch off rows of lights to enable the electronic board to be more visible). |  |
| 10.7 | Carefully take down and hand back to the College the existing light fittings within both rooms. Disconnect and remove the light switch located next to the door to be blocked up and cap off with 1 No white plastic blanking plate screw-fixed into the wall as required. In accordance with the Fitzgerald lighting specification (or equivalent approved and re-using the existing light switch, supply and fix 6 No Fitzgerald Spectrum 66x LED surface mounted LED luminaires (or equivalent approved), 5 No standard panels and 1 No emergency light panel, to achieve a minimum of 300 lux at desk level. |  |
| 10.8 | Decorate newly formed, enlarged classroom throughout as described above. Decorate corridor side of new door opening to K314 to 0.5m around the new door frame. (Generally, decorate door frames, architraves etc complete/ both sides). |  |
| 11.0 | Door to Former Room K207 |  |
| 11.1 | Carefully remove the door and door lining complete to the former room K207 and set aside ready for recycling in the existing door aperture of room K103B. |  |
| 11.2 | Carefully block up the opening now revealed from the removal of the door with new timber or metal studwork partitioning and leave all walls level and flush both sides as far as possible. All joints to be scrim taped and surfaces to be skimmed with finishing plaster as required prior to decoration. Supply and fix as required new skirting boards and piece-in with the existing prior to decoration (for the purposes of pricing allow 2 linear metres in total). Decorate both sides of the infilled opening to match colours as closely as possible on the respective sides and as detailed above. Decorate 0.5m around the former doorway both sides. |  |
| 12.0 | Room K103 |  |
| 12.1 | It is the intention to form a new 30m2 EMMS & HE Classroom by taking space from the existing room 103 (currently a very large IT room). The larger area of the room which is to be designated K103B at the conclusion of the works is to have almost no work undertaken within with the exception of carpet, lighting and replacement of the suspended ceiling. Light fittings to the room are relatively new – disconnect these and set aside for reinstatement at the completion of the works. |  |
| 12.2 | Having made provisions to limit the spread of dust to rooms and the corridor as described elsewhere, shoring and propping as required, carefully cut a new door opening to new room K103B as shown on the Vickery Holman drawing 71609/406 and to accommodate the door to be recycled from room K207. Supply and fix 1 No new precast concrete or steel lintel sized to suit and insert on the wall over new door opening. Plaster both sides using finishing plaster as required prior to decoration. |  |
| 12.3 | In the new door opening, insert the door and door lining previously set aside from room K207 complete and make good all surfaces disturbed prior to decoration. Generally overhaul and service the door and leave all in full working order. |  |
| 12.4 | To the corridor side of the new door, decorate 0.5m around the door frame, colour and paint type to match existing to corridor and as detailed above. |  |
| 12.5 | Decorate rooms K103 and K103B throughout as described elsewhere. Include the whole of the doorframes and linings in each case. |  |
| 12.6 | Carefully take down and dispose from site of the existing carpet to room K103 complete and the remove and dispose of the entire suspended ceiling ready to receive new. |  |
| 12.7 | Allow for 5m2 of concrete repairs using a suitable proprietary concrete repair product as described elsewhere prior to latexing the floor. |  |
| 12.8 | Latex the entire floor area of K103 complete using self-levelling latex as described elsewhere or similar approved prior to laying new carpet tiles. |  |
| 12.9 | Supply and lay new Forbo carpet tiles to the entire area of existing room K103. |  |
| 12.10 | Located as shown in the CCP room layout (KR Tower Block – 1st Floor) and Vickery Holman drawing 71609/406, supply and fix 1 No new self-finished demountable partition, colour blue (check with CA prior to ordering) suitable for dividing offices with noise attenuation to 45dB or better. Take the partition up to the concrete soffit and fix into the soffit as required. |  |
| 12.11 | Supply and fix new suspended ceilings to both new rooms (K103 & K103B) complete – eg Ecophon Focus A or equivalent approved (Saint-Gobain Ecophon, Old Brick Kiln, Monk, Sherbourne Road, Ramsdell, Tadley, RG26 5PP, Telephone: 01256 855213). |  |
| 12.12 | Located as per the Fitzgerald lighting plan, reinstate the light fittings previously set aside within room K103B. Supply and fix 1 No new 3 switch white plastic faced light switch and matching back box and all necessary white trunking as previously described and connect light fittings to permit economic use of the lighting in the room. |  |
| 12.13 | To room K103 and in accordance with the Fitzgerald lighting plan (or equivalent approved to achieve a minimum of 300 lux at desk level), supply and fix 9 No Celestial 35w LED recessed panels (7 No standard and 2 No emergency lights) or equivalent approved and supply and fix 1 No new white plastic triple switch light switch and matching back box and all necessary surface mounted trunking and cabling to enable economic switching of the lighting within the room. |  |
| 12.14 | Power and Data As an existing IT room there is no additional requirement for new trunking, DSOs and Cat 5e points to either room. Amend the existing installations so that power and data are available in each room. |  |
| 13.0 | ENTRANCE FOYER INTERVIEW ROOMS |  |
| 13.1 | The suspended ceiling to the entrance foyer lobby is new. Carefully take down the area of the existing suspended ceiling affected by these works only and amend as required following construction of the new rooms to leave all reinstated and neat and tidy at completion. Disconnect any light fittings affected by these works and hand these back to the College for use elsewhere on site (these are new). |  |
| 13.2 | CCP require 4 No small interview rooms to be installed sat on the existing linoleum in the entrance foyer area which offer a good measure of sound attenuation and privacy for interviews see drawing 71609/408. This is defined as not less than 40dB sound reduction across walls and ceilings if not better. The new rooms also require a ventilation installation which doesn’t compromise privacy, and similarly, arrangements for power and data, penetrations to structures installed etc will need to ensure that privacy is ensured. Further, ventilation needs to be independently controlled from within each room and to be “silent running” so as not to cause irritation to the occupants where persons are sensitive to constant hums, high pitched frequencies and so forth. | _ |
| 13.3 | Using proprietary timber (preferred) or metal 100mm stud partitioning with studs set at 400mm centres, construct the new rooms in stud walling shown in the Vickery Holman drawing 71555/408. As shown in the drawing, the works will provide rooms of slightly varying size to suit the available space: 1 No room = 1550 x 4200 x 2400 mm (W x L x H) 2 No rooms = 1550 x 4400 x 2400 mm 1 No room = 1725 x 4400 x 2400 mm Fully fill the cavity of the new stud walls using a high-density sound attenuating quilt such as Earthwool 100mm Acoustic Roll or equivalent approved. |  |
| 13.4 | Decorate all rooms internally and externally as described previously. |  |
| 13.5 | To each room, supply and fix 1 new FD30S fire door as described elsewhere (these must achieve a minimum of 30dB sound attenuation to maintain privacy in the booths), 4 No in total. All doors shall comply with the standard specification as written above and shall have 1 No long vision panel also as previously described. Door closers are not required to the rooms. Supply and fix all necessarily door linings, frames, architraves etc all as previously described. |  |
| 13.6 | Supply and fix new suspended ceilings to the 4 No new booths complete Ecophon Focus A or equivalent approved (Saint-Gobain Ecophon, Old Brick Kiln, Monk, Sherbourne Road, Ramsdell, Tadley, RG26 5PP, Telephone: 01256 855213). or equivalent approved. Over the new suspended ceilings to all rooms, lay new 100mm thick sound attenuating quilt such as Earthwool Acoustic Roll or equivalent approved. |  |
| 13.7 | Within the new suspended ceiling grid within each room supply and fix 1 No new extract inlet cover in white plastic. For the purposes of pricing assume size to be 150 x 150mm. Connect to proprietary plastic ducting ready to connect into new extract fans – these will supply air to the booths rather than extract. |  |
| 13.8 | Mounted the required distance away from the booths being served supply air so as vibration/ humming does not irritate occupants of the interview rooms, mount above the suspended ceiling to the corridor 4 No proprietary standard 150mm diameter extract fans (eg Vent Axia, Vectaire or equivalent approved) suitable for connecting to new duct which shall be laid on top of the corridor suspended ceiling. All fans are required to be manually operable. To this end, supply and fix within each interview room 1 No new white plastic faced switch and connect this in each case to the new fans. To minimise vacuum effects and lifting of surrounding ceiling tiles where the new fans are in operation, remove 3 No ceiling tiles from the corridor suspended ceiling (hand these back to Estates as they are new) and replace with (ie supply and fix) 3 no new white plastic “Egg Crate” grilles sized as the ceiling tile and to sit in the existing suspended ceiling grid. Supply and fix all necessary fuse spurs, cabling etc to provide an installation which complies with the relevant standards including the IEE Regulations 17th edition. |  |
| 13.9 | Each interview room will require power and data for 1 No workstation in each room set in dado trunking as detailed above. It is imperative that the sound integrity of the new rooms is not compromised by new installations and fixings to walls – if in doubt, check with CA prior to proceeding. For the purposes of pricing, assume length of trunking required in each room to be 1550mm set above desk height and containing 2 No DSOs and 1 No Cat 5e data point in each room (in total, 8 No DSO and 4 No Cat 5e data points). Assume that trunking installations can be installed back-to-back on the new partition walls. |  |
| 13.10 | In each of the interview pods and in accordance with the Fitzgerald lighting specification or equivalent approved, supply and fix 1 No Fitzgerald Celestial 35w LED recessed panel (or equivalent approved) to achieve 300 lux at desk height. To each pod, also supply 1 No new white plastic single switch light switch and matching back box along with all necessary cabling to connect the new light fittings. NB – do not compromise the sound integrity of the pods through installations and fixings. If in doubt, consult with CA prior to proceeding. |  |
| 13.11 | Heating will not be required within the new interview rooms. If required in future, this will be attended to separately. |  |

PHASE IV WORKS

REFURBISHMENT WORKS to rooms

K311, K312, K313, K207 & K208, K103 & formation of

entrance foyer interview pods

RATIONALISATIONa OF POWER & DATa TO ROOMS k308 & k309

AT

City college plymouth

king’s road campus

COLLECTION SHEET

| SECTION |  | PAGE No. | £ p |
| --- | --- | --- | --- |
| 1 | PHASE IV WORKS | 1-13 |  |
| ## Total Excluding VAT |  |  |  |

Date:  …………………………………………………………………………..

In the Capacity of:  	………………………………………………………………….

Authorised to sign

on behalf of :  		………………………………………………………………….

Registered Address:  	………………………………………………………………….

………………………………………………………………….

SPW/SPW/71609

Date 2017