## Panel Schedule
| BMS Panel Reference - Old Ref | Distribution Board Ref | MCB Ref | Rating | Type | Breaker Type | Isc(kA) | SIZE (mm2) | No of Cores | TYPE | COMMENTS | No | Drawing No
PLANT FLOOR F3
1 | AHU01A_ACP01 - AHU No 1A | DB_MCP1_A_LO2 | 8 - L2 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. Drawing has wrong detail as 1-L1 | 1 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| AHU02A_ACP01 - AHU No 2A | DB_MCP1_A_LO2 | 8 - L3 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 2 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
1 | AHU03A_ACP01 - AHU No 3A | DB_MCP1_A_LO2 | 10 - L1 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 3 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| BMS Network Panel | DB_MCP1_A_LO2 | 10 - L2 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 4 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| Leak Detection | DB_MCP1_A_LO3 | 19 - L1 | 16A | D | MCB | 10 | 6 | 3 | DRAKA | N/A | N/A | N/A
1 | AHU01B_ACP01 - AHU No 1B | DB_MCP1_B_LO2 | 1 - L1 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. Drawing has wrong detail as 8-L2 | 5 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
1 | AHU02B_ACP01 - AHU No 2B | DB_MCP1_B_LO2 | 1 - L2 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 6 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
1 | AHU03B_ACP01 - AHU No 3B | DB_MCP1_B_LO2 | 1 - L3 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 7 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| CHW_BMP02 - CHW Plant 2 BMS | DB_MCP1_B_LO2 | 2 - L2 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 8 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| LTHW _BMP01 - LTHW/Steam / HWS BMS | DB_MCP1_B_LO2 | 2 - L3 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 9 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| LV_BMP02 - LTHW/Steam / HWS BMS | DB_MCP1_B_LO2 | 3 - L2 | 16A | D | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 10 | P800-KIR-SMP-F3-LAY-001-PDF (EE1005)
| PHS_BMP02 - PH DWS System BMS | DB_MCP2_A_ LO2 | 6 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 11 | P800-KIR-SMP-F3M2-LAY-001-PDF (EE1006)
HEPA DECK F2
1 | AHU01_BMP01 - AHU01 Loc FO BMS | DB _06_ A_F2 | 1 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU01_BMP02 - AHU01 Lot F1 Zone 1 BMS | DB _06_ A_F2 | 1 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU01_BMP03 - AHU01 Loc F1 Zone 2 BMS | DB _06_ A_F2 | 1 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP07 - AHU02 Loc BMS | DB _06_ A_F2 | 2 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP01 - AHU02 Local Suite 1 BMS | DB _06_ A_F2 | 2 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP02 - AHU02 Local Suite 2 BMS | DB _06_ A_F2 | 2 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP03 - AHU02 Local Suite 3 BMS | DB _06_ A_F2 | 3 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP04 - AHU02 Local Suite 4 BMS | DB _06_ A_F2 | 3 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP05 - AHU02 Local Suite 5 BMS | DB _06_ A_F2 | 3 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_BMP06 - AHU02 Local Suite 6 BMS | DB _06_ A_F2 | 4 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU03_BMP01 - AHU 03 Local BMS | DB _06_ A_F2 | 4 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
| AHU01_PLP01 - AHU01 Loc F0 PLC | DB _06_ A_F2 | 4 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU01_PLP02 - AHU01 Loc F1 Zone 1 PLC | DB _06_ A_F2 | 5 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU01_PLP03 - AHU01 Loc F1 Zone 2 PLC | DB _06_ A_F2 | 5 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP07 - AHU02 Loc PLC | DB _06_ A_F2 | 5 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP01 - AHU02 Local Suite 1 PLC | DB _06_ A_F2 | 6 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP02 - AHU02 Local Suite 2 PLC | DB _06_ A_F2 | 6 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP03 - AHU02 Local Suite 3 PLC | DB _06_ A_F2 | 6 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP04 - AHU02 Local Suite 4 PLC | DB _06_ A_F2 | 7 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP05 - AHU02 Local Suite 5 PLC | DB _06_ A_F2 | 7 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU02_PLP06 - AHU02 Local Suite 6 PLC | DB _06_ A_F2 | 7 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | AHU03_PLP01 - AHU 03 Local PLC | DB _06_ A_F2 | 8 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | Network Rack | DB _06_ A_F2 | 8 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | SMS_01 | DB _07_ A_F2 | 9 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 12 | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
| SMS_02 | DB _06_ A_F2 | 9 - L3 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 13 | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | SMS_03 | DB _06_ A_F2 | 10 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 14 | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
| MVHR01 BMS Control Panel | DB _06_ A_F2 | 10 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
1 | SMS HMI Enclosure | DB _06_ A_F2 | 11 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
| Fumigation/BMS HMI | DB _06_ A_F2 | 11 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Distribution board backed up by single large UPS Riello UPS Master MPS 30kVA unit with Bypass switch |  | P800-KIR-SMP-F2-LAY-001-PDF (EE1004)
GROUND FLOOR F1
| Incinerator Gas Panel BMP01 | DB_05_A_LGF | 11 - L1 | 32A | C | MCB | 10 | 10 | 3 | XLPE SWA | Sentinel Pro single phase on line 2.2kVA (1980W) 240v a.c. | 15 | P800-KME-SMP-F1-LAY-001-PDF (2 of 2) (EE1003)
| Leak Detection | DB_05_A_LGF | 10 - L3 | 20A | B | MCB | 10 | 4 | 3 | XLPE SWA | N/A | N/A | N/A
| BMS Workstation | DB_15_B_LGF | 9 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 16 | P800-KME-SMP-F1-LAY-001-PDF (2 of 2) (EE1003)
| BMS Zone Information Panel | DB_15_B_LGF | 22 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 17 | P800-KME-SMP-F1-LAY-001-PDF (2 of 2) (EE1003)
ETP FO
| Leak Detection Undercroft | DB_11_B_LB2 | 18 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | N/A | N/A | N/A
| Leak Detection ETP Hall | DB_11_B_LB2 | 18 - L2 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | N/A | N/A | N/A
| Zone Control Panel (ETP) | DB_11_B_LB2 | 19 - L1 | 16A | C | MCB | 10 | 6 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 18 | P800-KIR-SMP-F0&F0M-LAY-001-PDF (EE1001)
EXTERNAL COMPOUND
| CHW_BMP01 - CHW Plant 1 External BMS | DB_09_A_EX1 | 8 - L3 | 20A | B | RCD | 10 | 4 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 19 | P800-KIR-SMP-xx-LAY-001-PDF (EE1007)
| NCP_EXT_NCP04 - NCP_EXT_NCP04 | DB_09_A_EX1 | 9 - L1 | 20A | B | RCD | 10 | 4 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 20 | P800-KIR-SMP-xx-LAY-001-PDF (EE1007)
| LV_BMP01 - Diesel +LV Monitoring BMS | DB_18_B_EX2 | 7 - L1 | 20A | B | RCD | 10 | 4 | 3 | XLPE SWA | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. | 21 | P800-KIR-SMP-xx-LAY-001-PDF (EE1007)
| Trace Heating | DB_08_A_L02 | 5 - L1 | 20A | B | MCB | 10 | 4 | 3 | XLPE SWA | UNKNOWN LOCATIONS TBC | N/A | N/A
1 | Trace Heating | DB_08_A_L02 | 6 - L3 | 20A | B | MCB | 10 | 4 | 3 | XLPE SWA | UNKNOWN LOCATIONS TBC | N/A | N/A
| Trace Heating (Roof) | DB_08_A_L02 | 7 - L1 | 20A | B | MCB | 10 | 4 | 3 | XLPE SWA | UNKNOWN LOCATIONS TBC | N/A | N/A
| Trace Heating (Roof) | DB_08_A_L02 | 7 - L3 | 20A | B | MCB | 10 | 4 | 3 | XLPE SWA | UNKNOWN LOCATIONS TBC | N/A | N/A
| Trace Heating | DB_17_B_L02 | 8 - L3 | 20A | B | MCB | 10 | 4 | 3 | XLPE SWA | UNKNOWN LOCATIONS TBC | N/A | N/A
1
1
1
1