## Front Cover
SCHEDULE OF WORKS
FOR THE
ALTERATIONS
TO
CANCER INFORMATION SERVICE
GROUND FLOOR ENTRANCE
SOUTH BLOCK
AT
SCARBOROUGH GENERAL HOSPITAL
WOODLANDS DRIVE
SCARBOROUGH
YO12 6QL
Sweett Group
Tower North Central
9th Floor
Merrion Way
Leeds LS2 8PA
Date: | 2015-05-19
Job Nr | 50069.199
Revision: | -
Revision Date:
`

## QA
CANCER INFORMATION SERVICE
CONTENTS
| Document prepared by |  | Alan Bedford | `
:
Signed
Date
For and behalf of Sweett Group
| Checked and Verified by | :
Associate Director
Signed
Date
For and behalf of Sweett Group
* Delete as applicable, if uncontrolled state reason

## Contents
CANCER INFORMATION SERVICE
CONTENTS
QA
Section One | Preliminaries
Section Two | Preambles/Materials and Workmanship
Section Three | Schedule of Works |  |  | `
Section Four | General Summary
Section Five | Form of Tender |  | Not required
Appendix A | Drawing Issue Sheet [Sweett]
Appendix B | Trust Guidelines for Contractors Working for the York Hospitals NHS Trust
Appendix C | Routine Maintenance of Artex ceilings and fixed equipment
Appendix D
Appendix E
Appendix F
Appendix G
Appendix H
* Delete as applicable, if uncontrolled state reason

## Sect 1 - Prelims
CANCER INFORMATION SERVICE
SECTION ONE
`
PRELIMINARIES
* Delete as applicable, if uncontrolled state reason

## Sect 2 - Preambles
CANCER INFORMATION SERVICE
SECTION TWO
PREAMBLES/MATERIALS & WORKMANSHIP
* Delete as applicable, if uncontrolled state reason

## Sect 2 - M&W
CANCER INFORMATION SERVICE
SECTION TWO
MATERIALS AND WORKMANSHIP
| C | Existing site/buildings/services
| C10 | Site survey
| C11 | Site investigation
| C20 | Demolition
| C41 | Repairing/ Renovating/ Conserving masonry
| F | Masonry
| F10 | Brick/ block walling
| F30 | Accessories/ sundry items for brick/ block/ stone
walling
| F31 | Precast concrete sills/ lintels/ copings/ features
| K10 | Plasterboard dry linings/ partitions/ ceilings
| K11 | Rigid sheet flooring/ sheathing/ decking/ sarking/
linings/ casings
| K30 | Panel partitions
| K40 | Demountable suspended ceilings
| L20 | Doors/ shutters/ hatches
| L40 | General glazing
| M | Surface finishes
| M10 | Cement based levelling/ wearing screeds
| M20 | Plastered/ Rendered/ Roughcast coatings
| M50 | Rubber/ plastics/ cork/ lino/ carpet tiling/ sheeting
| M60 | Painting/clear finishing
| N | Furniture/Equipment
| N10 | General fixtures/ furnishings/ equipment
| N14 | General signage systems
| N15 | Fire and safety signage systems
| P | Building fabric sundries
| P12 | Fire stopping systems
| P21 | Door/ window ironmongery
| P31 | Holes, chases, covers and supports for services
* Delete as applicable, if uncontrolled state reason

## Sect 3 - SoW
CANCER INFORMATION SERVICE
SECTION THREE
`
SCHEDULE OF WORKS
* Delete as applicable, if uncontrolled state reason

## SOW-Mgt
CANCER INFORMATION SERVICE
Please insert individual figures and amounts in to the Qty, Unit, Rate and Amount columns
Item | Description | Qty | Unit | Rate | Amount
0.0 | THE WORKS
0.0.1 | To carry out alteration works to the existing Cancer Information Service to the main entrance area to the South Block shown in more detail on drawings 50069.199-01 including all associated works. |  | item
0.0.2 | The works are to be carried out in strict accordance with the Preliminaries, Preambles, Specifications and Drawings; |  | item
0.0.3 | The Contractor must programme all works to achieve completion within the designated Contract period; |  | item
0.0.4 | The Contractor is to allow for out of hours and/or Weekend working to achieve completion within the designated Contract period; |  | item
0.0.5 | The Employer will not accept any claim from the Contractor for working outside normal working hours; |  | item
0.0.6 | Where materials are specified by manufacturers name, a full set of manufacturers instructions are to be retained on site and it is the Contractors responsibility that they are strictly observed at all times; |  | item
0.0.7 | The Contractor is to bring to the attention of the Contract Administrator (CA) at Tender stage any discrepancies or variations between the drawings, specifications, instructions and manufacturers instructions; |  | item
0.0.8 | The Contractor must also bring to the attention of the manufacturer/materials supplier immediately, any discrepancy between the materials supplied, the manufacturers literature or site conditions; |  | item
0.0.9 | The Contractor shall indemnify the Employer against all third party claims emanating from the works; |  | item
0.0.10 | The Employer and the CA reserve the right to amend or omit any items of the works by instruction. No claims for loss, expense or delay shall be allowed in connection with such; |  | item
| Total carried forward to Section 3 summary sheet |  |  |  | 0
0.1 | MANAGEMENT
0.1.1 | Supervision Allow for maintaining the same full time working Foreman on site, for the Full duration of the works to effectively programme resources, receive instructions from the CA, in full accordance with the Preliminaries section; |  | item
0.1.2 | The Foreman is to remain the same throughout the duration of the works, be experienced in this type of work, be responsible for supervision and control of these works, and be able to programme resources accurately, be able to monitor and coordinate sub contractors and suppliers. |  | item
0.1.3 | Safety/CDM Regulations This project is not notifiable to the Health & Safety Executive (HSE) as the Contract period is not expected to exceed 30 working days or 500 man days; |  | item
0.1.6 | The Contractor is to allow for acting as Principal Contractor as defined by the CDM Regulations, and must include for all specific requirements detailed in the Preliminary clauses of the specification and Pre Construction information, contained within the Preliminaries section. |  | item
0.1.7 | The Contractor is to provide suitable Health & Safety Plans, Method Statements, Risk Assessements etc for the approval of the client and the clients health and safety advisors, prior to any works commencing on site; |  | item
0.1.8 | The Health & Safety Plans are to provide full details of how the Contractor is to manage Health & Safety risks on site, taking into account the Preliminaries section A34; |  | item
0.1.10 | Security/Access Emergency Access/Escape through the Fire Exits, adjacent rooms including staircases and external pathways/roads etc must be maintained at all times for emergency use by members of staff / building users etc during the course of the works. Where the route is changed the diversion must be adequately signed. Method statements will be required showing how this access will be maintained and managed. Works that affect the client's normal operation of the building should be undertaken out of hours; |  | item
0.1.11 | The contractor must allow for protecting all work areas around the perimeter of the building where staff, pedestrians, vehicles etc have access to and shall include barriers, warning signs etc. Alternative suitably signed and protected pedestrian walkways are to be provided by the contractor where works interrupt existing pedestrian routes for the duration of the works; |  | item
0.1.12 | In conjunction with the items mentioned above the Contractor must provide suitable protection for the delivery route used by Trust staff. This is to include suitable framing and timber plywood sheets to form protected corridor to comply with infection prevention guidelines. All costs associated with this element are to be identified here and must include for protecting staff from debris, materials, tools etc falling from above; |  | item
0.1.13 | The Contractor is to ensure that the site is left secure and safe at all times, and must not be left open, particularly at the end of the working day or over weekends. All ladders and access routes to scaffold shall be removed or secured to prevent unauthorised access being gained to scaffold and subsequently through ward windows; |  | item
0.1.14 | Allow for all temporary screening to the works to protect the adjacent areas of the building from dust and other nuisances; |  | item
0.1.15 | The Contractor is to leave no tools or materials unattended on site at any time; |  | item
0.1.16 | The client shall accept no liability with regards to the above; |  | item
0.1.17 | General A photographic schedule of condition should be prepared by the contractor recording specific defects in the area subject to the works, and the approved contractor access routes, particularly of the corridor floors, walls etc adjacent to the works. The full extent of this is to be agreed with the CA prior to starting works on site; |  | item
0.1.18 | Clean away all rubbish and surplus materials regularly as necessary or as directed by the Contract Administrator. Scrub or clean all floors, metalwork, fittings, etc, eradicate all stains and splashes and leave every part of the Works included in the Contract in a sound and satisfactory condition, free from all defects at completion to the entire satisfaction of the Contract Administrator. Lockable Skips are required; |  | item
0.1.19 | The contractor must allow for locating, identifying, marking and protecting all services, cables, ducts, conduits, pipes, drains etc that may be within the work areas and provide the contract administrator with a suitably marked up plan identifying the same along with method statements on how this will be managed; |  | item
0.1.20 | The adjacent areas of the hospital will remain occupied and in use throughout the period of the works. The building services and supplies to the hospital shall be maintained throughout the duration of the works. Any interruption to the hospital shall be with prior agreement and shall be for the minimum period possible. All preparation work shall be complete prior to interruption of the supply. A detailed method statement shall be approved prior to any works being carried out on the existing hospital services. No services shall be isolated without prior agreement; |  | item
0.1.21 | All personnel employed by the contractor will comply with York Hospitals Estates Department Policy on the Control of Contractors and all other relevant standards adopted by York Teaching Hospitals NHS Foundation Trust [see Appendix for list of documents which can be made available upon request]; |  | item
0.1.22 | The Contractor shall identify here all the costs associated with the hire, delivery, emptying etc of waste skips which are to be lockable units and sited in position to be agreed with Trust prior to works starting on site; |  | item
0.1.23 | Drawings/Specification & Dimensions All dimensions provided in the descriptions and drawings are approximate and the Contractor, his sub contractors and suppliers shall examine the existing site , to ascertain the full extent of the works and take all necessary dimensions before preparing the tender. The Contractor shall insert quantities within the schedule of works; |  | item
0.1.24 | The Contract drawings are to be read as a whole. Any areas of works shown or described on the drawings but omitted from the specification, and vice versa are to be included by the Contractor in his Tender; |  | item
0.1.25 | It is the Contractors responsibility to check that the tender documentation correlates with the contents list and inform the CA if there are any discrepancies or missing documentation, so that this can be rectified immediately; |  | item
0.1.26 | Where reference is made to British Standards and the British Standards Code of Practice, the latest version will apply. Where no particular standards are available, the materials shall be the best of their respective kinds and to the approval of the CA; |  | item
0.1.27 | Any Contractor Design element of the works is to be provided for the Trust to comment on prior to works being carried out on site. This is not client design and does not absolve the contractor or specialist sub contractor from their design obligations and responsibilities; |  | item
| Total carried forward to Section 3 summary sheet |  |  |  | 0

## SOW-GENERAL
CANCER INFORMATION SERVICE
Please insert individual figures and amounts in to the Qty, Unit, Rate and Amount columns
Item | Description | Qty | Unit | Rate | Amount
1 | DEMOLITION & STRIP OUT WORKS
1.1 | Asbestos
1.1.1 | The contractor is to be provided with a copy of the pre-refurbishment and demolition asbestos report prior to commencement of works. The contractor is to allow a Provisional Sum for the removal of any artex/ textured finishes which may potentially contain asbestos based materials. Allow for safe removal and disposal. Provisional Sum £500.00 | 1 | prov sum | 500 | 500
1.2 | Demolition & Alteration (including all associated disposal costs)
1.2.1 | The contractor shall allow for carefully taking up existing floor finishes including any vinyl concealed by carpets, coved skirtings etc. Include for the removal of residual adhesive and clear debris from site. |  | m2
1.2.2 | Carefully take down and remove the existing internal walls in locations indicated on plan. The contractor is to include for the provision and installation of any temporary support as necessary prior to the removal of the walls. |  | item
1.2.3 | Where applicable, all existing surface mounted outlets/ sockets/ switches, power and data etc. to be carefully removed where affected by the proposed works. Existing cabling to be removed where no longer required or re-routed to suit new room layouts, all to contractors details and specification. All surfaces to be made good to accept decoration. |  | item
1.2.4 | Allow for constructing temporary hoardings in positions as necessary to segregate work area from staff areas, comprising stud partion with pre finish [wipeable surfaces] and sealed around all edges, sides, doors etc. Access door to be provided in location from main corridor side of room. |  | item
1.2.5 | Remove existing doors and frames as indicated on plan and dispose of off site. |  | item
1.2.6 | Carefully remove all loose furniture, fittings and equipment and store as necessary throughout the duration of the works. |  | item
1.2.7 | Carefully remove the existing glazed high level internal partition windows and dispose of. Allow for infilling the openings within the partitions. Include for any making good and preparation of adjacent surfaces. |  | item
1.2.8 | Carefully take down existing suspended ceiling tiles, grid, shadow battens and clear debris from site. |  | m2
| Total carried forward to Section 3 summary sheet |  |  |  | 0
2 | INTERNAL DOORS
2.1 | Door Leading from Corridor into Cancer Information Service room
2.1.1 | Supply and install new FD30S 44mm thick 'beech' veneer solid core timber door and frame including all ironmongery into opening. Also include for the supply and installation of the following; - 1½ Pairs of Butt Hinges BS EN 1935. lever handles, kick plates to corridor side of door, euro profile lock. - Combined intumescent heat, smoke and acoustic seals; 'Lorient LP1504DS' or similar approved 15 x 4mm combined seals rebated into door frame. - Door closer to comply with BS 8300, door closers must not require an opening force greater than 30N along the leading edge to operate in accordance with Approved Doc. M; - Ironmongery to be from 'Laidlaw Orbis' range, Laidlaw Ltd, Unit 1 Halifax Court, Halifax Road, Dunston, Gateshead, Tyne & Wear NE11 9JT. Tel. 0191 461 4100; - Signage "Fire Door Keep Shut" fixed to both sides of the door - Fire Resistance ID disk fitted both sides of door; - Vision panel in 'Pilkingtons' Pyroguard Safety Glass with 15x20mm HW timber glazing beads, including intumescent tape to perimeter of glazing. |  | item
2.1.2 | Door Leading into Cancer Information Office - Supply and install new FD30S 44mm thick 'beech' veneer solid core timber door and frame including all ironmongery into existing openings. Also include for the supply and installation of the following; - 1½ Pairs of Butt Hinges BS EN 1935. lever handles, kick plates to information area side of door, keypad to office. - Combined intumescent heat, smoke and acoustic seals; 'Lorient LP1504DS' or similar approved 15 x 4mm combined seals. - Door closer to comply with BS 8300, door closers must not require an opening force greater than 30N along the leading edge to operate in accordance with Approved Doc. M; - Ironmongery to be from 'Laidlaw Orbis' range, Laidlaw Ltd, Unit 1 Halifax Court, Halifax Road, Dunston, Gateshead, Tyne & Wear NE11 9JT. Tel. 0191 461 4100; - Signage "Fire Door Keep Shut" fixed to both sides of the door - Fire Resistance ID disk fitted both sides of door; - Vision panel in 'Pilkingtons' Pyroguard Safety Glass with 15x20mm HW timber glazing beads, including intumescent tape to perimeter of glazing. |  | item
2.1.3 | Adjacent Office (PAL Service) - carefully remove the existing door and frame and cart away. Set aside existing ironmongery where possible. Widen doorway as indicated on drawing no. 50069.199-01 to accept new door and frame. |  | item
2.1.4 | Supply and install new leaf and half door and frame to suit new widened opening. Doors to be Supply and install new FD30S 44mm thick 'beech' veneer solid core timber door and frame including all ironmongery into existing openings. Also include for the supply and installation of the following; Existing ironmongery to be re-used where possible. - 1½ Pairs of Butt Hinges to each door to BS EN 1935. lever handles, kick plates. - Combined intumescent heat, smoke and acoustic seals; 'Lorient LP1504DS' or similar approved 15 x 4mm combined seals rebated into door frame. - Door closer to comply with BS 8300, door closers must not require an opening force greater than 30N along the leading edge to operate in accordance with Approved Doc. M; - Ironmongery to be from 'Laidlaw Orbis' range, Laidlaw Ltd, Unit 1 Halifax Court, Halifax Road, Dunston, Gateshead, Tyne & Wear NE11 9JT. Tel. 0191 461 4100. - Signage "Fire Door Keep Shut" fixed to both sides of the door - Fire Resistance ID disk fitted both sides of door; |  | item
| Total carried forward to Section 3 summary sheet |  |  |  | 0
3.0 | FLOORING
3.1 | Flooring - Office & Information Service Area
3.1.1 | Supply and lay latex self-levelling screed if required to the existing floor in accordance with manufacturer's installation instructions as required to provide a suitable surface on to which to install new floor coverings. |  | m2
3.1.2 | Supply and install new carpet floor covering, to be 'Gradus Bodega' laid on suitable adhesive. All colours to be agreed with client. Gradus Ltd, Park Green, Macclesfield, Cheshire, SK11 7LZ. Tel. 01625 428 922. www.gradusworld.com |  | m2
| Total carried forward to Section 3 summary sheet |  |  |  | 0
4.0 | CEILINGS
4.1 | Allow for installing 50 x 25mm timber shadow battens to perimeter of rooms where suspended ceiling is to be fitted. |  | nr
4.2 | Supply and install new suspended ceiling to areas shown. To be 'Rockfon Medicare Standard' tiles with exposed 24 grid system. Modular size 600mm x 600mm. New ceiling to be installed at height of 2400mm above finished floor level. Rockfon, 26-28 Hammersmith Grove, Hammersmith, London W6 7HA. Tel. 0208 222 7457. www.rockfon.co.uk |  | m2
4.3 | Suspension system to include for all hangers, fixings, main runners, cross members, primary channels, perimeter trims, splines, noggings, clips, bracing, bridging etc. |  | nr
| Total carried forward to Section 3 summary sheet |  |  |  | 0
5.0 | DECORATIONS
5.1 | Prepare all surfaces intended for decoration in accordance with the paint manufacturer's instructions. Infill fixing holes and undertake minor plaster repairs. Clean and prime surfaces. Contractor to include for preparation, application of bonding agent and plaster skim finish to the display wall if required prior to decorating. |  | m2
5.2 | Painted surfaces to existing joinery (doors, door frames, architraves, shadow battens, skirtings and the like) to be prepared and sanded to provide smooth and sound surface, filling any holes with a proprietary filler, prepare to BS800 followed by applying primer, 1 full coat Johnstones Professional undercoat, 2 full coats Johnstones Professional gloss trade paints or similar or equal approved; colour to be confirmed. |  | m2
5.3 | Prepare wall surfaces, and ceiling surfaces where applicable. Prepare and rub down surfaces, abrade to provide smooth sound surface, filling any holes with a proprietary filler, prepare to BS800 followed by applying 2 full coats of Johnstones Acrylic Eggshell trade paint, similar or equal approved. Colours to be confirmed. |  | m2
| Total carried forward to Section 3 summary sheet |  |  |  | 0
6.0 | PARTITIONS
6.1 | Include for extending the existing partition walls up to the underside of the structural soffit using 'Knauf' or similar approved metal studs with layer of 12.5mm wallboard to either side and acoustic insulation slabs between studs. |  | m2
6.2 | Supply and install new partitions and glazed partitions in locations indicated on drawing no. 50069.199-01. Partitions to be 'Komfort 600' range complete with integral blinds to glazed partitions. Partitions to provide acoustic rating of 50 db Rw and minimum fire rating of 30 minutes. |  | m2
7.0 | DISPLAY RACKING
7.1 | Contractor to include for the fixing of 5no. Beech leaflet racking system. To be supplied by client and installed by contractor (Group 2 item). |  | item
7.2 | Contractor to include for the supply and installation of new signage above the entrance screen to the information area. Design and wording of the signage to be agreed prior to ordering. |  | item
8.0 | MECHANICAL & ELECTRICAL WORKS
8.1 | The contractor is to include cost for the design and installation of the following mechanical and electrical items. Refer to mechanical and electrical schedules. |  | item
9.0 | GENERAL
9.1 | Allow a contingency sum of £1,000.00 for unforseen works to be expended or deducted at the discretion of the Contract Administrator. | 1 | prov sum | 1000 | 1000
| Total carried forward to Section 3 summary sheet |  |  |  | 0

## SOW-ELEC
CANCER INFORMATION SERVICE
Please insert individual figures and amounts in to the Qty, Unit, Rate and Amount columns
BCIS reference | Item | Description | Qty | Unit | Rate | Amount
| E-1.0 | ELECTRICAL SERVICES - Introduction
| E-1.1 | For pricing purposes for sections below include all works necessary to achieve installation. The contractor is to include cost for the design and installation of the following electrical items. The contractor is to submit design to the Contract Administrator for approval prior to commencement of works. |  | item
General
| E-1.2 | Electrical Contractor to co-ordinate installation of services with main building contractor and furniture installer.
| E-1.3 | Electrical installation to comply with current edition of BS7671.
| E-1.4 | Electrical installation to comply with current Building Regulations.
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0
| E-2.0 | DEMOLITION & STRIP OUT WORKS [Electrical]
| E-2.1 | The Contractor is to allow for the following works;
| E-2.2 | Lighting
| E-2.2.1 | Isolate lighting circuit at distribution board. Remove existing light fittings and clear from site, retain associated wiring back to the distribution board for future use if compliant with current legislation; |  | item
| E-2.3 | Fire Alarm
| E-2.3.1 | Isolate, remove and retain existing smoke detectors and existing wiring. Include here for the re-fixing of the existing smoke detector on completion of the suspended ceiling installation, including associated plywood pattresses as required above ceiling tiles. |  | item
| E-2.3.2 | Include for all reprogramming and commissioning of detectors as required in accordance with Trust requirements. |  | item
| E-2.3.3 | Retain break glass call points in existing position. |  | item
| E-2.4 | Power
| E-2.4.0 | Isolate, disconnect and remove all small power within the rooms identified as redundant including associated wiring; make good structure (comprising localised patch repairs) and finishes disturbed and prepare for redecoration; |  | item
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0
| E-3.0 | OFFICE & INFORMATION AREA ALTERATIONS
| E-3.1 | The Contractor is to allow for the following works;
| E-3.2 | Allow for the installation of power and data sockets to new location to include all wiring, containment, conduit etc to suit new layout. Final positions to be agreed with the Project Manager prior to installation. To be installed in accordance with IEEE Wiring Regulations - Seventeenth Edition. |  | item
| E-3.3 | Small power. Allow for 13A white twin switched double socket outlet (3No.) to each workstation within office areas. Allow for 1no. single designated cleaners socket outlet. |  | No.
| E-3.4 | Data. Allow for provision of new double RJ45 CAT 5E data outlet for each workstation. |  | No.
| E-3.5 | Electrical containment. Include for the provision of 200mm 3 compartment white pvc dado trunking where required. |  | item
| E-3.6 | Allow for earth bonding all metal surfaces, pipe work etc in line with current legislation. |  | item
| E-3.7 | Safely disconnect and remove existing power point and light switch covers only in the areas indicated. Make safe. Retain all cabling for connection of new fittings. |  | item
| E-3.8 | Coffee Vending Machine - the existing coffee machine is to be disconnected and relocated by others. Contractor to include for carrying out adjustments to the pipework and electrical power outlets to suit new location prior to re-connection by others. |  | item
| E-3.5.1 | Emergency Lighting
| E-3.5.1 | Include for the supply, installation and commissioning of emergency light fittings as necessary to the newly formed office area. |  | No.
| E-3.6 E-3.6.1 | Lighting Design, supply and install new recessed light fittings into new suspended ceiling grid. To be semi-recessed 600 x 600 luminaire complete with frequency control gear. |  | item
| E-3.6.2 | Lighting to comply with current CIBSE Guidelines.
| E-3.6.3 | Include for adjusting all lighting circuits affected by works. |  | item
| E-3.6.4 | On completion of all systems the contractor shall carry out the full testing and commissioning of every installation. Each system shall be tested in full compliance with the relevant standard. |  | item
| E-3.7 | Fire Alarm
| E-3.7.1 | Carry out upgrade to fire alarm system to include for smoke detectors to inner office and high risk areas, break glass call points to final exit positions. Include for linking the existing door access controls to the fire alarm system to enable the doors to be released upon activation of the fire alarm. All fire alarm works are to be undertaken in accordance with BS5839 and to meet current building regulation requirements. |  | item
| E-3.7.2 | Allow for all testing and commissioning upon completion. |  | item
| E-3.7.3 | The existing fire alarm system is to be retained throughout and to remain operational throughout the duration of the works. |  | item
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0
| E-4.0 | GENERAL - ELECTRICAL
| E-4.1 | Other Work In Connection with Services
| E-4.1.1 | Include here additional costs associated with the liaison with Estates to comply with the electrical Permit to work system employed by the Trust. |  | item
| E-4.1.2 | Allow for adjusting existing fire alarm installation to take account of changes to room layout including provision of additional detectors as required, all commissioning, testing and certification. |  | item
| E-4.2 | Builder's Work In Connection with Services |  | item
| E-4.2.1 | Include for any Builders Work in Connection with the electrical installations e.g. forming openings, access points, making good wall etc. |  | item
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0

## SOW-MECH
CANCER INFORMATION SERVICE
Please insert individual figures and amounts in to the Qty, Unit, Rate and Amount columns
BCIS ref | Item | Description | Qty | Unit | Rate | Amount
| M-1.0 | MECHANICAL SERVICES - Introduction
| M-1.1 | For pricing purposes for sections below include all works necessary to achieve installation. The contractor is to include cost for the design and installation of the following mechanical items. The contractor is to submit design to the Contract Administrator for approval prior to commencement of works. |  | item
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0
| M-2.0 | DEMOLITION & STRIP OUT WORKS [Mechanical]
| M-2.1 | Allow for stripping out and removing back to source all services that are not to be retained for future use following removal of items mentioned above. |  | item |  | 0
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0
| M-3.0 | OFFICE & INFORMATION CENTRE ALTERATIONS
| M-3.1.1 | Heating Modifications – carry out modifications and reconfiguration to the existing heating system as necessary to meet the required temperatures. All to meet the requirements of current CIBSE guidance. |  | item |  | 0
| M-3.1.2 | Ventilation Modifications - carry out modifications and reconfiguration to the existing ventilation system as necessary to meet the required temperatures. All to meet the requirements of current CIBSE guidance. |  |  |  | 0
| M-3.2 M3.2.1 | Coffee Vending Machine - the existing coffee machine is to be disconnected and relocated by others. Contractor to include for carrying out adjustments to the pipework and electrical power outlets to suit new location prior to re-connection by others. |  | item |  | 0
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0
| M-5.0 | GENERAL - MECHANICAL
| M-5.1 | Builder's Work In Connection with Services
| M-5.1.1 | Include for any Builders Work in Connection with the mechanical installations e.g. forming openings, access points, making good wall etc. |  | item
|  | Total carried forward to Section 3 summary sheet |  |  |  | 0

## Section 3 Summary
CANCER INFORMATION SERVICE
SECTION 4
COLLECTION
|  | Description | Qty | Unit | Rate | Amount
Schedule of Works Summary/Collection Page
BUILDING SCHEDULE OF WORKS
0.0 | THE WORKS | THE WORKS
0.1 |  | MANAGEMENT
1 | DEMOLITION & STRIP OUT WORKS | DEMOLITION & STRIP OUT WORKS
2 |  | INTERNAL DOORS
3.0 |  | FLOORING
4.0 |  | CEILINGS
5.0 |  | DECORATIONS
6.0 |  | PARTITIONS
7.0 |  | DISPLAY RACKING
8.0 |  | MECHANICAL & ELECTRICAL WORKS
9.0 |  | GENERAL
ELECTRICAL SCHEDULE OF WORKS
E-1.0 |  | ELECTRICAL SERVICES - Introduction
E-2.0 |  | DEMOLITION & STRIP OUT WORKS [Electrical]
E-3.0 |  | OFFICE & INFORMATION AREA ALTERATIONS
E-4.0 |  | GENERAL - ELECTRICAL
MECHANICAL SCHEDULE OF WORKS
M-1.0 | #REF! | MECHANICAL SERVICES - Introduction
M-2.0 | #REF! | DEMOLITION & STRIP OUT WORKS [Mechanical]
M-3.0 |  | OFFICE & INFORMATION CENTRE ALTERATIONS
#REF! |  | #REF!
M-5.0 |  | GENERAL - MECHANICAL
|  |  |  | TOTAL CARRIED TO GENERAL SUMMARY | £

## Sect 4 - Gen Sum
CANCER INFORMATION SERVICE
SECTION FOUR
`
GENERAL SUMMARY
* Delete as applicable, if uncontrolled state reason

## Sect 4 - GENERAL SUMMARY
CANCER INFORMATION SERVICE
SECTION FOUR
GENERAL SUMMARY
Item | Description | Qty | Unit | Rate | Amount
Section One - Preliminaries
Section Two - Preambles
Section Three - Schedule of Works
|  |  | TOTAL CARRIED TO TENDER RETURN FORM | £

## Sect 5 - FORM OF TENDER
CANCER INFORMATION SERVICE
SECTION FIVE
`
FORM OF TENDER
* Delete as applicable, if uncontrolled state reason

## APPENDIX A
CANCER INFORMATION SERVICE
`
APPENDIX A | APPENDIX A
Drawing Issue Sheet [Sweett]
* Delete as applicable, if uncontrolled state reason

## APPENDIX B
CANCER INFORMATION SERVICE
`
APPENDIX B | APPENDIX A
Trust Guidelines for Contractors Working for the York Hospitals NHS Trust
Asbestos policy
Codes of Practice for Contractors
Contract award criteria
Fire Prevention
Maintaining confidentiality
Parking
Procedures for the Control of contractors
Race Equality Scheme
Working on electrical installations
For signature

## APPENDIX C
CANCER INFORMATION SERVICE
`
APPENDIX C | APPENDIX A
Routine Maintenance of Artex ceilings and fixed equipment
Routine maintenance of artex ceilings and fixed eqipment
Some artex ceilings contain minimal amounts of white asbestos (chrysotile) and in general this is very difficult to detect as there is no uniform distribution of the material throughout the coating.
Good housekeeping methods will deal with minor disturbances of the coating to enable routine maintenance work to take place safely without causing alarm to people who may not be able to leave the area.
Follow these simple rules and keep everyone safe, primarily yourself
1. Do wear a face mask and disposable overalls when cleaning, removing fixtures or drilling a single hole in a ceiling, this will also protect against other contaminants like aspergillus 2. Do use a plastic dust sheet to protect the floor area and collect any spoil that may fall. 3. Do cut round any fitting which has adhered to the ceiling with a sharp blade to reduce uneven breakage of the coating 4. Do capture any dust directly into a container whenever possible, when drilling a single hole the hole should be marked and smeared with Vaseline or similar prior to drilling this will prevent the surface coating from becoming airborne, surplus material should be wiped clean with a damp cloth 5. Do fill any screw holes or damaged surfaces with filler or paint. 6. Do clean any tools or equipment with a damp cloth after use to remove any dust particles. 7. Do clean all surfaces using damp wipes, do not brush any dust as this may make it airborne 8. Contaminated clothing, (overalls and mask) cleaning materials and dustsheet must be placed into a clear plastic bag and sealed at the neck and brought back to the Boilerhouse where it will be placed into a red bag labelled Asbestos then placed into the asbestos skip for disposal as contaminated waste. 9. Wash your hands thoroughly
This working practice should typically be used when washing or painting a ceiling, replacing a curtain track into existing screw holes, replacing light fittings or fire alarm detectors, replacing or working above suspended ceilings or work of a similar nature that creates minimum disturbance of the textured coating
Any work that requires a greater disturbance of the surface coating will only be carried out to a written Method Statement under the Permit to Work system
Remember all airborne dust particles are a source of infection to any patient particularly those with a respiratory condition. Suspended ceiling tiles should be replaced as soon as possible and not left open overnight for any reason whatsoever.
Masks should be PP3 standard, overalls will be blue hooded with elastic cuffs and ankles suitable for asbestos stripping, clear plastic bags will be heavy duty rubble sacks, all are available from the stores