Core

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-03: Central Operator Station | giles.digby@stfc.ac.uk

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-03: Central Operator Station | giles.digby@stfc.ac.uk

06-03 Central Operator Station

Date: 05 Sep 2017

Version: 3

Unit of Measure: Nr

| Summary |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frequencies |  |  | Tasks |  |
| 1M (Month) 30 mins |  |  | 1 2 3 4 5 6 |  |
| 6M (Months) 5 mins |  |  | 7 |  |
| 12M (Months) 120 mins |  |  | 8 |  |
| Annual Timing |  |  | 490 mins |  |
| Introduction |  |  |  |  |
| The technologies used in building management systems have changed significantly resulting in a wide range of maintenance tools. Systems that use data communications networks may enable remote monitoring and diagnostics, thus reducing the number of site visits required. Systems that are automated or remotely managed may also reduce maintenance and energy costs. BMS hardware itself has also evolved such that maintenance for a modern central operator station is less intensive than for older systems. The maintenance regime for a particular BMS should therefore be defined by the type of hardware and software employed, the specialist tools available and the scope of the installation. The risk profile of the organisation and the nature of its building services must also be assessed to ensure that safety related systems are appropriately maintained. The service timings in this schedule are provided for guidance only. Timings may vary, depending on the system installed and the level of remote management available from the maintenance service provider. Please refer to the overarching introduction (SFG 00-01) to make sure you are of the correct skill level as indicated within the task schedule to carry out the described works. Ensure you have read and understood the manufacturer’s recommendations, carried out risk assessment(s) on each item of plant to identify the correct frequency of maintenance, identified all safety procedures that need to be applied and recorded in order to carry out the work in a safe and reliable manner. |  |  |  |  |
| Display Order | Tasks |  |  |
| 1 | Software backup Criticality: Action: | Amber Frequency: 1M Skill Set: Controls Engineer Perform a software backup of the central operator station. Install the software temporarily on a different server to verify the backup was successful. Ensure the location of stored backup meets IT policy. If an external drive is used, ensure this is scanned for viruses before use. Software backup should be performed monthly, or after any significant system changes. The frequency of software backup should be periodically assessed to ensure it is appropriate for the risk profile of the organisation. |  |
|  | Notes: | Remote software backup may be available for some building management systems. Any personnel perfoming software backup must operate within the guidelines of the site's IT policy. For example, some sites specify that backups should be kept on an encrypted drive. |  |

| 2 | Software upgrades Criticality: Amber Frequency: 1M Skill Set: Controls Engineer Action: Perform any necessary software upgrades including: - Service pack installation. - BMS software upgrades. Notes: Certain upgrades may incur downtime for the plant. All upgrades should be risk-assessed and confirmed with the Client. |  |
| --- | --- | --- |
| 3 | Anti-virus software Criticality: Amber Frequency: 1M Skill Set: Controls Engineer Action: Check that the anti-virus software is up to date. Install new versions as necessary. Notes: This may be an automated or remotely managed operation. If the BMS operates across an organisation's existing data network then the organisation's Information Technology department is responsible for updating anti-virus software. |  |
| 4 | Cyber security Criticality: Action: | Amber Frequency: 1M Skill Set: Controls Engineer Check for any unauthorised devices installed on the network. Check for any unauthorised software on servers or workstations that may be in breach of IT security policy. Prove the validity of any software updates that have been installed, and issue notice accordingly. Perform appropriate hardening of the system by removing unnecessary accounts or services, applying patches, closing any unused ports on network switches etc. If any malware defence is installed, ensure this is being managed and updated. Check any firewall, router and switch settings on BMS-specfic equipment, to ensure that only the required ports are open. Perform port scans on a periodic basis. |
|  | Notes: | Many building management systems operate across an existing network which is managed according to the organisation's own IT policy. However, in some cases it may be prudent for the controls engineer to check for any devices on the system that should not be there. On an existing network, some elements of system hardening would be done by the organisation's own IT department. |
| 5 | Password management Criticality: Amber Frequency: 1M Skill Set: Controls Engineer Action: Check that default passwords have been changed to site-specific passwords. Check that passwords have been periodically changed if this is specified by site policy. Ensure that no default passwords are used. Ensure that all passwords meet the organisation's network security policy. |  |

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-03: Central Operator Station | giles.digby@stfc.ac.uk

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-03: Central Operator Station | giles.digby@stfc.ac.uk

| continued5 | Notes: |  |
| --- | --- | --- |
| 6 | Data network health Criticality: Amber Frequency: 1M Skill Set: Controls Engineer Action: Ensure that any standalone BMS data network is secure and is functioning correctly. Notes: Some building management systems operate across an organisation's existing data network. In such cases the organisation's IT department is responsible for monitoring and maintaining the network. |  |
| 7 | Time and date settings Criticality: Amber Frequency: 6M Skill Set: Controls Engineer Action: Check the real-time clock and date settings and adjust as necessary. Notes: This may be an automated or remotely managed operation. |  |
| 8 | System hardware Criticality: Action: | Amber Frequency: 12M Skill Set: Controls Engineer Visually inspect the central operator station for degradation, wear and tear or damage. Check the temperature and humidity of the environment to ensure optimum conditions for operation. Check all cooling fans to ensure they are working and clear any fluff from inlet grilles. Perform electrical checks to establish the operational state of the equipment. Check that all control and safety interlocks are operating correctly. Ensure setpoints and space conditions are maintained as economically as possible. Check that alarm reporting procedures and systems are operating correctly. Ensure that any emergency power backup systems are operational and will maintain the BMS during power failure. Recommend any action necessary to optimise or improve system performance and reliability. Provide a detailed report of the service visit, listing all findings and control parameter settings. |
|  | Notes: | These checks should be done as part of a planned preventive maintenance visit. |

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-03: Central Operator Station | giles.digby@stfc.ac.uk

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-03: Central Operator Station | giles.digby@stfc.ac.uk