Core

06-05 Outstations

Date: 05 Sep 2017

Version: 3

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-05: Outstations | giles.digby@stfc.ac.uk

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-05: Outstations | giles.digby@stfc.ac.uk

Unit of Measure: Nr

| Summary |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Frequencies |  |  | Tasks |  |  |  |
| 12M (Months) 240 mins |  |  | 1 2 3 4 5 6 7 8 9 |  |  |  |
| Annual Timing |  |  | 240 mins |  |  |  |
| Introduction |  |  |  |  |  |  |
| The technologies used in building management systems have changed significantly resulting in a wide range of maintenance tools. Systems that use data communications networks may enable remote monitoring and diagnostics, thus reducing the number of site visits required. Systems that are automated or remotely managed may also reduce maintenance and energy costs. BMS hardware itself has also evolved such that maintenance for a modern outstation may be less intensive than for older systems. The maintenance regime for a particular BMS should therefore be defined by the type of hardware and software employed, the specialist tools available and the scope of the installation. The risk profile of the organisation and the nature of its building services must also be assessed to ensure that safety related systems are appropriately maintained. The service timings in this schedule are provided for guidance only. Timings may vary, depending on the system installed and the level of remote management available from the maintenance service provider. Please refer to the overarching introduction (SFG 00-01) to make sure you are of the correct skill level as indicated within the task schedule to carry out the described works. Ensure you have read and understood the manufacturer’s recommendations, carried out risk assessment(s) on each item of plant to identify the correct frequency of maintenance, identified all safety procedures that need to be applied and recorded in order to carry out the work in a safe and reliable manner. |  |  |  |  |  |  |
| Display Order | Tasks |  |  |  |
| 1 | Outstation hardware Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Visually inspect the mechanical condition of all outstation enclosures and fixings. Check that cable glands and door seals are in good condition to prevent the ingress of moisture. Check that environmental conditions such as temperature and humidity are within the manufacturer's recommended limits. Notes: |  |  |  |
| 2 | Outstation firmware Criticality: Amber Frequency: 12M Action: Check that the outstation firmware is the current version. Upgrade to the latest version if necessary. Notes: |  | Skill Set: | Controls Engineer |
| 3 | Cable connectors Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Visually inspect all cable connectors and incoming cables for security, integrity and damage. Notes: |  |  |  |

© 2020 BESA All rights reserved	Page 1 of 2

| 4 | Automatic restart Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Safely isolate the outstation/controller to check that the outstation automatically restarts and re-boots the software. Check the voltage on all power supplies. Notes: |  |  |
| --- | --- | --- | --- |
| 5 | Backup power Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Check that the standby batteries or uninterruptible power supply (UPS) comply with the manufacturer's specification. Replace standby batteries as necessary. Interrupt the electrical supply to each outstation, reinstate backup power and ensure system restarts satisfactorily. Notes: |  |  |
| 6 | Hardwired safety interlocks Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Confirm that all hardwired safety interlocks to field equipment are operating correctly by checking that the devices operate as designed. Notes: Hardwired safety interlocks are used for equipment such as pressurisation units, emergency plantroom safety circuits and flue fans. If a hardwired safety interlock operates, fault status is monitored by the BMS and a high-level alarm is raised. |  |  |
| 7 | Analogue inputs Criticality: Amber Frequency: 12M Action: Read and check calibration of analogue inputs. Check the calibration of any control sensors. Notes: | Skill Set: | Controls Engineer |
| 8 | Analogue outputs Criticality: Amber Frequency: 12M Action: Check for accuracy of output signal. Notes: | Skill Set: | Controls Engineer |
| 9 | Outstation override Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Visually inspect the panel settings to ensure the outstation controls are set to Automatic, not Hand or Manual. Check the software settings to ensure the outstation Automatic setting has not been overridden. Notes: Review and report to client if any controls have been overridden. |  |  |

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-05: Outstations | giles.digby@stfc.ac.uk

Uncontrolled Copy - Printed: 31/03/2020 | Science & Technology Facilities Council | 06-05: Outstations | giles.digby@stfc.ac.uk

© 2020 BESA All rights reserved	Page 2 of 2