Core

Uncontrolled Copy - Printed: 30/04/2020 | Science & Technology Facilities Council | 06-06: Software Functions | matthew.kenyon@stfc.ac.uk

Uncontrolled Copy - Printed: 30/04/2020 | Science & Technology Facilities Council | 06-06: Software Functions | matthew.kenyon@stfc.ac.uk

06-06 Software Functions

Date: 05 Sep 2017

Version: 4

Unit of Measure: Nr

| Summary |  |  |  |  |
| --- | --- | --- | --- | --- |
| Frequencies |  |  | Tasks |  |
| 6M (Months) 120 mins |  |  | 1 2 3 |  |
| 12M (Months) 240 mins |  |  | 4 5 6 7 8 9 10 11 12 13 14 15 |  |
| Annual Timing |  |  | 480 mins |  |
| Introduction |  |  |  |  |
| The technologies used in building management systems have changed significantly resulting in a wide range of maintenance tools. Systems that use data communications networks may enable remote monitoring and diagnostics, thus reducing the number of site visits required. Systems that are automated or remotely managed may also reduce maintenance and energy costs. BMS software has evolved such that maintenance may be less intensive than for older systems. The maintenance regime for a particular BMS should therefore be defined by the type of hardware and software employed, the specialist tools available and the scope of the installation. The risk profile of the organisation and the nature of its building services must also be assessed to ensure that safety related systems are appropriately maintained. The service timings in this schedule are provided for guidance only. Timings may vary, depending on the system installed and the level of remote management available from the maintenance service provider. Please refer to the overarching introduction (SFG 00-01) to make sure you are of the correct skill level as indicated within the task schedule to carry out the described works. Ensure you have read and understood the manufacturer’s recommendations, carried out risk assessment(s) on each item of plant to identify the correct frequency of maintenance, identified all safety procedures that need to be applied and recorded in order to carry out the work in a safe and reliable manner. |  |  |  |  |
| Display Order | Tasks |  |  |
| 1 | Control loops Criticality: Action: | Amber Frequency: 6M Skill Set: Controls Engineer Check integrity of the installed software program. Check sequence, operation of control, outputs and stability of plant. Undertake as necessary fine tuning of control loops. Check against design/commissioning figures. Adjust settings in conjunction with the building manager to achieve the required internal environmental conditions. |  |
|  | Notes: | Many modern buildings now have some form of carbon dioxide (CO ) control to ensure that optimum 2 indoor air quality (IAQ) is maintained. This is performed via mechanical or natural ventilation and should be treated as a standard control loop performance check. To maintain the full loop, it is necessary to refer to the relevant SFG20 schedules for sensors, dampers etc. The frequency of control loop checks should be agreed with the Client, and should be related to the critical nature of the operation. |  |

| 2 | Redundant software Criticality: Amber Frequency: 6M Skill Set: Action: Check for redundant software and either remove it or upgrade it as appropriate. Notes: |  |  | Controls Engineer |
| --- | --- | --- | --- | --- |
| 3 | Outstations Criticality: Amber Frequency: 6M Skill Set: Action: Back up all outstation files. Make two copies. Store one on site and one off site. Notes: |  |  | Controls Engineer |
| 4 | Optimised start/stop Criticality: Amber Frequency: 12M Skill Set: Action: Verify operation by interrogating software/hardware copy. Notes: Building layouts and occupational requirements are seldom of a static nature. Th and their suitability need to be reassessed on a regular basis. |  |  | Controls Engineer erefore control strategies |
| 5 | Data logging Criticality: Amber Frequency: 12M Skill Set: Action: Review need for existing data logs. Delete/archive logs as required. Notes: Report to Client on the need to review existing arrangements. |  |  | Controls Engineer |
| 6 | Transaction activity Criticality: Amber Frequency: 12M Skill Set: Action: Check that transaction activity data is being logged and is valid. Notes: Report to Client on the need to review existing arrangements. |  |  | Controls Engineer |
| 7 | Criticality: Action: | Alarm management and report Amber Frequency: 12M Skill Set: Controls Engineer Review frequencies of generated alarms. Review alarm log records for indication of untoward conditions. Check that plant alarms and software interlocks with safety implications are operating correctly. Check alarm priorities, routings and reactions. Check alarm priorities are appropriate. |  |  |
|  | Notes: | The checking of possible reactions to certain critical alarms and programmes must be carefully coordinated with other trades and building tenants. Where there are safety implications, verify alarm integrity. Review system of reporting outstanding alarm conditions and report discrepancies. Report as appropriate to Client. |  |  |
| 8 | Generator loading programme Criticality: Amber Frequency: 12M Action: (If applicable) Check plant startup sequence. Notes: Report as appropriate to Client. |  | Skill Set: Controls Engineer |  |
| 9 | Maximum demand/load shedding Criticality: Amber Frequency: 12M Action: (If applicable) Check sequence and operation. |  | Skill Set: Controls Engineer |  |

Uncontrolled Copy - Printed: 30/04/2020 | Science & Technology Facilities Council | 06-06: Software Functions | matthew.kenyon@stfc.ac.uk

Uncontrolled Copy - Printed: 30/04/2020 | Science & Technology Facilities Council | 06-06: Software Functions | matthew.kenyon@stfc.ac.uk

| continued9 | Notes: Report as appropriate to Client. |  |  |
| --- | --- | --- | --- |
| 10 | Load cycling Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: (If applicable) Check operation and report as appropriate to Client. Notes: Load cycling is a form of energy optimisation incorporated in some building management systems. |  |  |
| 11 | Software interlocks Criticality: Amber Frequency: 12M Action: Verify operation. Notes: Report as appropriate to Client. |  | Skill Set: Controls Engineer |
| 12 | Manual status review Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Check manual overrides and their effect on the system and its operation. Notes: At Client access level, review parameters, lockouts, changes, all points in manual override and forced analogue values. Review findings with Client. |  |  |
| 13 | Operations and maintenance Criticality: Amber Frequency: 12M Skill Set: Controls Engineer Action: Advise where control strategy descriptions in operating and maintenance manuals are incorrect. Ensure, where appropriate, additional documentation meets all quality assurance procedures. Notes: |  |  |
| 14 | Schematics Criticality: Action: Notes: | Amber Frequency: 12M Check schematics indicate correctly. | Skill Set: Controls Engineer |
| 15 | Log books Criticality: Action: | Amber Frequency: 12M Maintain a log book of all changes made to the system. | Skill Set: Controls Engineer |
|  | Notes: | As necessary. |  |

Uncontrolled Copy - Printed: 30/04/2020 | Science & Technology Facilities Council | 06-06: Software Functions | matthew.kenyon@stfc.ac.uk

Uncontrolled Copy - Printed: 30/04/2020 | Science & Technology Facilities Council | 06-06: Software Functions | matthew.kenyon@stfc.ac.uk