## Equipment Register
Tudor Park Academy Trust
Building | Location | Year of Manufacturer | Life Exepcancy | Year to be replaced (Unless serious faults present) | Product Description | Serial Number | F-Gas Information | Serves / TF Notes / Safe Access Notes
Tudor Park Office | LHS of Building on Wall | 2022 | 10 | 2032 | Mitsubishi Heavy Ind. SRC35ZS-W2 Split Condensing Unit HP | 286703767CE | R410A=M2.95+T0.0Kg - Assumed no trim charge needed
Tudor Park Office | First Floor HEP Office | 2021 | 10 | 2031 | Mitsubishi Heavy Ind. SRK35ZS-W Wall Mount FCU | 146738652CF
Tudor Park Office | Rear LHS of Building | 2004 | 15 | 2019 | Mitsubishi Electric PURY-P250YMF-C VRF Condensing Unit HR | 22W07459 (Serial numbers worn away) | R407C=M10.5Kg+T14.0Kg - Trim Charge Estimated | Ground or First Floor Units - LHS Unit not working. Undiagnosed faults. Main and Inverter PCB's obsolete. Many other parts still available.
Tudor Park Office | First Floor Conference Room 1 RHS of divide | 2001 | 15 | 2016 | Mitsubishi Electric PCFY-P100VGM-A Ceiling suspended FCU | Unreadable from photo
Tudor Park Office | First Floor Conference Room 2 | 2001 | 15 | 2016 | Mitsubishi Electric PCFY-P63VGM-A Ceiling suspended FCU | 18H00568
Tudor Park Office | First Floor Server Nearest Door | 2002 | 10 | 2012 | Mitsubishi Electric PCFY-P40VGM-A Ceiling suspended FCU | 29H00355
Tudor Park Office | First Floor By Disabled Toilets | 2001 | 10 | 2011 | Mitsubishi Electric PCFY-P40VGM-A Ceiling suspended FCU | 17H00396
Tudor Park Office | First Floor Kitchen | 2001 | 15 | 2016 | Mitsubishi Electric CMB-P106V-F Branch Controller Box | 31W00828
Tudor Park Office | IT Hardware Office | 2001 | 15 | 2016 | Mitsubishi Electric PCFY-P40VGM-A Ceiling suspended FCU | 3XH00017
Tudor Park Office | Rear LHS of Building | 2004 | 15 | 2019 | Mitsubishi Electric PURY-P250YMF-C VRF Condensing Unit HR | 23W04956 (Serial numbers worn away) | R407C=M10.5Kg+T14.0Kg - Trim Charge Estimated | Ground or First Floor Units
Tudor Park Office | Ground Floor HR Trust & Leadership | 2003 | 15 | 2018 | Mitsubishi Electric PKFY-P50VGM-A Wall Mount FCU | 35000907
Tudor Park Office | Ground Floor Meeting Room | 2003 | 15 | 2018 | Mitsubishi Electric PKFY-P50VGM-A Wall Mount FCU | 34001667 or 34001660 or 34001663 |  | No access as people in meeting room
Tudor Park Office | Ground Floor Office Rear LHS | 2001 | 15 | 2016 | Mitsubishi Electric PCFY-P63VGM-A Ceiling suspended FCU | 14H00155
Tudor Park Office | Ground Floor Office Rear RHS Finance | 2001 | 15 | 2016 | Mitsubishi Electric PCFY-P63VGM-A Ceiling suspended FCU | 14H00165
Tudor Park Office | Ground Floor Reception | 2001 | 15 | 2016 | Mitsubishi Electric PCFY-P125VGM-A Ceiling suspended FCU | 33G00084
Tudor Park Office | Ground Floor Location TBA | 2001 | 15 | 2016 | Mitsubishi Electric CMB-P106V-F Branch Controller Box | TBA |  | Didn’t locate - will be in ceiling somewhere
Tudor Park Office | Rear LHS of Building Above VRF CU | 2016 | 10 | 2026 | Mitsubishi Heavy Ind. SRC25ZD-S1 Split Condensing Unit HP | 640900555 | R410A=M0.90+T0.0Kg - Assumed no trim charge needed
Tudor Park Office | Ground Floor Karens Office | 2016 | 10 | 2026 | Mitsubishi Heavy Ind. SRK25ZD-S Wall Mount FCU | TBA |  | No access locked room. Model number assumed from cond. Info
Tudor Park Office | RHS of Building on Wall 1st unit | 2017 | 10 | 2027 | Mitsubishi Heavy Ind. FDC71VN Split Condensing Unit HP | K71002052AF | R410A=M2.95+T0.0Kg - Assumed no trim charge needed
Tudor Park Office | First Floor Server Furthest From Door | 2022 | 10 | 2032 | Mitsubishi Heavy Ind. FDE71VH Ceiling Suspended FCU | No plate visible |  | Data plate will be under filter covers. Model number assumed from cond. Info
Tudor Park Office | RHS of Building on Wall 2nd Unit | 2018 | 10 | 2028 | Fujitsu AOYG36LMTA Split Condensing Unit HP | T004041 | R410A=M2.10+T0.0Kg - Assumed no trim charge needed
Tudor Park Office | First Floor Server Middle LHS Wall | 2018 | 10 | 2028 | Fujitsu ASYG36LMTA Wall Mount FCU | T003987
Tudor Park Office | RHS of Building on Wall 3rd Unit | 2022 | 10 | 2032 | Mitsubishi Heavy Ind. SRC50ZTL-W Split Condensing Unit HP | 222900095CE | R32=M0.90+T0.0Kg - Assumed no trim charge needed
Tudor Park Office | First Floor Conference Room 1 RHS of divide | 2022 | 10 | 2032 | Mitsubishi Heavy Ind. SRK50ZTL-W Wall Mount FCU | 270500697CF
Tudor Park Office | RHS of Building on Wall 4th Unit | 2022 | 10 | 2032 | Mitsubishi Heavy Ind. SRC50ZTL-W Split Condensing Unit HP | 222900103CE | R32=M0.90+T0.0Kg - Assumed no trim charge needed
Tudor Park Office | First Floor Conference Room 1 LHS of divide | 2022 | 10 | 2032 | Mitsubishi Heavy Ind. SRK50ZTL-W Wall Mount FCU | 270500677CF
Springwood Academy | External Roof area through loft in class room M313. UNSERVEYED | 2007 | 10 | 2017 | Fujitsu AOYS12LDC Split Condensing Unit HP | E008971 | R410A=M1.05+T0.0Kg - Assumed no trim charge needed | Didn’t Locate Unit - Based location on paperwork provided. Age Estimated
Springwood Academy | Headteachers Kitchen | 2007 | 10 | 2017 | Fujitsu ASYA12LCC Wall Mount FCU | E009004 |  | Age Estimated
Springwood Academy | Raised Gardens | 1998 | 10 | 2008 | Daikin R45DBV11B Split Condensing Unit HP | 0905876 | R22=M1.6Kg+T0.0Kg | Units at 3.7M - MiTower For Safe Access
Springwood Academy | Gnd Flr Server Via Library | 1998 | 10 | 2008 | Daikin FTY45GAV1B Wall Mount FCU | 0902788 |  | Refrigerant R22 Banned - System should be replaced - Server Room should have run and standby units
Springwood Academy | Raised Gardens | 2018 | 10 | 2028 | Mitsubishi Heavy Ind. SRC71ZE-S1 Split Condensing Unit HP | TBA | R410A=M1.90+T0.0Kg - Assumed no trim charge needed. Age Estimated. Model Number Estimated. | Units at 3.7M - MiTower For Safe Access
Springwood Academy | Gnd Flr Server Via Library | 2018 | 10 | 2028 | Mitsubishi Heavy Ind. SRK71ZE-S1 Wall Mount FCU | 815403777 RE
Springwood Academy | Raised Gardens | 2008 | 10 | 2018 | Mitsubishi Heavy Ind. SRC71ZE-S1 Split Condensing Unit HP | Unreadable from photo | R410A=M1.90+T0.0Kg - Assumed no trim charge needed. Age Estimated. Model Number Estimated. | Units at 3.7M - MiTower For Safe Access
Springwood Academy | Ground Floor Print Room | 2023 | 10 | 2033 | Mitsubishi Heavy Ind. SRK71ZR-WF Wall Mount FCU | 332001585CF
Springwood Academy | Raised Gardens | 2023 | 10 | 2033 | LG PC18NSQ Split Condensing Unit HP | Unreadable from photo | R32=M0.90+T0.0Kg - Assumed no trim charge needed. Age Estimated | Units at 3.7M - MiTower For Safe Access
Springwood Academy | Incident / Inclusion Room | 2023 | 10 | 2033 | LG PC18SVQWall Mount FCU | Children in room no photo | Age Estimated
Springwood Academy | Sunken Gardens | 2016 | 10 | 2026 | Mitsubishi Heavy Ind. SRC63ZR-S Split Condensing Unit HP | 686501345BE | R410A=M1.55+T0.0Kg - Assumed no trim charge needed. Age Estimated. Model Number Estimated. | Units at 3.7M - MiTower For Safe Access
Springwood Academy | Study Room by Hall Gnd Flr. | 2016 | 10 | 2026 | Mitsubishi Heavy Ind. SRK71ZR-S Wall Mount FCU | 644101706BE
Springwood Academy | Dance Studio Rear of Building | 2004 | 10 | 2014 | Mitsubishi Heavy Ind. FDC100VN Split Condensing Unit HP | K10003016N | R410A=M3.80+T0.0Kg - Assumed no trim charge needed. Age Estimated. Model Number Estimated. | Units at 3.2M to underside of CU - MiTower For Safe AccessAge estimated
Springwood Academy | Dance Studio Ceiling | 2004 | 10 | 2014 | Mitsubishi Heavy Ind. FDTC50V Cassette FCU | A50000026KK |  | 3.3 Metre to cassette. MiTower for safest access. Put protection under wheels to protect studio floor
Springwood Academy | Dance Studio Ceiling | 2004 | 10 | 2014 | Mitsubishi Heavy Ind. FDTC50V Cassette FCU | A50000024KK |  | 3.3 Metre to cassette. MiTower for safest access. Put protection under wheels to protect studio floor
Springwood Academy | Flat Roof | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRC50ZD-S Split Condensing Unit HP | 657700317 RE | R410A=M1.35+T0.0Kg - Assumed no trim charge needed. | Service will probably confirm replacement required
Springwood Academy | Office M209 RHS | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRK50ZD-S Wall Mount FCU | 507604942 RE | Marked Unit 3 | Service will probably confirm replacement required
Springwood Academy | Flat Roof | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRC50ZD-S Split Condensing Unit HP | Worn Away | R410A=M1.35+T0.0Kg - Assumed no trim charge needed. | Service will probably confirm replacement required
Springwood Academy | Office M209 LHS | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRK50ZD-S Wall Mount FCU | 507604431 RE | Marked Unit 4 | Service will probably confirm replacement required
Springwood Academy | Flat Roof | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRC35ZD-S Split Condensing Unit HP | 55761368 RE | R410A=M1.10+T0.0Kg - Assumed no trim charge needed. | Service will probably confirm replacement required
Springwood Academy | Office M209 Rear Back Office | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRK35ZD-S Wall Mount FCU | 507500015 RE | Marked Unit 1 | Service will probably confirm replacement required
Springwood Academy | Flat Roof | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRC25ZD-S Split Condensing Unit HP | 557510530 | MISSING | Removed off of roof? Evidence of cut power cable but not pipework.
Springwood Academy | Office M209 Rear LHS Office | 2005 | 10 | 2015 | Mitsubishi Heavy Ind. SRK25ZD-S Wall Mount FCU | 507400729 RE | Marked Unit 2 | Service will probably confirm replacement required
Springwood Academy | Flat Roof | 2016 | 15 | 2031 | Mitsubishi Heavy Ind. SRC25ZM-S/A Split Condensing Unit HP | 681603446BE | R410A=M0.75+T0.0Kg - Assumed no trim charge needed.
Springwood Academy | 1st Floor Ex Deputy Head / Store Rm. | 2016 | 15 | 2031 | Mitsubishi Heavy Ind. SRK25ZM-S Wall Mount FCU | 639706344BE
Logic | Rear of Bldg overlooking pitches | 2009 | 10 | 2019 | Mitsubishi Heavy Ind. FDC125 Split Condensing Unit HP | K12002329AF | R410A=M3.80+T0.0Kg In need of replacement and re-location of external unit position. | Unsafe access over food truck. Approx. 3.8m. Install protective cage on new unit?
Logic | Computer Room | 2009 | 10 | 2019 | Mitsubishi Heavy Ind. FDEN125V Ceiling Suspended FCU | B12001056KK | Children in room no photo
Logic | Rear of Bldg Wooden Compound | 2016 | 15 | 2031 | Toshiba MMY-MAP1206HT8P-E 2 Pipe VRF Condensing Unit HP | 62800049 | R410A=M11.50+T8.5Kg - Trim charge estimated.
Logic | Canteen | 2016 | 15 | 2031 | Toshiba Ducted FCU | TBA |  | Too many children around for pictures
Logic | Canteen | 2016 | 15 | 2031 | Toshiba Ducted FCU | TBA |  | Too many children around for pictures
Logic | Canteen | 2016 | 15 | 2031 | Toshiba Ducted FCU | TBA |  | Too many children around for pictures
Logic | Classroom 02 | 2016 | 15 | 2031 | Toshiba Ducted FCU | TBA |  | Too many children around for pictures
Logic | Canteen | 2016 | 15 | 2031 | LSA Air Curtain | TBA
Logic | Rear of Bldg Wooden Compound | 2016 | 10 | 2026 | Toshiba RAV-SM804ATP-E Split Condensing Unit HP | 62700238 | R410A=M1.7+T1.0Kg - Trim charge estimated.
Logic | Glass Server Room 1st Unit RHS | 2016 | 10 | 2026 | Toshiba RAV-SM806KRT-E Wall Mount FCU | 30400463
Logic | Rear of Bldg Wooden Compound | 2016 | 10 | 2026 | Toshiba RAV-SM804ATP-E Split Condensing Unit HP | 62700241 | R410A=M1.7+T1.0Kg - Trim charge estimated.
Logic | Glass Server Room 2nd Unit LHS | 2016 | 10 | 2026 | Toshiba RAV-SM806KRT-E Wall Mount FCU | 62700458
Logic | Rear of Bldg Wooden Compound | 2016 | 15 | 2031 | Toshiba RAV-SM1104ATP-E Split Condensing Unit HP | 62800741 | R410A=M1.7+T1.0Kg - Trim charge estimated.
Logic | Classroom 01 | 2016 | 15 | 2031 | Toshiba Ducted FCU