- PURPOSE AND SCOPE

The purpose of this procedure is to identify hazards and isolation points on both mechanical and electrical equipment in order to minimise the risk of injury to personnel. This will ensure that work can be carried out safely, and enable equipment to be restored to normal state upon completion.

The   Lockout/Tagout procedure is a twofold procedure. It ensures that personnel correctly lock out equipment, systems or circuits before conducting maintenance. This also includes life preserving circuits i.e. fire alarms, Co2 alarms, BMS circuits etc. The Tagout will ensure that personnel are notified when equipment, systems or circuits are not in a normal configuration. This work instruction applies to project and maintenance works performed by Capability EMS personnel or contractors under their control.

The Health and Safety at Work Act 1974 places a duty on employers to ensure, as far as is reasonably practicable, a safe system of work is in place. Mandatory permits are an essential component of working in a safe environment. The implementation and correct use of these will ensure that Pirbright Institute is complying with current legislation and ensures that work activities are carried out under a controlled practice, minimising risk to employers.

FAILURE TO FOLLOW THIS LOCKOUT PROCEDURE MAY RESULT IN INJURY TO PERSONNEL OR DAMAGE TO EQUIPMENT.

- REFERENCES

Health and Safety at Work Act 1974.
The Electricity at Work Regulations 1989.

The Safe Isolation of Plant and Equipment HSG 253.

Electricity at Work: Safe working practices HSG85.
Pressure Systems Safety Regulations 2000

- RISK ASSESSMENT

There is a requirement within the Pirbright Institute to produce a Point of Work Risk Assessment (PoWRA) prior to any and all works.

All works performed by EMS personnel requiring a Mandatory Permit require a task specific Risk Assessment to be completed via the Permit to Work (PtW) form Part B & C.

All works performed by contractors require a task specific risk assessment submitted in advance of the works.

Hazard based risk assessments are situated within ‘Oshens’.

If no risk assessments are available, highlight this to your line manager.

- RESPONSIBILITIES

| Senior Capability EMS Leader | Ensures the full implementation of this procedure. Ensures all relevant personnel are trained in the legal requirements of the Health and Safety at Work Act 1974. |
| --- | --- |
| Capability EMS Leader (Engineering & Operations) and Capability EMS Leader (Projects and Process) | Provide Site Operating Procedures (SOP’s), work Instructions and training to ensure all systems are implemented safely and effectively when used. |
| Capability EMS Health, safety & Risk Manager | Owns and maintains the SOP and associated Work Instructions and Forms. |
| Senior Maintenance Owner and Senior Specialist Equipment Owner and Senior BMS Owner | Ensures the system is used correctly on all occasions where there is a mandatory, procedural or Risk Assessment requirement. |
| Competent Person | EMS Personnel or Contractors under EMS control carrying out the works. Must understand the conditions and their responsibilities with regards to all Work Instructions & RAMS where req’d. Only carry out the work in a competent and safe manner. Inform the Supervisor (Responsible/Authorising person) of any training needs or any unsafe working practices. Ensures ALL control measures required to safeguard those who may be affected by the activity, are identified, included on all permits and actioned. |
| Responsible Person | Approves mandatory and non-mandatory permits. Ensures ALL control measures required to safeguard those who may be affected by the activity, are identified, included on all permits and actioned. Ensures the competent person undertaking the work is fully conversant with the safety implications and control measures associated with the activity. Ensure ALL Competent Persons under their control fully understand and comply with the permit system. |
| Authorising Person | Person issuing a Permit to Work. Ensure all contractors & EMS staff fully understand and comply with the Permit to Work system. Only issues permits which have been approved by the responsible person, have a completed PoWRA and for contractor works, adequate RAMS Coordinate all technicians/BMS Engineers activities on site, including EMS related contractors. |

- PROCESS

At The Pirbright Institute we have two variants of the Lockout procedure; “Personal Lockout” and “Permit Lockout” Both ensure a safe working environment, are highly effective when used in the correct manner, and both are based on informed judgement AND/OR operational judgement. A permit will NOT be required for the personal lockout.

For BOTH procedures, a Point of Work Risk Assessment (PoWRA) WILL be carried out by a CP.

Personal Lockout

The Personal Lockout system has been introduced in order to allow a reasonably practicable Safe System of Work (SSoW) whilst maintaining controlled measures, so that risks to personnel and equipment are minimised.
All Technicians/BMS Engineers have their own personalised set of padlocks (Yellow) and keys which are marked with the Technicians/BMS Engineers initials. If needed, lock out devices and various lengths of chain or cable locks are also available from the Permit Station.

Once a task has been assigned via Planon, the engineer will utilise this system, if needed, in order to safely carry out the maintenance.

Upon completion of this, the Technician/BMS Engineer will make the necessary engineering checks before removing the locks and de-isolating the system/electrical supplies, re instating the equipment / system / circuit before moving on to the next task.

This method can only be used if the task can be started AND completed within the Technicians daily working hours or the BMS Engineers working shift. If this is not the case then a Permit Lockout will need to be used.

Permit Lockout

There will become a time when the Personal Lockout procedure is not durable enough when weighed against the increased risks. This would be on occasions such as;

- When the task completion time will extend beyond your normal working hours

- If the Technician/BMS Engineers feels that the associated risks are deemed sufficient enough to warrant a mandatory permit.

- All isolations required for contractor works to take place

The Permit Lockout procedure is associated with MANDATORY PERMITS and as such, has to be strictly adhered to.

Once permission is given and the Permit to Work request has been filled out, mechanical AND/OR electrical isolations are made and the isolators are locked in position using lockout devices and padlocks (Red). A sign/tag will be used to indicate that maintenance work is in progress. Any stored energy (either mechanical or electrical) must be dissipated before the work starts.

If more than one Technician/BMS Engineer is involved in the work, each of them should lock off the energy source with their own padlock. Multi-padlock hasps and/or lock out boxes, can be used in such circumstances.

Before entering or working on the equipment, it is essential that the effectiveness of the isolation is verified by a suitably Competent Person.

Contractor Works

Isolation of site services to enable contractor works of any type should always be performed by a TPI technician under permit.

Following this, contractors should also add their own padlocks to the isolation, either locally (utilising a hasp) or at the central permit station (utilising a lock out box).

Written Scheme of Examination

All users and owners of pressure systems need to be able to demonstrate that their equipment is safe to use and that they are firmly aware of its safe operating limits. 
A written scheme of examination is a document containing information about selected items of plant or equipment which form a pressure system, operate under pressure and contains a ‘relevant fluid’.

The term ‘relevant fluid’ is defined in the Pressure Systems Safety Regulations 2000 and covers compressed or liquefied gas, including air, at a pressure greater than 0.5 bar (approximately 7 psi) above atmospheric pressure; pressurised hot water above 110 °C; and steam at any pressure.

If any plant or equipment is going to fall outside of its examination or test date, the competent person (i.e. Insurance inspector) will need to be contacted to request an extension prior to the expiry date.

The plant or equipment would be ‘locked off and tagged out’ under The Institutes Safe System of Work procedure and Line Managers will be informed.

- FLOWCHART

- INSTRUCTIONS

| Step by step actions |  |
| --- | --- |
| 1 | Fill out a Point of Work Risk Assessment. |
| 2 | Is a Mandatory Permit required? (If you are a Contractor or the risk is deemed sufficient enough to warrant a Mandatory Permit.) If YES go to step 9, if NO then go to step 3. Note: Items containing a (P) are MANDATORY, in addition to; - When the task completion time will extend beyond your normal working hours - If the Technician/BMS Engineer feels that the associated risks are deemed sufficient enough to warrant a mandatory permit |
| 3 | Can the task can be completed within your working day? If YES go to step 4. If NO go to step 10. |
| 4 | Implement ‘personal’ Lockout, isolate equipment under ‘normal’ circumstances before applying personal padlocks and tags. |
| 5 & 6 | Isolate relevant valves and/or breakers and apply the lockout to each isolation, locking them in the ‘valve closed’ position and/or the ‘breaker open’ position. NOTE: Double isolations will be carried out where appropriate OR when risk dictates. |
| 7 | Ensure personnel are safe BEFORE confirming the equipment has been isolated, THEN confirm the isolations. |
| 8 | Verify any stored energy on the equipment/system/circuit has been released. |
| 9 | If it is identified that a permit is required, notify the Responsible Person (RP) of the need for a Permit to Work (PtW). |
| 10 | Fill out parts ‘A’, ‘B’ and ‘C’ on the PtW form, entering isolations on part ‘C’. Enter isolations here |
| 11 | Ensure the top copies go onto the Permit Board. Second copy to the AP’s file and the final copy to the CP. |
| 12 | Fill out the Work Control Board with the location, type of work and the name of the person carrying out the work (CP). |
| 13 | Numbered padlocks and tags are to be issued and the lock out devices collected that are required to isolate the equipment/system/circuit mechanically and/or electrically. |
| 14 | Isolate equipment as per normal operating procedure (e.g. via stop button). Isolate relevant and agreed valves and/or breakers and apply the lockout to each isolation, locking them in the ‘valve closed’ position and/or the ‘breaker open’ position. If more than one person is involved in the work, each of them should lock off with their own padlock utilising a multi padlock hasp and a lockout box. |
| 15 | Verify any stored energy on the equipment/system/circuit has been released. Place padlock keys into key safe on the Permit Board at the Permit Station. |
| 16 | RP to lock the “LoTo Board Key Safe” and return the key #42 into the Workshop 1-180 ‘Traka’ cabinet. |
| 17 | Proceed with maintenance. |