	HR and Corporate Affairs Directorate

Maintenance Services
	[image: image1.jpg][NHS|

Greater Manchester

Mental Health
NHS Foundation Trust







	Scheme Title:
	Greater Manchester Mental Health NHS Foundation Trust [GMMH]
Management of Water Systems

	Site Locations:
	Prestwich Site
Royal Bolton Hospital Site

Safford Royal Hospitals Site

Trafford General Hospital Site
Salford Community Sites

Bolton Community Sites

Trafford Community Sites

Cumbria Locations

Central Lancashire Locations

	Customer:
	Greater Manchester Mental Health NHS Foundation Trust
HR & Corporate Affairs Directorate

Bury New Road

Prestwich

Manchester

M25 3BL

Telephone | 0161 358 1361
Email | john.warburton@gmmh.nhs.uk



	Contact for Information:
	John Warburton | Maintenance Manager.

Telephone Number: 0161 358 1361

	Contract Period:

Start Date:

Completion Date:


	01st December 2018
30th November 2020 with an option to extend for another 12 month period

	Scope of the Contract:
	Management of Domestic Water Systems

The requirement of the Trust is to appoint a contractor to undertake the management of domestic water systems in accordance with current legislation. The successful contractor will be appointed for a twenty four month period.


	Management of Water Systems Criteria:
	The management of water systems will be in accordance with all current Legionella legislation, Regulations and HTM Publications:



	1.0
	Specification of Work:

	1.1
	The successful contractor will be required to record all testing data on GMMH’s Micad 4 Document Exchange module Micad 4 is GMMH’s central repository for all key estates information and documentation. Training and log in details will be provided to the successful contractor.

	1.2
	Monthly 
Draw-off Sentinel Hot and Cold Water Temperature Readings:

Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To locate and measure the hot and cold water sentinel outlet temperatures at the relevant draw-off points after allowing the water to run for a period of two minutes for cold water and one minute for hot water; the results are to be recorded in the location log book.

	1.3
	Monthly 

Calorifier and Domestic Hot Water Generators Temperature Readings:

Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To measure the storage heater, flow and return temperatures of the domestic hot water at the relevant calorifier or domestic hot water generators. The results are to be recorded in the building location logbook. 

	1.4
	Monthly 

Expansion Vessel Flushing:

Where possible provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. Flush and purge water from the vessel and supply pipe to a suitable receiver. The results are to be recorded in the building location logbook.

	1.5
	Quarterly 
Showerheads and Hoses:
Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To carefully remove the flexible hose and handset, dismantle as far as possible, mechanically clean with detergent solution and immerse into a 20ppm chlorinated solution for 3 minutes or other approved solution, ensuring that air bubbles, are not trapped in the hoses.  After replacement, the shower hose and handset should be carefully discharged for one minute to remove any solution remaining in the components. The procedure is to be recorded in the location logbook.



	1.0
	Specification of Work Continued

	1.6
	Quarterly 

Spray Taps and Point of Use Water Heater Spray Nozzles:

Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To carefully remove any fittings and dismantle as far as possible, mechanically clean with detergent solution and immerse into a 20ppm chlorinated solution for 3 minutes or other approved solution. After replacement, the fitting should be carefully discharged for one minute to remove any solution remaining in the components. The procedure is to be recorded in the building location logbook.

	1.7
	Six Monthly 
Thermostatic Mixing Valve Maintenance:

Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To locate and measure the hot and cold water supply and blended temperatures at all thermostatic mixing valves in accordance with the HTM 04-01 D 08: and manufacturer’s instructions, check that they fail-safe and continue to deliver the water at the temperature levels required. The procedure is to be recorded in the location logbook.

	1.8

	Annually 
Draw-off Randomised Hot and Cold Water Temperature Readings:

Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To locate and measure the hot and cold water temperatures at agreed representative outlets. The representative outlets will be determined by taking 20% of the total outlets installed within the building. The outlets to be, checked will be, selected on a rotational basis year on year. The results are to be recorded in the location logbook.



	1.9

	Annually Cold Water Storage Tanks Inspection:

Provide all necessary labour, transport and equipment to attend each location identified on the Location Listings detailed in [Appendix 1]. To locate and complete inspections of all cold water storage tanks within the properties. Produce a report detailing the inspection and any defects identified. The report is to be recorded in the location logbook.




	1.0
	Specification of Work Continued

	1.15
	Existing Water Draw-off Points:

Detailed in [Appendix 1] is a detailed listing of draw-off points within the buildings located throughout GMMH Trust Estate.

	1.16
	Domestic Cold Water Supply and Storage Information:

Detailed in [Appendix 1] is the cold water supply and storage information for the buildings located throughout the GMMH Trust estate.


Page | 4

[image: image1.jpg]