|  |  |
| --- | --- |
| **Scope of Works** |  |
| **Title:** | Supply and Install of Uninterrupted Power Supply to BACS Control Panels  |
| **Project:** | The Brooksby Building BACS Alarm Categorisation and Integration, additional BACS Alarms and Uninterrupted Power Supply Requirements |   |
| **Date:** | 11-11-2024 |  |
| **Author:** | Ben Williams |  |
| **Owner:** | David Shadwell |  |
| **Client:** | The Pirbright Institute |
| **Version No:** | 1 |  |

# Scope of Works History

## Document Location

N:\E&M Dept\private\-8-COMMERCIAL\Procurement\UPS Tender Pack

## Revision History

|  |  |  |  |
| --- | --- | --- | --- |
| **Version** | **Date** | **Details** | **Author** |
| 1 | 11/11/2024 | First Issue. | BW |

## Approvals

This document requires the following approvals.

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| **Name** | **Title** | **Signature** | **Date** | **Version** |
| Ben Williams | EMS Programme Manager |  | 11/11/2024 | 1 |

## Issue History

In addition to the approvers, this document has been issued to:

|  |  |  |  |
| --- | --- | --- | --- |
| **Name** | **Purpose** | **Date of Issue** | **Version** |
| Potential Suppliers | For Tender | TBC | 1 |
|  |  |  |  |
|  |  |  |  |

# Table of Contents

[1 Scope of Works History 1](#_Toc182301215)

[1.1 Document Location 1](#_Toc182301216)

[1.2 Revision History 1](#_Toc182301217)

[1.3 Approvals 1](#_Toc182301218)

[1.4 Issue History 1](#_Toc182301219)

[2 Table of Contents 2](#_Toc182301220)

[3 Introduction 4](#_Toc182301221)

[3.1 Document Purpose 4](#_Toc182301222)

[3.2 Summary Description of works 4](#_Toc182301223)

[3.3 Contact Details 6](#_Toc182301224)

[3.4 Location of Works 7](#_Toc182301225)

[4 Site Information 8](#_Toc182301226)

[4.1 Health & Safety Requirements 8](#_Toc182301227)

[4.1.1 Risk Assessments & Method Statements 8](#_Toc182301228)

[4.1.2 Tools and Equipment 8](#_Toc182301229)

[4.1.3 PPE 9](#_Toc182301230)

[4.1.4 Barriers and Warning Signs. 9](#_Toc182301231)

[4.1.5 Scaffolding and Access Equipment 9](#_Toc182301232)

[4.1.6 Equipment Certification 9](#_Toc182301233)

[4.1.7 Permits 9](#_Toc182301234)

[4.1.8 Isolations 9](#_Toc182301235)

[4.1.9 Asbestos 9](#_Toc182301236)

[4.1.10 Emergency Procedures 10](#_Toc182301237)

[4.2 Security and Site Access Requirements 10](#_Toc182301238)

[4.2.1 Photos 10](#_Toc182301239)

[4.2.2 Site Access 10](#_Toc182301240)

[4.2.3 Site Inductions 10](#_Toc182301241)

[4.2.4 Approved Contractors and Escort Requirements 10](#_Toc182301242)

[4.2.5 Vehicle Movements 10](#_Toc182301243)

[4.2.6 Welfare Facilities 11](#_Toc182301244)

[4.2.7 Working Hours 11](#_Toc182301245)

[4.2.8 Construction site management 11](#_Toc182301246)

[4.3 Bio Safety Quarantine and Decontamination Requirements 11](#_Toc182301247)

[4.4 Design Requirements 11](#_Toc182301248)

[4.4.1 Design Responsibility 11](#_Toc182301249)

[4.4.2 Standards and Specifications 11](#_Toc182301250)

[4.4.3 Design Review 11](#_Toc182301251)

[4.4.4 Documentation 11](#_Toc182301252)

[4.5 Completion of works 11](#_Toc182301253)

[4.5.1 Inspection and Testing 11](#_Toc182301254)

[4.5.2 Commissioning 12](#_Toc182301255)

[4.5.3 End Users Training 12](#_Toc182301256)

[4.5.4 Snagging Surveys 12](#_Toc182301257)

[4.5.5 Project Information File (PIF) 12](#_Toc182301258)

[4.5.6 Operations Handover Workshops 12](#_Toc182301259)

[4.5.7 Project Completion Sign Off 12](#_Toc182301260)

[4.5.8 Waste Management 13](#_Toc182301261)

[4.6 Commercial Requirements 13](#_Toc182301262)

[4.7 Project Management Requirements 13](#_Toc182301263)

[4.7.1 Project Meetings. 13](#_Toc182301264)

[4.7.2 Project Risk Register 13](#_Toc182301265)

[4.7.3 Project Programme 13](#_Toc182301266)

[4.7.4 Documentation Storage 14](#_Toc182301267)

[4.7.5 Project Co-Ordination 14](#_Toc182301268)

[4.7.6 Client Representative 14](#_Toc182301269)

[4.7.7 Responsibilities 14](#_Toc182301270)

[5 Works Information 16](#_Toc182301271)

[5.1 Work Package 1: Supply and Installation of UPS and associated works 16](#_Toc182301272)

[6 CDM requirements 17](#_Toc182301273)

[6.1 Client Brief 17](#_Toc182301274)

[6.2 Duty Holders 17](#_Toc182301275)

[6.3 Management Arrangements 18](#_Toc182301276)

[6.4 Notification to HSE 18](#_Toc182301277)

[6.5 Construction Phase Plan 18](#_Toc182301278)

[6.6 Health and Safety File 18](#_Toc182301279)

[6.7 Application of CDM to this project 19](#_Toc182301280)

# Introduction

## Document Purpose

The primary purpose of this version of the document is intended to:

* Give details of works required to potential suppliers so they can submit a tender and programme of works.
* Fulfil the client brief and pre-construction information aspects of construction design management (CDM) regulations 2015.

For comparison only, this version of the document could be aligned with Royal Institute of British Architecture (RIBA) Plan of work 2014 Stage 1 (Preparation & Brief).

As the project progresses, this document will be updated to contain more detailed information on the proposed design and delivery of the works.

Should changes to the scope occur, these will always be recorded in meeting notes and the scope document will be updated and re-issued if appropriate.

This document details the envisaged requirements of the works but should not been seen as restrictive. All parties should advise if:

* Appropriate alternatives are available.
* There are additional requirements needed.
* Envisaged requirements are required.

## Summary Description of works

The Brooksby Building at The Pirbright Institute (Pirbright) will be a high containment facility for work on high consequence pathogens such as foot-and-mouth diseases virus (FMDV) when fully operational in 2026.

As part of the post-construction ‘Day 2’ works there is a requirement to carry out additional works to the Building Automation and Control System (BACS) within the Brooksby Building to ensure it is fully aligned with the primary system used across the rest of the Pirbright site.

The following package of work has been funded:

* Installation of Uninterrupted Power Supply (UPS) to critical BACS Control Panels

**The Scope of Works for this contract is as follows:**

|  |  |  |
| --- | --- | --- |
| **Activity** | **Description** | **Details** |
| Equipment | 1 x Large UPS Unit | Riello 30kVA Master MPS (6 Pulse Rectifier, 384VDC Battery, UPS to be fitted with a Multicom 384 comms card to be wired by Pirbright appointed contractor.  This UPS to be fitted 90Ah 384V 10-year design Life Battery Extension Pack with Isolator.An external maintenance bypass switch rated at 125Amp 3 phase 415v a.c. External wall mounted manual bypass switch that facilitates total electrical and physical isolation of the Reillo UPS without break to the load. Safety interlocking is incorporated within these units. Complete with protected sockets. This unit measures 500mm high by 500mm wide by 200mm deep and weighs 23kg.The DB serves 24 x 240v outgoing SWAs to BACs panels and associated equipment, the UPS will support power for a period of 53 mins as per design criteria if DRUPS fails to start with additional noted battery expansion pack.***Please also include a separate ‘option b’ quotation for Modbus compatible unit or Riello with Multicom302 board for MODBUS*** |
| Equipment | 20 x Small UPS units | Sentinel Pro single phase on line 1kVA (0.8kW) 240v a.c. UPS’ to be fitted with Multicom 384 comms card to be wired by Pirbright appointed contractor at locations indicated in drawings (provided to successful tenderer), external to control panels to give best possible ventilation. The “shelf” to be constructed of Unistrut and installed at a height to be serviceable and not to cause obstruction or in a position that may pose a concern to engineering team members. Cost of Unistrut supply and installation should be included in quotation for this work. ***Please also include a separate ‘option b’ quotation for Modbus compatible units or Riello with Multicom302 board for MODBUS*** |
| Materials | As required | All required materials to be included: Cable, containment, Unistrut etc. |
| Installation | Large UPS unit | Installation of 1 large UPS to 415v a.c. 3ph distribution board 50-DB-06-A-MECH rated at 100Amp complete with bypass switch fed from 50-SB-01-A at the main LV switch board on the AHU deck. This is inclusive of re-routing SWA and black plastic coated metallic flexible conduits. Install a Unistrut base to keep the UPS off the concrete with a clearance of 100mm.  |
| Installation | 20 Small UPS Units | Installation 20 Sentinel Pro UPS Units at locations indicated in drawings, external to control panels to give best possible ventilation. The “shelf” to be constructed of Unistrut and installed at a height to be serviceable and not to cause obstruction or in a position that may pose a concern to engineering team members.  |
| Commissioning and testing | All units | Test and commission all the above UPSs with installation to BS7671 electrical installation standard |
| Documentation | ALL | Updated drawings showing site installation worksTesting and commissioning results  |

To also be included in quotation:

* Delivery of all materials to site
* Production and issue of a programme of works
* Provision of O&M Manual
* Project management

*Please note that Pirbright in-house team will update existing drawings upon completion of works, contractor not required to provide updated drawings.*

## Contact Details

John Nixon

* Role: Procurement Buyer
* John.Nixon@pirbright.ac.uk
* 01483 232441
* Normal working hours: 08:30h to 17:00h, Monday to Friday

Maz Al-Zobaidy

* Role: The Pirbright Institute Project Business Sponsor
* maz.al-zobaidy@pirbright.ac.uk
* 01483 231 044

 Ben Williams

* Role: The Pirbright Institute Project Business Sponsor
* Ben.williams@pirbright.ac.uk
* 01483 231290

## Location of Works

These works will take place at the following addresses: The Pirbright Institute

Ash Road, Pirbright, Woking, GU24 0NF

# Site Information

This section contains information related to delivering these works at The Pirbright Site.

## Health & Safety Requirements

All works related to this specification should be performed in line with site Health & Safety (H&S) rules and the Health and Safety at Work Act 1974.

The following documents are attached in Appendix E1 C and detail the site rules to be considered when tendering and when works are performed on site:

* RISK-SOP-7: Management of Contractors
* R&A-COP-3: Contractor Site Handbook
* R&A-FORM-4: Pirbright Site Rules Overview
* EMS-WI-085: Permit to work
* EMS-FORM-100: Point of Work Risk Assessment (POWRA)
* EMS-FORM-098: Permit to Work Part A, Part B & Part C
* EMS-WI-82: EMS Lockout/Tagout Work Instruction

If required, further training on the procedures detailed in the above documents can be given on site.

The above documents detail Pirbright’s management of H&S for construction works, the following sections highlight aspects requiring particular attention.

### Risk Assessments & Method Statements

Any works on the site must be preceded by a risk assessment and method statement (RAMS). These must be submitted to the Pirbright responsible person at least 5 days in advance of the works.

RAMS must be specific to the task and date of the works and should include a detailed step by step method.

RAMS are never “approved” but will be “reviewed” by Pirbright personnel, and feedback will be given. A permit to work will not be issued if the RAMS are deemed to be inappropriate.

Where appropriate, RAMS should be accompanied by drawings to help explain their context.

Details of the competent person performing works and their relevant training records should be included and/or referenced in the RAMS.

### Tools and Equipment

Contractors should always provide their own tools and equipment they require to complete their works. Pirbright will not issue equipment to contractors.

Equipment which must be supplied by the contractor is as follows. The equipment must be suitable for fumigation or can be disposed of. All items of test equipment must have a current calibration certificate.

Equipment used by contractors should be in good working order and comply with all relevant legislation. Electrical equipment should be PAT tested.

Equipment brought into Pirbright’s restricted areas will need to be suitable for fumigation or disposal.

Where appropriate calibration, inspection and testing certificates of equipment being used should be issued to the responsible person before work commences.

### PPE

Contractors should provide their own personal protective equipment (PPE). PPE used should be suitable for the works and specific type/specification of PPE should be detailed in the RAMS.

### Barriers and Warning Signs.

Area of works must be cordoned off with suitable barriers and warning signs to prevent unauthorised pedestrian access during work activities.

Contractors must provide their own barriers and warning signs.

### Scaffolding and Access Equipment

Contractors should arrange scaffolding required to facilitate their works, Pirbright preferred suppliers can be utilised. Contractors should ensure that scaffolding is inspected and tagged on a weekly basis once erected.

Contractors should provide all temporary access equipment such as ladders and mobile platforms. These should be class 1 (industrial) certification standard. Pirbright will not issue access equipment to contractors.

All access equipment should be in good working order (visual check before use) and have been inspected in the last 6 months.

### Equipment Certification

Where appropriate, evidence of inspection / testing / commissioning of equipment supplied or used for installation works should be provided.

### Permits

All construction works performed by contractors require a permit to work. See EMS-WI-085: Permit to work (Appendix E1 C) for further details.

Note: The application of the safe system of work and permits to the construction works with relevant members of Capability EMS as advised by the project sponsor in advance of works commencing.

### Isolations

Isolations of Pirbright site energy sources must be performed under permit by Pirbright maintenance technicians and should be witnessed by the contractor performing the work.

These isolations should then be secured with padlocks of contractors working downstream of the isolation. See EMS-WI-87: EMS Lockout/Tagout Work Instruction (Appendix E1 C) for further details.

### Asbestos

There is no asbestos risk associated with this construction work, the site asbestos register is available on request.

If any suspected asbestos is identified during the works, then works in the area should be stopped and it should be highlighted to the site contact, who will arrange sampling to take place.

### Emergency Procedures

If an emergency event is discovered, such as a fire or medical emergency, the site gatehouse should be contacted for assistance on the emergency extension number 1000 or on radio channel 1.

On discovering a fire, the area should be evacuated, and all personnel should go to the fire assembly point. If safe to do so, fire alarm call points should be activated on the way out of the area.

In the event of a fire alarm, works should cease, and contractors should make their way to their fire assembly point (to be given by the project manager).

## Security and Site Access Requirements

RISK-COP-3 and RISK-FORM-4 (Appendix E1 C) details site access requirements. The following sections highlight aspects to be considered.

### Photos

Photos can only be taken with prior agreement from the project manager. Any photos taken should not include any faces or vehicle number plates.

### Site Access

To gain access to site, all contractors must have visitor forms raised for them by their site host before arrival on site, therefore a full names and dates of all personnel attending site must be provided at least 24h in advance.

Contractors must report to the gatehouse and present photo ID each time they access site.

### Site Inductions

There are no works within restricted area, therefore no site induction over and above the contractor handbook is required for these works.

Construction site specific inductions should be created and delivered to all personnel visiting or working within the construction site.

### Approved Contractors and Escort Requirements

Contractors must be fully escorted by Pirbright personnel unless there are approved contractors within the team.

An appropriate number of contractors in each team should complete an institute security check (performed by Agenda). The cost of this is covered by the institute. This process can take up to 2 weeks to complete. In order to do initiate this process, provide full names and an email address specific to the person to the site contact.

1 approved contractor can escort up to 3 unapproved contractors.

Even approved contractors may require an escort in certain restricted areas of site, however none of the works are envisaged to take place within restricted areas.

### Vehicle Movements

Vehicle movements on site roads is subject to a speed limit of 10 mph, which must be always obeyed. Extra caution should be taken by drivers on site roads due to shared use of roads by pedestrians, bicycles and vehicles.

Vehicle access to the site is through the main entrance at the north boundary of the site.

### Welfare Facilities

Welfare facilities are available next to the site office.

### Working Hours

Contractors will be able to access site from 0700h – 1600h Monday to Friday, works outside of these hours need to be arranged with the project sponsor.

### Construction site management

The construction site is a CDM Site and is managed by Pirbright’s Clerk of Works.

## Bio Safety Quarantine and Decontamination Requirements

There aren’t expected to be any such requirements, however further details will be given on site if this changes.

## Design Requirements

### Design Responsibility

Design work should be carried out by the individual contractor and agreed with The Pirbright Institute via the Project Sponsor.

### Standards and Specifications

All equipment supplied and installed should be manufactured, installed, tested and commissioned in accordance with all applicable national and international standards and manufacturer’s instructions. These should be referenced in any quotation documentation and RAMS documents.

### Design Review

The proposed design should be reviewed with appropriate Capability EMS personnel.

The Principal Designer and any appropriate sub designers must provide any information requested in advance.

### Documentation

The following documentation should be issued before works commence:

* + - * Design Drawings
			* Control Philosophies
			* Design calculations, or statements confirming they are not required.
			* Relevant safety certificates for equipment being used to perform the works.

## Completion of works

The following sections details what constitutes completion of the works.

### Inspection and Testing

Any records relating to the inspection, testing and commissioning of an installation should be provided to the project manager.

Where appropriate, witnessing of these by a member of the Pirbright engineering team may be required.

### Commissioning

Commissioning of equipment must take place to prove that requirements as detailed by this scope of works have been successfully met.

Commissioning requirements must be drafted during the Design development phase of the project and finalised during the detailed design phase of the project.

### End Users Training

Appropriate end users training must have taken place to a level that the end user feels they can successfully operate and maintain any equipment.

### Snagging Surveys

All works, they must be visually inspected by an appropriate member of the Pirbright engineering team. Any snags identified shall be listed on a project snagging schedule by the project manager and reviewed with the principal contractor and project sponsor to agree where responsibility for remedial works lies.

Performance and documentation defects/deficiencies can also be recorded and traced on this schedule.

### Project Information File (PIF)

Final handover to the Pirbright operations team includes the completion of a Project Information File (PIF). This includes information from the contractors. Details of what is to be included in the PIF are shown in the PIF check sheet included in Appendix E1 B.

All project documentation is to be handed overusing Pirbright’s document naming convention

A full list of assets disinvested and new assets will be provided in accordance with Pirbright’s asset naming convention

### Operations Handover Workshops

Operational handover workshops should take place between once the activities in the sections above have been completed, this should be facilitated by the Project Manager and should involve the following people:

* + - * Capability EMS Leader Operations and Maintenance
			* Capability Operations Projects Manager
			* Appropriate Capability EMS Specialist Equipment Owners
			* Capability EMS BMS Owner
			* EMS Technical Coordinator
			* Maintenance Supervisor(s)
			* Science Users (if applicable)
			* IT representatives (if applicable)
			* HSBS representatives (if applicable).

All project and Handover documentation will be accessed on “Procore”, the cloud-based system which Pirbright use for their document and drawing management.

All documentation for review will be uploaded to Procore and will be organised according to Pirbright’s stated document naming convention.

### Project Completion Sign Off

Once all the activities in the above sections have been completed, then a project completion sign off sheet should be signed by those that attended the handover workshops.

This marks the completion of the project and any new equipment installed is now managed by Capability EMS Operations and Maintenance.

### Waste Management

A project will not be signed off if waste from the works remains on site, contractors must dispose of waste from the works via appropriate means.

Pirbright waste streams must not be used without prior agreement.

It is envisaged that no Pirbright waste streams will be used for the delivery of these works.

All waste spoil created by the works must be removed from site by the contractor and disposed of in an appropriate manner. However, this must be confirmed in writing with the Pirbright Biosafety team as spoil from some areas of site must be stored and/or sampled on site before disposal.

Any waste skips/bins/collections must be arranged by the contractor.

## Commercial Requirements

Contractor capability should be reviewed before works are awarded. This may involve but is not limited to:

* Completion of Supplier Pre-Qualification Questionnaire
* Assessment of the quality of Request for a Quote submission via a scoring matrix
* Issuing of relevant company certification (such as ISO 9001, safe contractor etc.). Where certification is not present, documentation showing a satisfactory alternative system is in place should be issued.
* Visits by Pirbright personnel to supplier manufacturing facilities or reference sites
* Issuing relevant training records of all contractors and managers associated with the works Were appropriate, contracts will be administered under an NEC standard form of contract.

## Project Management Requirements

### Project Meetings.

Regular project progress meetings between the project manager will take place with the principal designers/ contractors and any other relevant personnel required regularly.

### Project Risk Register

A project risk register is included in Appendix E1 D.

### Project Programme

An envisaged project delivery schedule is as follows:

* Procurement of main contractor: November to December 2024
* Programme of works (including lead time and installation): January to March 2025

A live project programme will be agreed once contractors are procured.

Contractors should provide a delivery and installation programme associated with any works they are quoting for.

The project manager should own and maintain the overarching project programme and principal contractors/designers should provide information on their elements of works as required.

### Documentation Storage

Pirbright’s document management system is the cloud-based “Procore” system and this will be used for the sharing of all design information, handover, etc to ensure traceability.

The Following documents apply:

EMS-WI-230 - Technical Library Principles of Use

* Appendix 1 - EMS Document Naming Convention
* Appendix 2 - Procore Disciplines EMS-WI-403 - Procore User Guide
* Appendix 1 - Procore Superuser Guide EMS-WI-329 – EMS Asset Convention
* Appendix 1 - EMS Asset Naming Convention
* Appendix 2 - TOPdesk Asset Import Template

### Project Co-Ordination

The following activities will ensure project co-ordination:

* + - * Regular project management meetings, primarily between the Pirbright client representative and the principal contractor
			* Regular site checks to see progress and ensure works are taking place in a safe manner.
			* Regular updates from the Pirbright engineer overseeing the works to the Pirbright Capability EMS Team.

### Client Representative

Pirbright Project Manager will be acting as the Client Representative in terms of CDM responsibilities.

### Responsibilities

The responsibilities of each party for these works are as follows:

Pirbright Project Sponsor.

* + - * Business Case Author
			* Budget Control
			* Benefit realisation
			* Escalation of issue to senior management when required
			* Halting project if required
			* Approving changes to project scope
			* Reviewing and agreeing detailed design before works commence
			* Responding to contractor queries
			* Review and amending of Project Highlight reports.
			* Advising the Project Manager on the application of site processes and what personnel should be consulted for project queries.

Pirbright Project Manager & CDM Client Representative.

* + - * Drive day to day activities to delivery of the scope of works.
			* Preparation of monthly Project Highlight Reports on Pirbright template
			* Act as site host for principal contractors / designers.
			* Create and agree with principal contractors the content of the construction site induction.
			* Create and maintain scope of works document.
			* Create and maintain a project risk register.
			* Create and maintain project programme.
			* Managing project documentation
			* Raise purchase orders if required.
			* Co-ordinate the contractor, designers and institute personnel to facilitate works.
			* Facilitate site access.
			* Reviewing and agreeing detailed design before works commence.
			* Arrange and chair project meetings and issuing notes of meetings.
			* Responding to contractor queries
			* Arrangement of permits and isolations
			* Ensuring works are performed in a safe manner.
			* Fulfil CDM Client Responsibilities including appointing principal contractors/designers and submission of F10 forms for notifiable projects.
			* Co-ordinating snagging surveys as required.
			* Handover to Pirbright Engineering Management
			* Arranging training where appropriate

# Works Information

This section describes the particular requirements of each works package of the scope of works.

This is not restrictive or fully detailed and the principal contractors / designers should provide additional detail where required and suggest alternatives if appropriate.

## Work Package 1: Supply and Installation of UPS and associated works

This work package is for:

* Supply and installation of new UPS and associated equipment as per Section 3.2 to existing Control Panels in Brooksby Building
* Delivery of all materials to site
* Production and issue of a programme of works
* Project management of works
* Handover to Pirbright Engineering Management ensuring all information required by the PIF is available for the Pirbright Institute

# CDM requirements

This section outlines the CDM specific requirements for the project.

## Client Brief

This scope document forms the client brief.

## Duty Holders

**Client**

The client is The Pirbright Institute; represented by the Pirbright project manager (TBC) and as such will:

* Assist with the appoint of the principal contractors as required, Pirbright will lead on the procurement.
* Take reasonable steps to satisfy themselves that appointees have H&S skills, knowledge, and experience.
* Complete HSE notification if required and display the notification at a location all contractors can see it.
* Update HSE notification if required.
* Provide Pre-Construction information as required.
* Ensure a construction phase plan is drawn up before works commence and ensure it is updated throughout the project.
* Ensure a health and safety file is drawn up before works commence and ensure it is updated throughout the project.
* Take reasonable steps to ensure the principal contractor and designer are fulfilling their responsibilities.

**Principal Designer**

The Principal Designer for each work package is to be confirmed. The principal designers will:

* Manage all sub-designers.
* Produce a health and safety file and update it throughout the project.
* Provide pre-construction information as required.

**Principal Contractors**

The Principal contractor(s) will:

* Manage all sub-contractors.
* Produce a construction phase plan and update it throughout the project.
* Provide pre-construction information as required.

## Management Arrangements

Section 4 outlines the management arrangements for the project.

## Notification to HSE

If applicable, HSE notification will be done by the client representative.

## Construction Phase Plan

Separate construction phase plans for each work package will be written and issued by the relevant principal contractor. This must be reviewed with the client before any works can begin.

The construction phase plan should include the following sections (relevant sections of this document are also referenced):

* The health and safety aim for the project:
* The site rules:
* Arrangements to ensure co-operation between project team members:
* Co-ordination of their work, such as regular site meetings:
* Arrangements for involving workers.
* Site induction.
* Welfare facilities.
* Emergency procedures, such as fire and first aid.
* The control of any of the specific site risks relevant to the.

## Health and Safety File

Each work package should have a health and safety file maintained by the relevant principal designer throughout the project and issued to the client as a standalone document on the completion of works.

It should include the following information:

* Brief Description of the work being carried out.
* Project Risk Assessment.
* Key structural principles.
* Hazardous materials used.
* Information on the future removal of installed plant.
* H&S information about equipment provided for cleaning or maintaining installed plant.
* The nature, location and markings of significant services.
* Information and as built drawings of buildings, plant, and equipment.

## Application of CDM to this project

The Brooksby Building is a CDM site managed by the Site Manager; Pirbright’s Clerk of Works. These works will form part of the wider project of ‘Day 2’ Works.