NBS L20 /410 Specification for Timber Doorsets.

Date: 26th January 2024

Number:

Project: City College Plymouth 2nd Floor Tower

Architect: G Parry Consulting

Manufacturer: Hanson and Beards Ltd. Holmfield Industrial Estate, Holmfield, Halifax.  HX2 9TN. Tel: (01422) 306830.

E mail: info@hansonandbeards.co.uk.

- Product reference: Anodoor and Anodoor Ultra range doorsets, in accordance with issued drawings and schedules.

- Fire resistance rating: Tested in accordance with BS 476 Part 22: 1987. In accordance    with manufacturers certified tested dimensions and published technical manual.

Non- Fire Rated and FD30 and FD30s

NB: All fire doorsets with ‘S’ rating to have drop down seals

- Acoustic Rating: Tested in accordance with BS EN ISO 140-3:1995 with results expressed as a single weighted index in accordance with BS EN ISO 717-1:1997.

Where noted on architect’s schedule to 32dB Rw

- Mechanical Strength: Mechanical Test evidence to “Severe Duty” in accordance with DD171: 1987

- Timber Chain of Custody:  FSC (Forestry Stewardship Council) mixed sources.

Door Leaf Core:

- Anodoor Ultra core, 44 mm thick door, weighing 27 kg m2 with graduated density particle board having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Anodoor standard core 44mm thick door weighing 27 kg/M2 with graduated density particle board.

- Facings: Crown Cut American White Oak Veneer

- Lippings:   Oak hardwood 10 mm thick, with a chamfered lipping to all 4 no edges, with factory applied clear lacquer.

- Meeting Stiles: Square vertical.

- Vision Panels: (Where noted on schedule) Fully Glazed

- Glass: FD30 Integrity and Insulation 15mm clear Pyroguard (1.90 m2 max)

- Beading: Oak Hockey stick angled glazing bead, to suit FD30, fixed in position with angled pins.

- Doorframes: FD30 door frames to be approved hardwood minimum density 640 kg/M3 /softwood with a minimum density 450kg/m3. Frame will be fitted with approved / tested intumescent strips / smoke seals.  Refer to specification door type.

All paint grade frames up to 150mm wide to be one piece timber with MDF extension liner thereafter.

Type: INT-LS01, rectangular single action frame, minimum dimensions 70mm x 32mm having separate timber stop 32mm x 12mm.

- Finish: Factory primed paint for on-site preparation and finish by others.

- Architraves: 69mm wide x 18mm thick Square Profile ‘C’

- Timber species: MDF, factory primed paint for on-site finish by others.

- Ironmongery: To be as ‘Synthesis’ ironmongery as per schedule and specification.

- Moisture content on delivery: All door cores to be 6% with hardwood lipping’s to be 10%

(+/- 2%)

- Appearance class to BS EN 942:

- Preservative treatment: Not applicable

- Perimeter seals: See manufacturers recommendations / information

- Fixings: : See manufacturers recommendations / information

- Other requirements: NB:

L20/410 Internal Timber Double doorset Type DD01

FD30s Single Swing Equal Double Doors with Vision Panel and Solid Over Panel

- Door Leaf Core:

“Anodoor Ultra” core, 54 mm thick door, weighing 34 kg m2, having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered with contrasting seal to opening edge.

- Meeting Stiles: Square vertical

- Acoustic Tested Drop-down seal and batwing seals

- Vision Panels:  Full width with 150mm top/edge stiles and 200mm bottom stile

- Glass:   FD30 Integrity/Insultation 15mm clear Pyroguard (1.90 m2 max)

- Beading: a) Hockey stick angled glazing bead, to suit non fire, FD30, vision panels, fixed in position with angled pins.  To match leaf facing, Oak.

- Doorframes: FD30 door frames, white primed, to be approved softwood with a minimum density 450kg/m3 and fitted with approved / tested intumescent strips / smoke seals

Lining and loose stop as per door schedule. All paint grade frames up to 150mm wide to be one-piece timber with MDF extension liner thereafter.

- Over Panel:

Solid 44mm particle board core with transom

- Timber species: Crown Cut American Whtie Oak to match door.

- Architraves:

Profile ‘C’ 69mm wide x 18mm thick 1 edge pencil round

- Timber species: MDF, factory primed paint finish.

.

- Ironmongery:

Minimum 3 No, 100 mm x 88 mm satin stainless steel (Minimum’ BS EN1935 Grade 13) Butt hinges with radiused corners.

- Ironmongery should be fully tested with the door set / from Synthesis Hardware range refer L10 spec?

L20/411 Internal Timber Double doorset Type DD01a

FD30s Single Swing Equal Double Doors with Vision Panel

- Door Leaf Core:

“Anodoor Ultra” core, 54 mm thick door, weighing 34 kg m2, having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered with contrasting seal to opening edge.

- Meeting Stiles: Square vertical

- Acoustic Tested Drop-down seal and batwing seals

- Vision Panels:  Full width with 150mm top/edge stiles and 200mm bottom stile

- Glass:   FD30 Integrity/Insultation 15mm clear Pyroguard (1.90 m2 max)

- Beading: a) Hockey stick angled glazing bead, to suit non fire, FD30, vision panels, fixed in position with angled pins.  To match leaf facing, Oak.

- Doorframes: FD30 door frames, white primed, to be approved softwood with a minimum density 450kg/m3 and fitted with approved / tested intumescent strips / smoke seals

Lining and loose stop as per door schedule. All paint grade frames up to 150mm wide to be one-piece timber with MDF extension liner thereafter.

- Architraves:

Profile ‘C’ 69mm wide x 18mm thick 1 edge pencil round

- Timber species: MDF, factory primed paint finish.

.

- Ironmongery:

Minimum 3 No, 100 mm x 88 mm satin stainless steel (Minimum’ BS EN1935 Grade 13) Butt hinges with radiused corners.

- Ironmongery should be fully tested with the door set / from Synthesis Hardware range refer L10 spec?

L20/412 Internal Timber Single doorset Type SD01

FD30s Single Swing with Vision Panel

- Door Leaf Core:

“Anodoor Ultra” core, 54 mm thick door, weighing 34 kg m2, having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered with contrasting seal to opening edge.

- Meeting Stiles: n/a

- Acoustic: n/a

- Vision Panels:  Fully glazed with 150mm top/edge stiles and 200mm bottom stile.

- Glass:   FD30 Integrity/Insultation, 15mm clear Pyroguard (1.90 m2 max)

- Beading: a) Hockey stick angled glazing bead, to suit non fire, FD30, vision panels, fixed in position with angled pins.  To match leaf facing, Oak.

- Doorframes: FD30 door frames, white primed, to be approved softwood with a minimum density 450kg/m3 and fitted with approved / tested intumescent strips / smoke seals

Lining and loose stop as per door schedule. All paint grade frames up to 150mm wide to be one-piece timber with MDF extension liner thereafter.

- Architraves: Profile ‘C’ 69mm wide x 18mm thick 1 edge pencil round

- Timber species: MDF, factory primed paint finish.

- Ironmongery:

Minimum 3 No, 100 mm x 88 mm satin stainless steel (Minimum’ BS EN1935 Grade 13) Butt hinges with radiused corners.

- Ironmongery should be fully tested with the door set / from Synthesis Hardware range refer L10 spec?

L20/413 Internal Timber Single doorset Type SD02

FD30s Single Swing No Vision Panel

- Door Leaf Core:

Anodoor standard core, 44 mm thick door, weighing 27 kg m2 with graduated density particle board.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered with contrasting seal to opening edge.

- Meeting Stiles: n/a

- Acoustic n/a

- Vision Panels:  n/a

- Glass:   n/a

- Beading: n/a

- Doorframes: FD30 door frames, white primed, to be approved softwood with a minimum density 450kg/m3 and fitted with approved / tested intumescent strips / smoke seals

Lining and loose stop as per door schedule. All paint grade frames up to 150mm wide to be one-piece timber with MDF extension liner thereafter.

- Architraves:

Profile ‘C’ 69mm wide x 18mm thick 1 edge pencil round

- Timber species: MDF, factory primed paint finish.

.

- Ironmongery:

Minimum 3 No, 100 mm x 88 mm satin stainless steel (Minimum’ BS EN1935 Grade 13) Butt hinges with radiused corners.

- Ironmongery should be fully tested with the door set / from Synthesis Hardware range refer L10 spec?

L20/414 Internal Timber Single doorset Type SD03

FD30s Single Swing with Vision Panel and 1No Side Screen

- Door Leaf Core:

“Anodoor Ultra” core, 54 mm thick door, weighing 34 kg m2, having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered with contrasting seal to opening edge.

- Meeting Stiles: n/a

- Acoustic: n/a

- Vision Panels:  Fully glazed with 150mm top/edge stiles and 200mm bottom stile.

- Glass:   FD30 Integrity/Insultation,15mm clear Pyroguard (1.90 m2 max)

- Beading: a) Hockey stick angled glazing bead, to suit non fire, FD30, vision panels, fixed in position with angled pins.  To match leaf facing, Oak.

- Doorframes: FD30 door frames, white primed, to be approved hardwood with a minimum density 640kg/m3 and fitted with approved / tested intumescent strips / smoke seals

Lining and loose stop as per door schedule. All paint grade frames up to 150mm wide to be one-piece timber with MDF extension liner thereafter.

- Architraves: Profile ‘C’ 69mm wide x 18mm thick 1 edge pencil round

- Timber species: MDF, factory primed paint finish.

- Side Screen: FD30 Integrity/Insultation,16mm clear Pyrobelite (1.90 m2 max) glazing fitted into a 4 edge 33mm hardwood primed frame minimum density 640kg/m3.

- Glazing Bead:  Chamfered beading 30mm x 30mm primed

- Bead Fixing: Pinned

- Ironmongery:

Minimum 3 No, 100 mm x 88 mm satin stainless steel (Minimum’ BS EN1935 Grade 13) Butt hinges with radiused corners.

- Ironmongery should be fully tested with the door set / from Synthesis Hardware range refer L10 spec?

L20/415 Internal Timber Single doorset Type SD04

FD30s Single Swing with Vision Panel and 2No Side Screen

- Door Leaf Core:

“Anodoor Ultra” core, 54 mm thick door, weighing 34 kg m2, having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered with contrasting seal to opening edge.

- Meeting Stiles: n/a

- Acoustic: n/a

- Vision Panels:  Fully glazed with 150mm top/edge stiles and 200mm bottom stile

- Glass:   FD30 Integrity/Insultation,15mm clear Pyroguard (1.90 m2 max)

- Beading: a) Hockey stick angled glazing bead, to suit non fire, FD30, vision panels, fixed in position with angled pins.  To match leaf facing, Oak.

- Doorframes: FD30 door frames, white primed, to be approved hardwood with a minimum density 640kg/m3 and fitted with approved / tested intumescent strips / smoke seals

Lining and loose stop as per door schedule. All paint grade frames up to 150mm wide to be one-piece timber with MDF extension liner thereafter.

- Architraves: Profile ‘C’ 69mm wide x 18mm thick 1 edge pencil round

- Timber species: MDF, factory primed paint finish.

- Side Screen: FD30 Integrity/Insultation,16 mm clear Pyrobelite (1.90 m2 max) glazing fitted into a 4 edge 33mm hardwood primed frame minimum density 640kg/m3.

- Glazing Bead:  Chamfered beading 30mm x 30mm primed

- Bead Fixing: Pinned

- Ironmongery:

Minimum 3 No, 100 mm x 88 mm satin stainless steel (Minimum’ BS EN1935 Grade 13) Butt hinges with radiused corners.

- Ironmongery should be fully tested with the door set / from Synthesis Hardware range refer L10 spec?

L20/416 Internal Timber Single Sliding Door Type SD05

Non-Fire Rated

- Door Leaf Core:

Anodoor Ultra” core, 44 mm thick door, weighing 27 kg m2, having perimeter softwood timber framed construction around a particle board core and faced with 3 mm thick moisture resistant MDF substrate to both faces.

- Facings:  Crown Cut American White Oak Veneer

- Lippings:  Hardwood Oak 10 mm thick concealed lipping to all 4 no edges lacquered.

- Meeting Stiles: n/a

- Acoustic n/a

- Vision Panels:  n/a

- Glass:   n/a

- Beading: n/a

- Doorframes: n/a

- Architraves: n/a

.

- Ironmongery: