## AW5.2
AW5.2 Price Schedule
SOURCING REFERENCE: | FM17178 |  | This Schedule is worth a maximum of 40.00% of the vendors overall bid. The total in Cell G98 will be used for the evaluation of this project. |  |  |  | Bidders are required to complete all red highlighted cells. Where bidders are not offering a discounted price please ensure that you copy your list price into the discounted cell.
SOURCING DOCUMENT TITLE: | NERC NOC Energy Centre Chiller Structure Refurbishment Project
BIDDER NAME
|  |  |  | List | Discounted | Total
Item Number | Description | Quantity | Unit | Price | Price | Price |  | Notes & Comments
Provision of Access for Works | Provide access for Chillers Refurbishment works and inspection by the Engineer to energy centre roof.
| York Glycol Chillers | 3 | Nr |  |  | 0
York Chillers Refurbishment | York Glycol Chiller 1 - External Case Refurbishment
Price per square meter | Surface preparation - Paint coatings surrounding damaged areas shall be cleaned by approved means and ensured to be free of dust, dirt and any other foreign matter. Where oil or grease are present this shall be removed with the use of Degreaser™ W500* or similar which shall be rinsed off with clean water and allowed to dry. Areas of damage which exhibit surface rusting shall be prepared by mechanical means to ensure all residual rust is removed to BS EN ISO 8501-1:2007 Grade St3. Surrounding paint coatings shall be removed back to a firm sound edge and then feathered over a distance of 50mm in the region of the affected area. | 33 | Sqm |  |  | 0
| Spot coat - - Macropoxy™ M902 Winterfast Hi-Build Brushing Aluminium or equivalent | 6 | Sqm |  |  | 0
| Surface Tolerant Primer - - MACROPOXY TM M902 Primer or equivalent | 33 | Sqm |  |  | 0
| Undercoat - MACROPOXY TM M905 Epoxy Undercoat/Mio or equivalent | 33 | Sqm |  |  | 0
| Finish Coat - ACROLON™ C137V2 Special Finish or Equivalent | 33 | Sqm |  |  | 0
York Glycol Chiller 01 – Condenser Wire Grills replacement
| Wire Enclosure Top Section - 200 | 10 | Item |  |  | 0
| Wire Enclosure Bottom Section - 200 | 6 | Item |  |  | 0
| Wire Enclsure Bottom Section - 201 | 2 | Item |  |  | 0
York Glycol Chiller 01 – 25mm Spring isolator replacement
| 25mm Spring isolator – Part number – 029-24583-011 or similar | 8 | Item |  |  | 0
| 25mm Spring isolator – Part number – 029-24583-008 or similar | 2 | Item |  |  | 0
York Glycol Chiller 01 – Fixings replacement
| Galvanized Fixing to match the existing | 150 | item |  |  | 0
York Glycol Chiller 02 – External case refurbishment
Price per square meter | Surface preparation - Paint coatings surrounding damaged areas shall be cleaned by approved means and ensured to be free of dust, dirt and any other foreign matter. Where oil or grease are present this shall be removed with the use of Degreaser™ W500* or similar which shall be rinsed off with clean water and allowed to dry. Areas of damage which exhibit surface rusting shall be prepared by mechanical means to ensure all residual rust is removed to BS EN ISO 8501-1:2007 Grade St3. Surrounding paint coatings shall be removed back to a firm sound edge and then feathered over a distance of 50mm in the region of the affected area. | 33 | Sqm |  |  | 0
| Spot coat - - Macropoxy™ M902 Winterfast Hi-Build Brushing Aluminium or equivalent | 6 | Sqm |  |  | 0
| Surface Tolerant Primer - - MACROPOXY TM M902 Primer or equivalent | 33 | Sqm |  |  | 0
| Undercoat - MACROPOXY TM M905 Epoxy Undercoat/Mio or equivalent | 33 | Sqm |  |  | 0
| Finish Coat - ACROLON™ C137V2 Special Finish or Equivalent | 33 | Sqm |  |  | 0
York Glycol Chiller 02 – Condenser Wire Grills replacement
| Wire Enclosure Top Section - 200 | 10 | Item |  |  | 0
| Wire Enclosure Bottom Section - 200 | 6 | Item |  |  | 0
| Wire Enclsure Bottom Section - 201 | 2 | Item |  |  | 0
York Glycol Chiller 02 – 25mm Spring isolator replacement
| 25mm Spring isolator – Part number – 029-24583-011 or similar | 8 | Item |  |  | 0
| 25mm Spring isolator – Part number – 029-24583-008 or similar | 2 | Item |  |  | 0
York Glycol Chiller 02 – Fixings replacement
| Galvanized Fixing to match the existing | 150 | Item |  |  | 0
York Glycol Chiller 03 – External case refurbishment
Price per square meter | Surface preparation - Paint coatings surrounding damaged areas shall be cleaned by approved means and ensured to be free of dust, dirt and any other foreign matter. Where oil or grease are present this shall be removed with the use of Degreaser™ W500* or similar which shall be rinsed off with clean water and allowed to dry. Areas of damage which exhibit surface rusting shall be prepared by mechanical means to ensure all residual rust is removed to BS EN ISO 8501-1:2007 Grade St3. Surrounding paint coatings shall be removed back to a firm sound edge and then feathered over a distance of 50mm in the region of the affected area. | 33 | Sqm |  |  | 0
| Spot coat - - Macropoxy™ M902 Winterfast Hi-Build Brushing Aluminium or equivalent | 6 | Sqm |  |  | 0
| Surface Tolerant Primer - - MACROPOXY TM M902 Primer or equivalent | 33 | Sqm |  |  | 0
| Undercoat - MACROPOXY TM M905 Epoxy Undercoat/Mio or equivalent | 33 | Sqm |  |  | 0
| Finish Coat - ACROLON™ C137V2 Special Finish or Equivalent | 33 | Sqm |  |  | 0
York Glycol Chiller 03 – Condenser Wire Grills replacement
| Wire Enclosure Top Section - 200 | 10 | Item |  |  | 0
| Wire Enclosure Bottom Section - 200 | 6 | Item |  |  | 0
| Wire Enclsure Bottom Section - 201 | 2 | Item |  |  | 0
York Glycol Chiller 03 – 25mm Spring isolator replacement
| 25mm Spring isolator – Part number – 029-24583-011 or similar | 8 | Item |  |  | 0
| 25mm Spring isolator – Part number – 029-24583-008 or similar | 2 | Item |  |  | 0
York Glycol Chiller 03 – Fixings replacement
| Galvanized Fixing to match the existing | 150 | Item |  |  | 0
PROVISIONAL SUMS
| Allow for the following Provisional Sums to be expended at the direction of the Contract Administrator or deducted in whole or in part if not required: Building Works - Provisional sum for unidentified additional replacement parts | 1 | Total |  |  | 0
Preliminaries and General Conditions
| Local Authority Fees | 1 |  |  |  | 0
| Liaison with local and statutory authorities | 1 |  |  |  | 0
| Parent Company Guarantee | 1 |  |  |  | 0
| Considerate Constructors Scheme | 1 |  |  |  | 0
| Insurances | 1 |  |  |  | 0
| Management - Contracts Manager | 1 |  |  |  | 0
| Management - Site Manager / Agents | 1 |  |  |  | 0
| Managament - M&E Co-ordinator | 1 |  |  |  | 0
| Management - Quantity Surveyor | 1 |  |  |  | 0
| Management - Other, please state: | 1 |  |  |  | 0
| Labourers | 1 |  |  |  | 0
| Accomodation and Welfare Provisions - Contractors | 1 |  |  |  | 0
| Services and Facilities | 1 |  |  |  | 0
| Catering for Site Meetings | 1 |  |  |  | 0
| Power and Lighting for works | 1 |  |  |  | 0
| Water for works | 1 |  |  |  | 0
| Plant | 1 |  |  |  | 0
| Internal Access Scaffolding | 1 |  |  |  | 0
| External Access Scaffolding | 1 |  |  |  | 0
| Temporary Works - formation of Site Access and Site Compound | 1 |  |  |  | 0
| Temporary Works - other required form the works, please state; | 1 |  |  |  | 0
| Heras fencing to form Contractors Compound and Other Working Areas | 1 |  |  |  | 0
| Maintain access throughout the Works | 1 |  |  |  | 0
| Fire fighting equipment and signage for Fire exit routes | 1 |  |  |  | 0
| Site Name Board | 1 |  |  |  | 0
| Photographic condition survey | 1 |  |  |  | 0
| General Protection | 1 |  |  |  | 0
| Protection of pavements and roads | 1 |  |  |  | 0
| Reinstatement to area of Site Access and Site Compound | 1 |  |  |  | 0
| Samples | 1 |  |  |  | 0
| Disposal of rubbish and debris | 1 |  |  |  | 0
| Final cleaning | 1 |  |  |  | 0
| Other preliminary items. Please state; | 1 |  |  |  | 0
| Sundries | 1 |  |  |  | 0
0
All costs appearing here are for information only and will not be scored as part of AW5.2 Pricing Schedule Evaluation
Item Number | Description | Quantity |  | List Price | Discounted Price | Total Price
1 | All works to be completed in normal working hours 07:00 - 16:00 |  |  | 0 | 0 | 0
2 | All works to complete outside of normal working hours 16:01 - 06:59 |  |  | 0 | 0 | 0
TOTAL | [5 empty] | 0