PREPARATION OF EXISTING HELICOPTER LANDING SITE WITH UTILITY SERVICES AND DRAINAGE SYSTEM WITHIN NYATI BARRACKS

BRITISH ARMY TRAINING SUPPORT UNIT KENYA (BATUK)

BOOKLET 3 SPECIFICATION LUMP SUM FIRM PRICE CONTRACT FOR KEN/GE/2104 PREPARATION OF EXISTING HELICOPTER LANDING SITE WITH UTILITY SERVICES AND DRAINAGE SYSTEM WITHIN NYATI BARRACKS BRITISH ARMY TRAINING SUPPORT UNIT KENYA (BATUK)

# Contractor’s Design

# The Contractor is to advise the authority of all design consultants / Sub-contractors who will be employed on this Contract and the areas of their design responsibility.  Any Works undertaken without prior issue of full information for the necessary approvals will be entirely at the Contractor’s own risk.

# The Contractor shall not commence any work in accordance with any Design Document until the authority has agreed the relevant Design Document.  The Contractor shall keep one copy of each Design Document on the Site, to which the authority or his representatives may have access at all reasonable times.

# Design Responsibilities

# Contractor’s Design Responsibilities.   The Contractor is responsible for the design of all elements contained within the Schedule of Works.  Where required, all designs are to be submitted to the Authority for concurrence and authorisation prior to implementation of Works.  Where the nature of Works does not warrant full design, a descriptive proposal complete with proposal sketch must be submitted for concurrence.

# The Contractor shall ensure all designs are in accordance with and include the applicable requirements as contained within References and all other design documents specified within these specifications.  NOTE: These references are provided as guidance and minimum requirement only; the responsibility remains with the Contractor to ensure that all design and construction Works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the Works, geography, climate, environment and Theatre of operations.  Where there are conflicts between the Contractor’s design drawings and the Specification (Booklet 3) the Performance Specifications (PS) will take precedence in all cases.  Any queries should always be addressed to the Authority in the first instance.  The references and specified British Standards (BS) / Euro Norms (EN), within this PS are to be used (or similar Authority approved standards) as a minimum standard, throughout the Works.

# UK Building Regulations.  All Works shall comply with the latest UK Building Regulations.  Should any variation be required, approval from the Authority shall be obtained in writing prior to the commencement of any Works.

# Health and Safety (H&S).  All Works shall be carried out in accordance with the Health And Safety At Work Act 1974 (HASAWA 74).  The Contractor shall submit a Construction Phase Plan (CPP) to the Authority for approval, including but not limited to all risk assessments, method statements, hazardous material procedures.

# Construction Drawings.  All Works shall be constructed in accordance with the final approved Contractor furnished construction drawings (or written proposal in this case).  Where a conflict in design is found, authorisation shall be obtained in writing prior to any changes in design.  No construction shall commence prior to obtaining written approval of the final construction drawings / proposal by the Authority.

# Design Life.  The design life of all new fuel and structural components and assemblies to first major overhaul, repair or replacement shall be a minimum of 25 years.  The Contractor shall supply and install all components, elements and systems / structures to satisfy this requirement, and any additional Contractual requirements that may apply.

# Existing Services.  The Contractor is responsible for ensuring all services on or adjacent to the site that will be affected by the Works are identified, located and appropriate action taken to prevent damage before work commences.  The Contractor shall ensure that any existing services and concrete slabs are reinstated to a condition similar to the existing, with the minimum of disruption to existing facilities and services during construction.  All Works that could possibly influence existing services may only commence with written approval. The Authority must be informed immediately if any unknown services are discovered that will have an impact on the Works.

# The Contractor shall ensure that any existing services and affecting Works – including all connections and services tied into – are of an acceptable standard to ensure the required performance over the life of the facility.  Should it be found that one or more of the services (including but not limited to existing water, sewerage, drainage and electrical reticulation) is not considered acceptable to the requirements, the Contractor shall inform the Authority and obtain written approval / instruction prior to taking any actions to rectify or make good the pertinent unacceptable situation.

# Construction Preliminaries

# Existing Ground Conditions.  The Contractor is responsible for confirming the existing ground conditions, which are to be considered whilst designing and compiling the CPP.

# Obstructions.  As the proposed Works are to be carried out around existing infrastructure and surrounding areas, there are obstructions in the form of fences, roads and buildings etc, the Contractor is to review the site before commencing Works.

# H&S Restrictions, Precautions and Monitoring.  The Contractor shall implement the requirements described in the HASAWA 74 to protect members of the public and persons visiting the site from risks arising from the use of equipment, materials or substances defined therein.

# Control of Noise and Vibration.  The Contractor shall comply with the recommendations for practical measures to reduce noise set out in BS 5228-1:2009+A1:2014

# It is expected that the Contractor will not require a forward resources area other than the site. Should one be required a location shall be made available, as agreed by the authority.  Packaging shall be to a good standard capable of withstanding transportation and handling loads.  The Contractor shall be solely responsible for storage and movement of all equipment to site.  The Contractor shall always remain responsible for the security of equipment including prevention of theft.

# Proposed Works

- Key Project Details:  The key project details are shown below:

| Contract title: Site location: | KEN/GE/2104. Preparation of existing helicopter landing site with utility services and drainage system. NYATI Barracks |
| --- | --- |
| Proposed start date: | 23 Aug 21 |
| Proposed completion date: | 30 Nov 21 |
| Design life: | 25 years |

- Background: NYATI barracks in Nanyuki has an existing HLS. The site is an open aggregated area where helicopters land in and out of NYATI barracks. There is a requirement to make the site permanent by constructing offices, service hangar, fuel tanker holding area, ablution and parking areas which will be constructed after this phase of the project. The HLS area has no utility connections currently. In order to make the site operational with the mentioned facilities in the future, there is an initial requirement to provide utilities within the area and connect them to the existing services within the NYATI barracks. The services to be provided include:

  - Storm water connection

  - Potable water

  - Electrical power

  - Sewer.

- Contract Deliverables: There is a requirement to provide services to the HLS area to allow for the final termination into the facilities that will be constructed in future as an operation base for helicopters flying in and out of British Army NYATI barracks in Nanyuki. Below is a summary of the contract deliverables for this contract:

- Task 1 – Construction of an Oil Water Interceptor (OWI) to act as a catchment for storm water and any accidental oil spillage at the HLS within NYATI barracks and to connect to the existing open storm water drain.

- Task 2 – Supply of electrical power to the HLS from MDU3 within NYATI barracks.

- Task 3 – Supply of potable water from the Forward Mounting Base (FMB) area potable water ring main to a new Inspection Chamber (IC) at the HLS within NYATI barracks.

- Task 4 – Installation of a new sewer line to link the HLS sanitary facilities to the existing barracks main sewer line.

Task 1

Oil Water Interceptor (OWI) construction – NYATI Camp HLS

- Construction of OWI in NYATI barracks at proposed location shown in the Dwg No DIO(K)2104/ME/HLS/001 to contain any spillage from the HLS.

Requirements

- Currently the HLS has no OWI. In order to comply with Joint Service Publication 317 (JSP317) and UK regulations there is a requirement to install a suitable sized OWI.

Scope of Works

- The scope of work shall be carried out in conjunction with the specification:

  - Marking out and excavation.

  - Construction/installation of OWI chambers linked to the constructed inlet inspection manhole through pipe work approximately 15m distance

  - Construction of an inlet inspection manhole approximately 15m distance from the OWI.

  - Linking the interceptor outlet pipe to the existing storm water system. Approximately 30m distance.

  - Installation of chamber covers.

  - Installation of the interceptor overfill monitoring system.

  - Back filling of the excavated areas and appropriately reinstating the disturbed areas.

  - Testing and commissioning of the system.

Performance Specifications

- The following will need to be considered in the contractor’s design:

  - The OWI to be designed must be a forecourt separator type as per BS EN 858-2:2003. A forecourt separator must be a ‘full retention’ separator, large enough to serve the catchment area (HLS) and have an enough oil storage volume to retain any unforeseeable spillages.

  - The OWI is to be a class 1 separator. Class 1 separators are designed to achieve a discharge concentration of less than 5 mg/litre of oil under standard test conditions. These separators are required for discharges to surface water drains.

  - The Nominal Size (NS) of the OWI is to be obtained using the formula: NS = 0.018 x A (in m2) where A is the catchment area. The catchment area is to be assumed to measure 50m X 80m but must be confirmed prior to procurement.

  - The interceptor walls are to be made of impermeable material which should be able to withstand the liquid pressure when full.

  - The interceptor walls, pipes and the covers are to be resistant to acid corrosion. The covers should be lockable.

  - The interceptor is to have a coalescing device which draw the oil droplets together and facilitates separation.

  - The interceptor is to be fitted with an automatic closure device that will prevent flow passing through the separator when the quantity of the oil in the separator exceeds the oil storage volume.

  - The interceptor is to be fitted with a robust device to provide a visual warning when the oil level reaches 90% of the oil storage volume under static liquid level conditions.

  - There will be a fuel tanker with an assumed capacity of 18,000 litres on site throughout. The site will have two helicopters at a time and the assumed fuel capacity of each helicopter is not more than 500 litres.

  - The interceptor is to be vented with the correct pipe size and should be 2.4m minimum in height from the floor level with an elbow facing down at the top.

  - The interceptor is to be marked with a durable, visible label marked indelibly with the following information;

    - Manufacturer’s reference number and year of manufacture.

    - Oil storage capacity.

    - Volume of separator.

    - Type of the separator.

    - Oil level warning device details.

    - Class of separator.

    - Automatic closure device details.

    - Nominal size.

  - Any electrical device used within in the interceptor must be intrinsically safe and certified to a suitable explosion protection standard. Any control panel must be located within a safe area and conform to the requirements of BS EN 60079-10

Task 2

Electrical Power Supply – NYATI barracks HLS

- Electrical power supply in NYATI barracks to supply the HLS in order to enable the operation and maintenance of the helicopters, as shown on the Dwg No DIO(K)2104/ME/HLS/001

Requirements

- Currently the HLS has no electrical power supply. The HLS will require an electrical power supply for operation.

Scope of Works

- The scope of work shall be carried out in conjunction with the specification.

  - Marking out the required area.

  - Excavation for cable trenches as shown on drawing No. DIO(K)2104/EM/HLS/002

  - Laying of the armoured cable as per BS7671:2018 Regulation 522.8.10 and terminating it on the existing Main Distribution Unit (MDU) 3 and the newly installed 3-phase BS630A type SAIF feeder pillar. Approximately 220m distance.

  - Supply and Installation of BS630A type SAIF feeder pillar as per spec 34 and specification 39.

  - Mounting the SAIF feeder pillar, as per the feeder pillar manufacturer literature.

  - Back filling of the excavated areas and appropriately reinstating the disturbed areas.

  - Testing and commissioning of the installation.

Performance Specifications

- The following data will need to be considered in the contractor’s design.

  - The main power supply armoured cable size should be sized, considering the following:

    - The conductor type – copper

    - Phases – 3 Phase

    - Nominal voltage - 415Vac

    - Installation method – direct in ground

    - Configuration – 4core armoured cable.

    - Load – 125Amps.

    - Cable length – 300 meters.

  - The power cable is to be supplied with a separate Circuit Protection Conductor (CPC).

  - All electrical cable supplied should be East African Cables (EAC) manufactured and the colour code should be as per BS767:2018 or as approved by the authority.

  - It is assumed that the office space and ablution will be used by a maximum of 10 persons at any given time.

  - The supplied Merlin Gerin SAIF Outdoor Feeder Pillar should include the below specifications along with and specification 39.

    - Rated insulation voltage - 690V

    - Rated operational voltage - 415V

    - Rated operational current to of duty AC22B of IEC 60947-3 and BSEN 60947-3Tested load make and break current (A) – 600

    - Rated operational performance in accordance with AC22B of IEC 60947-3 and BSEN 60947-3, tested load make and break current (A)" - 2400 at 436V and 0.65 p.f.

    - Rated fused short circuit current Through fault and make onto fault Single pole IEC 60947-3 and BSEN 60947-3 – 50.

    - Rated fused short circuit current Three phase through fault IEC 60439 (kA) – 50

    - Degree of protection - IP2X doors opened and IP65 door closed.

    - Busbar Rating (A) – 600.

    - Number of outgoing ways (3 Phase supply) – 4.

    - Carrier types - 630BS.

    - Fuse type - IEC60269-2-1 SECTVI (92mm).

    - It is to be lockable and made of material as per specification 39 for outdoor use.

  - Construction of a C30 concrete plinth for mounting the SAIF feeder pillar, as per the feeder pillar manufacturer’s literature.

  - Where the power cable is not able to achieve the minimum separation distance between water pipes and power cables, the cable shall be run on a duct.

  - The cables are to be buried at a minimum depth of 600mm and appropriately covered all round with fine sieved sand as specified in the Defence Estates Specification 34 and as shown on the drawing No. DIO(k)/2104/MECH/HLS/002.

  - All road crossings are to be ducted to allow any future changes without having to break the concrete road again. The road will be reinstated to its original state or better. A minimum of concrete strength C30 shall be achieved.

  - The SAIF feeder pillar is to be marked with a visible label that is durable showing the SAIF feeder pillar number.

  - The SAIF feeder pillar is to be protected from being knocked by moving machines by erecting steel/concrete bollards around it. With the following minimum specifications.

    - Made of steel pipe infilled with concrete.

    - Pipe to be a minimum of 4-inch diameter.

    - Minimum height of 1 meter from ground level.

    - 1 meter clearance from the feeder pillar.

    - Concreted on the ground.

    - To be painted with black and yellow stripes.

Task 3

Potable Water Supply – NYATI barracks HLS

- Potable water supply in NYATI barracks to supply the HLS in order to enable the operation of the site. As per the drawing No. DIO(K)2104/ME/HLS/001.

Requirements

- Currently the HLS has no potable water supply. The HLS will require a potable water supply for operation.

Scope of Works

- The scope of works shall be carried out in conjunction with the specification:

  - Marking out the required area.

  - Excavation of the water pipe trenches as shown on the drawing No. DIO(k)/2104/MECH/HLS/002.

  - Laying of the water pipe from the existing wash down point water tank inlet pipe by constructing a new Inspection Chamber (IC) at the tap off point and terminating in the newly IC at the HLS which will be approximately 190m away.

  - Supply and Installation of necessary isolation valves.

  - Construction of the ICs.

  - Back filling of the excavated areas and making good all disturbed surfaces.

  - Testing and commissioning of the system.

Performance Specifications

- The following data will need to be considered into the contractor’s design.

  - It is assumed that the office space and ablution will be used by a maximum of 10persons at any given time.

  - The pipe should be HDPE buried a minimum of 1200mm below the ground and appropriately covered all round with fine sieved sand as shown on the drawing No. DIO(k)/2104/MECH/HLS/002.

  - The water supply pressure is to be at least 2 bars at the terminal point.

  - The tap off point is supplied using an HDPE pipe of 63mm diameter and a flow rate of about 210litres per minute.

  - All road crossings are to be ducted to allow any future changes without having to break the concrete road in the future.

  - The IC is to be big enough to allow maintenance of the system and it should be marked with a visible label that is durable showing the IC number.

  - The IC is to be provided with a lockable lid which should be able to withstand adverse weather conditions experienced in Nanyuki and painted with appropriate paint which will withstand external weather conditions.

  - The IC should also be impermeable to raising water table which is experienced within NYATI barracks and should have access steps depending on the IC depth.

Task 4

Sewer system supply – NYATI barracks HLS.

- Sewer system supply in NYATI barracks to supply the HLS in order to enable the operation of the site as shown on the drawing No. DIO(K)2104/ME/HLS/001.

Requirements

- The HLS has no sewer connection, so it will require a sewer line for operation. The line is to be connected into the existing camp sewer system. The system should be as per BS EN 752:2017.

Scope of Works

- The scope of work shall be carried out in conjunction with the specification:

  - Marking out the required area.

  - Excavation of the sewer pipe trenches.

  - Laying of the sewer pipe and terminating it on the existing camp sewer manhole number 2 depending on the levels and the to be constructed sewer manhole at the HLS. Approximately 450m distance.

  - Construction of the necessary sewer manholes approximately 50m apart.

  - Construction/provision of a sewer break tank.

  - Construction of concrete plinth a minimum of concrete strength C30 to fit the supplied the control panel as per manufactures literature.

  - Supply and installation of a duty and standby sewer pump complete with automated controls.

  - Back filling of the excavated areas and making good disturbed areas.

  - Testing and commissioning of the system.

Performance Specifications

- The following data will need to be considered into the contractor’s design.

  - The sewer system should be able to support the following.

    - A kitchenette within the office which will have grey water from the kitchen sink.

    - An ablution comprising of the ladies’ and gents’ sides.

  - It is assumed that the ablution will have a maximum occupancy of 10 persons.

  - Each manhole is to be big enough to allow maintenance of the system and is to be marked with a visible label that is durable showing the manhole number.

  - The manhole walls are to be impermeable and strong enough to withstand the sewer pressure in case of a blockage on the line.

  - The pipe gradient on the gravity drain section shall achieve a minimum slope of 1:100.

  - Manhole covers are to be fit for purpose, withstand adverse weather conditions and be airtight.

  - The breaker tank is to be properly sized to hold the waste as per BS EN 752:2017. The sewer pump delivery pipe should be fit for purpose and withstand expected pressure.

  - The sewer pump is to be fit for purpose to be able to pump sewer black water. The system shall have a duty and a stand-by pump. With the below specifications as a minimum:

    - The pump shall have a moisture detector to safeguard the motor.

    - The motor enclosure is to be IP68.

    - Self-cleaning mechanism to prevent clogging of the impellers.

    - Able to pump large size particles.

  - The pump control unit is to be IP 68 rated. It is to be mounted on a reinforced concrete plinth.

  - Electrical works is to be carried out as per BS 7671:2018.

  - The pumping breaker tank is to be protected with steel/concrete bollards to avoid being run over by vehicles. With the following minimum specifications.

    - Made of steel pipe infilled with concrete.

    - Pipe to be a minimum of 4-inch diameter.

    - Minimum height f 1 meter from ground level.

    - 1 meter clearance from the feeder pillar.

    - Concreted on the ground.

    - To be painted with black and yellow stripes.

General Points for the Entire Task

- Inspection and Test Procedure.  The inspection and testing of the new installation shall include the following:

  - Visual inspection.

  - Test in accordance with the standard test procedure as per BS and EN for each task.

- Trenching.  No work shall commence until the Authority has taken all reasonable steps to ensure that the area is free of all cables, drains and other services.  Cable Avoidance Tool (Cat) and Signal Generator (Genny) or any other equivalent cable detector tools shall be used to detect services.  Unless otherwise indicated the following is required.

  - Excavations within 600 mm of existing services shall be by hand digging.  Any damage to services shall be reported immediately to the Authority.  No repairs or replacement shall be done unless the Authority gives approval.  All works will be at the Contractors expense.

- Commissioning.  The Contractor shall be responsible for carrying out all inspection and testing. The Contractor is to complete their required sections of the commissioning forms and present them to the Authority.

- All Works shall be carried out maintaining Safe System of Work (SSOW) practices as per JSP 375 Part 2 Vol 3.

- Existing Services and Facilities.  It is the Contractor’s responsibility to conform to the following:

  - The Contractor is responsible for ensuring all services or facilities on or adjacent to the site including public roads approaching the site, that may be affected by the works are identified and that appropriate action is taken to prevent damage occurring before work commences.  Liaison between adjacent sites is essential where any activity on the site or on an adjacent sites are identified which may have an impact on the project or which may be impacted upon by the project the Authority is to be informed in writing at the earliest opportunity (e.g. services requiring redirection).  If damage is incurred, it will be the sole responsibility of the Contractor to rectify to the Authorities given standard.

  - All works that could possibly influence existing services may only commence upon receipt of appropriate written documentation (e.g. Statement of known services), a copy of which must be provided to the Authority.  The Contractor must discuss in advance with the Authority which specific agencies it will need to obtain approvals and documentation from (e.g. NEMA etc.).  Obtaining any such approvals and documentation is the Contractor’s responsibility.

  - Upon request, and subject to security caveats, the Contractor may have access to all relevant existing drawings relating to the contracted works on the site, held by the Authority.  During the tender stage, the Contractor shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

  - The Contractor shall conduct a detailed site investigation and ensure that any existing services which are to be tied in to are of an acceptable standard to ensure the required performance over the life of the new facility.  Where it is found that an existing service (including, but not limited to water, sewerage, drainage and electrical power) is not adequate for the project requirements, the Contractor shall inform the Authority and obtain written instruction prior to taking any remedial action.

  - Where the proposed works interact with any existing facilities and defects are found in said facilities this shall be reported to the Authority without delay.  Instructions must be obtained from the Authority before proceeding with work which may cover up, or otherwise hinder access to, the defective construction, or be rendered abortive by carrying out of subsequent remedial work.

- Setting Out.  The Contractor is responsible for all setting out and for all on-going monitoring of line, level and accuracy as works progress

- Communication will be the key in planning and conducting concrete works, excavation works, design works, final connection, and new connections to the existing systems, and during commissioning.  Therefore, contractor must communicate with the authority in timely manner.

- All personnel employed to work on the above tasks should be suitably qualified and must have their CV submitted to the authority.  They may also be interviewed by the authority to confirm their competency.

- Before any work is performed, pertinent risk assessments and method statements should be issued to the authority.  The authority will then issue the appropriate permits to work if required. The contractor must seek Statement of known hazards from the authority prior starting and excavation on site.

- All detailed design drawings, pipes sizing calculations, cable sizing calculations, interceptor sizing, drainage sizing, concrete mixing ratios, materials safety data sheets and samples for materials are to be submitted to the authority for approval beforehand.

- Authority will issue the necessary paperwork for transportation of goods in the camp e.g. gate pass.

- Any Scaffolding ladders to be used in the tasks are to be serviceable and where required presented to the Authority for inspection and permission to use.

- Any electrical works will be carried out as per BS 7671-18.

- Under no circumstances will trench digging works be carried-out without gaining statement of known hazards from the authority.

Restrictions / Constraints

- Access to the Site.   This is to be agreed in detail with the PM prior to start on site.  Passes may be required, and the contractor should submit the details and ID of any technicians that will be working on the contract within the tender return.

- Notice.  The contractor is to provide notice to the authority in writing (or through email), before a minimum of 3 working days prior to the work on site.  The notice must include the date and expected time of arrival, name and ID No of the workforce, and contact telephone no for both the contract manager and the workforce.

- Working Hours.   The contractor may choose to work in his/her suitable hours; however, assistance from the authority will only be available 0800-1600 hrs Mon – Fri.  For any assistance from the authority, the contractor must submit request with a minimum of 24hrs notice.

- Permits to Work.  Permits to work applicable for this task are as follows:

  - Statement of Known Services.

  - Working at Height.

  - Confined Spaces.

  - Electrical connection permit

Annexes:

A.	Generic Points - Pre-Contract

B.	Generic Points - Pre-Construction.

C.	Generic Points - During construction.

D.	Generic Points - Post construction.

Drawings.

DIO(K)/2104/EM/HLS/001  PROPOSED HLS UTILITIES TOWN PLAN.

DIO(K)/2104/EM/HLS/002  PROPOSED COMBINED SERVICE TRENCH DETAIL

Annex A to

Contract/KEN/GE/2104/BK/3/Spec

Dated 28 May 2021

Generic Points - Pre-Contract

Designers

- This project is a Design and Build contract, meaning the contractor must fulfil the role of both the designer, and the Principal contractor.  The design work must be carried out by a qualified and competent person.  The contractor shall ensure all designs are in accordance with, and includes the applicable requirements contained within references and all other design documents specified within this PS.  If the contractor is not competent to carry out some aspects of the design work, a qualified person or consultancy firm should be sub-contracted to carry out that portion of the work.  The Contractor is to inform the authority of all design consultants/sub-contractors who will be employed in this project and the areas of their responsibility.

- Where design work is required to be carried out by a professionally qualified person, details of their qualifications and experience, registration with the Engineers Board of Kenya and copy of their professional indemnity insurance needs to be submitted to the authority.

- Pre-Construction Information (PCI).  All the pre-construction information is contained within this Booklet 3. If any additional information is required, the contractor is to request a copy in enough time to affect any changes prior to tender submission.

Contractor’s Design

- The contractor is to ensure that their design meets the parameters outlined within this Specification.

- Site Visit.  The Contractor shall acquaint himself completely with the exact conditions relating to access and site environment, along with the layout, conditions and positions of the existing services, the full extent of the works required, and the supply and conditions affecting labour, carriage, carting, unloading, storage, tools, scaffolding etc. as well as any security and access constraints.

- Existing Ground Levels.  The Contractor shall confirm or identify all existing site levels required prior to any construction works.

- Ground Water Level.  The ground water level has not been established but it is not expected to impact on any of the works.  It is the Contractors responsibility to consider the ground water levels when submitting technical and commercial proposals.

- Existing record drawings.  The Contractor will upon request, be supplied with copies of all available and relevant as built drawings.  The Contractor during tender stages shall fully acquaint himself with the nature and extent of all existing services within the area of the contract works.

- The responsibility remains with the Contractor to ensure that all design and construction works comply with the latest methods, requirements and guides, and generally accepted practice as relates to the works, geography, climate, and environment.  Where there are conflicts between the design drawings and Detailed Specification the Detailed Specification will take precedence in all cases.  Any queries should always be addressed to the Authority in the first instance.

Use of Design Codes and Specifications

- All designs must conform to the most current editions of BS or EN.  Other Design Codes may, on occasion, be used if they meet the minimum requirements and the Contractor shall submit proof of equivalency to the Authority for approval of use.  The Authority can be approached for clarification of the relevant BS if required.  On no account is the contractor to use any design information other than that stated or approved by the Authority.

- All Contractors will be required to certify their designs for conformity to the specification and to the relevant BS/EN.  Only appropriately qualified and experienced engineers are to certify the designs.

  - Design Conformity.  The design engineer is to produce a letter to state that the design conforms with all applicable legislation, most current editions of BS or EN, and best practice.  The letter is to have the company header (of the design agency if sub-contracted) and to be signed by the lead designer with his name, contact details and qualifications detailed in the signature block.

  - Construction Inspections.  Prior to the start of construction, the contractor, designer and authority shall agree key stages at which the works are to be inspected by the designer for compliance with the design.

  - Build Conformity.  At the end of the project, the lead designer is to confirm in writing that the works have been built correctly, in accordance with his design.

- Design Life.  The design life of all new works to first major overhaul, repair or replacement is 25 years.  The Contractor shall supply and install all components, elements and systems/structures to satisfy this requirement and provide documentary evidence.

Annex B to

Contract/KEN/GE/2104/BK/3/Spec

Dated 28 May 2021

Generic Points - Pre-Construction

Detailed Design and Planning

- Additional Design Information.   The Contractor is to submit any additional design information to the Authority prior to commencement of the construction phase.  The authority will examine design documentation and shall be entitled to reject a design as unsatisfactory where it is not in accordance with the specification, statutory regulations or if it would be unfit for purpose.

- A copy of all construction drawings is to be provided by the Contractor to the PM prior to commencing Works.  Amended or updated drawings are to be provided as necessary.  The minimum design information to be provided by the Contractor shall include the following:

  - Any additional design calculations for the works.

  - Any additional general layout plans for the site and the structures.

  - Any additional detailed structural design, calculations and drawings.

  - Any additional foundation plans shall (as a minimum) indicate: all footing locations and dimensions, screeds and / or ground slabs or plinths, as applicable.

  - Any additional services layouts and calculations.

  - Any additional detailed Electrical, Mechanical drawings and calculations.

  - Manufacturer product details including safety data sheets.

  - Designers risk register.

  - Project Programme to be regularly updated or upon request by the Authority and provided electronically on Microsoft Project or equivalent in a regularly basis or on request.

Design Responsibilities (under CDM)

- The designer has the following responsibilities under CDM 2015:

  - Eliminate Hazards and Risks During Design.  Designers are to analyse the risks posed during the construction, daily use, maintenance and ultimate demolition of the facility.  Once identified, these risks should, where practicable, be designed out.

  - Provide Information on Remaining Risks.  Remaining risks after the design process are to be compiled onto a designer’s risk register and submitted with the final design.

Provision of Information

- Unless otherwise specified the following is to be provided:

  - Three copies of all information, including valid certification, in respect to work, goods and materials proposed by the Contractor, shall be supplied to the Authority.  Where the original document is written in a language other than English, it shall be accompanied by an English translation.

  - Information and certificates shall be supplied at least two days prior to the use of the work, goods or materials in the Works.

  - Three copies of detailed working and fabrication drawings and calculations shall be submitted to the Authority for reference purposes.  Such submittal shall in no way relieve the Contractor of his responsibilities for the work under the contract.

- The Authority reserves the right to request copies of all calculations and drawings for analysis prior to the commencement of any construction on site.  The contractor will provide copies of all calculations and ‘As Built Drawings’ for the Health and Safety File.

- The signed and approved drawings shall be used as the construction drawings on site for all work purposes and to satisfy the requirements as specified by the Construction, (Design and Management) Regulations 2015 (CDM 2015) & appropriate ACOP.

Construction Phase Plan

- Under the requirements of CDM, the contractor is to prepare a construction phase plan detailing how they will safely conduct the works.  Risk assessments are to be included for all elements of work and method statements are required for any works that are out of the ordinary or high risk.  The Construction Phase Plan must cover the following area’s (where applicable):

  - Safety Risks:

    - Protecting the public.  The public is any persons not involved in the works.  Particular attention should be paid to area’s where children are likely to have access to the site outside of working hours.

    - Traffic routes.  Traffic routes for delivery of stores and equipment should be clearly highlighted and controlled.  Movement of plant and machinery on site should be organised in a way that minimises risk to the workforce and any visitors to site.  Care must also be taken to minimise risk from existing traffic routes.

    - Existing buried and overhead services.  Some of these may be identified in the permit to dig process, however care must be taken to identify and avoid any damages on existing services.

    - Adjacent land use.  The use of adjacent land and properties will affect the level of protection for things such as noise and dust suppression etc.

    - Stability of nearby structures.  Care must be taken that works do not affect the stability of nearby structures.

    - Demolition works.  Demolition work is a particularly dangerous task and careful planning must be conducted.  Method statements for all aspects of demolition will be required by the authority.

    - Work equipment.  Work equipment must be calibrated where necessary, inspected and is to be in a suitable condition not to cause a hazard on site.

    - Electrical safety.  Electrical works will be conducted in accordance with the JSP and CDM recommendations.

    - Preventing falls.   Falling from height is one of the biggest killers in the construction industry.  Even when not working under a permit, it is expected that the correct equipment and management methods are utilised to prevent falls.

    - Working with or near fragile materials.  Fragile materials should be identified prior to work commencing and appropriate action must be taken.

    - Control of lifting operations.  Lifting operations are to be carefully planned and controlled on site.

    - Excavations / confined spaces.  All excavations inside buildings where work is to be conducted are to have the appropriate level of shoring / protection.  Where an area is deemed a confined space, a permit may need to be issued to control the works.  If permit is not issued, the contractor is to have a suitable system in place with appropriate paperwork i.e. risk assessment and method statements associated to the work being carried out.

    - Working on or near water.  If working on or near water the contractor is to plan the works to minimise the risk drowning.

  - Health Risks:

    - Temperature / weather protection.  Protection from the elements for the workforce.

    - Substance misuse.  The misuse of drugs or alcohol by the workforce.

    - Manual handling.  Correct lifting techniques, lifting equipment etc.

    - Dust.  Dust suppression and removal.

    - Noise.  Reduction and suppression of noise.  Management of timings for noisy activities etc.

    - COSHH.  The correct storage and use of hazardous substances.  Appropriate protective equipment must be worn when handling COSHH materials.  Safety data sheets must be available on site at all time.

    - Asbestos.  Identification and appropriate management of Asbestos.

  - Provision of:

    - Welfare facilities.  Water, food, shade, toilet facilities etc.

    - First aid.  There should always be at least one qualified first aider with appropriate medical equipment on site.

    - Emergency procedures.  Procedures for response to incidents such as Fire, major and minor injuries, security incident etc.

    - Reporting of accidents, incidents or near misses.  Procedure for reporting and follow-on actions to prevent re-occurrence.

    - Waste management.  Management, storage and disposal of waste and arising from the site.

    - Fire prevention, detection and firefighting.  Methods to prevent the start and spread of fire, and to identify any fire that does start. There must also be appropriate firefighting equipment available and access to the site for firefighting services.

Pre-Start Meeting.

- Prior to the commencement of any works, a Pre-Start meeting is to be held with the contractor, lead designer and chaired by a representative from the authority.  The following topics are to be discussed as a minimum:

  - Mobilisation plan

  - Site setup

  - Health and safety

  - Required permits

  - Access and security

  - Programme

Annex C to

Contract/KEN/GE/2104/BK/3/Spec

Dated 28 May 2021

Generic Points - During Construction

Facilities/Temporary Works/Services

- Locations.  The Contractor is to agree with the PM of the intended siting of all spoil heaps, temporary works and services in advance.  The Authority shall verify with the Contractor which site features are to be removed and protected during construction works.

- Survey and Setting out.  The Contractor will be responsible for all setting out and levelling during construction.  The Contractor shall keep updated schedules and drawings of all benchmarks used in setting out of the site; these must be made available to the Authority when required.  A minimum of 2 survey control stations are to be constructed, one visible from the site at 50 m and the other 200 m away from the first but in line of site.

- Record Drawings.  The Contractor shall record details of all grid lines, setting out stations, benchmarks and profiles on the site setting out drawing.  Retain on site throughout the contract and hand to PM on Completion.

- Signage.  The Contractor shall supply and erect all applicable and appropriate signage to the site.  This shall include as a minimum all H&S signage, directions and location of site office and emergency contact details of the Contractor’s representative on site.  Temporary warning signs and careful demarcation of works areas must be undertaken with care to ensure compliance with any and all requirements.

- Lighting and Power.  The Contractor shall provide all lighting and power for his works.  No facility will exist on site from the general base infrastructure.

- Communications.  The Contractor shall provide his workforce with adequate means of communications throughout the duration of the Contract period in order to carry out the work specified.

- Temporary Services.  The Contractor shall provide temporary service connections to both mechanical and electrical systems.  All temporary service connections are to be in accordance with current UK regulations.

- Use of the Site.  The Site shall not be used for any purpose other than undertaking the specified works.  The Contractor may erect the site office and storage compound in a location agreed with the Authority.  No storage of materials, parking of vehicles, temporary accommodation or any other use of areas beyond the boundaries shall be permitted.  Under no circumstances shall it be permissible for the Contractor to cause an obstruction to normal pedestrian or vehicular movements within the vicinity of the site.

- Restrictions to the Works.  The Works are to be undertaken without interfering with every day running of the Authority’s operations within the area.  The demarcation of the Site boundary is to be obvious and clearly marked to restrict access to the Site whilst the Works are being undertaken.

Project Management

- The authority.  The Superintending Officer (SO) has overall authority on this project.  For the purpose of this specification, the SO is the only person acting on behalf of the authority, in most cases.

- The Contractor shall not commence any work in accordance with any Design Document until the authority has agreed to the relevant Design Document.

- Buried Services.   Prior to carrying out any excavation work, the Contractor must:

  - Obtain a Permit to Dig (Statement of Known Services) and all drawings relating to existing services that may interfere with the proposed works.  A copy of the Permit to Dig must be given to the Authority prior to any works commencing.

  - Identify all local services and take adequate precautions to protect such services from damage for the duration of the works.

  - Inform the Authority immediately if any unknown services are discovered that will impact on the works.

- Supervision.  The Contractor shall accept responsibility for delivery, co-ordination, supervision and administration of the Works, including all subcontracts.  They shall arrange and monitor a programme with each subcontractor, supplier, local Employer and any statutory undertaker, and obtain and supply information as necessary for co-ordination of the work.

- Site Diary.  The Contractor shall keep an up to date daily site diary.  This document is to be used to record all decisions made on site both verbally and written.  The document is also to be used to record visits to site and note anything, which has a direct effect on the project in terms of cost and extensions to time, or any other occurrence that affects the project programme.  This document will be used as the audit trail considering any disputes, concerning the project.

- Contractor’s Site Meetings.  The Contractor is to hold meetings with appropriate subcontractors and suppliers shortly before site meetings with the Authority to facilitate accurate reporting of progress.

- Site Meetings.  The authority, or his representative will hold regular progress meetings to review progress and other matters arising from the administration of the Contract.  It will be the Contractors responsibility to ensure the availability of accommodation and attend all such meetings.

- Liaison with the Authority.  The Contractor shall designate a site manager from within his organisation who will be responsible for liaising with the SO on a day to day basis and as the need arises.  At all times the Contractor shall ensure that the Site Manager presents on site that has the capability of reading, writing, speaking and receiving instructions in the English Language, including being able to understand and interpret technical drawings and specifications.  The Site Manager must be able to explain the work operations to person performing the work in a language that those performing the work are capable of understanding.  The PM shall have the right to determine, whether the proposed representative has enough technical and linguistic capabilities.

- Approvals.  Where products or work are specified to be approved or the authority instructs or requires that they are to be approved, the same must be supplied and executed to comply with all requirements.

- Access.  The Contractor shall provide at all reasonable times, access to the Works.  The Contractor shall supply the PM or his representative with copies of any documentation and drawings, which may reasonably be required for the purposes of monitoring the work performed under this or any sub-contract.

- Regulations.  It is the Contractor’s responsibility to be fully conversant with all local/MOD regulations and requirements in respect of fire, safety, security and occupational health, etc.  These are to be fully complied with throughout the contract period.

Health and Safety

- Health and Safety (H&S).  All works shall be carried out in accordance with the HASWA 74.

- JSP 375.  The contractor shall comply with the Client’s permit to work system and the JSP 375, Volume 3, (details of which are obtainable from the Authority), including the provision of method statements, risk assessments, switching/isolating safety programmes, permit to dig, etc.

Permits to Work

- Permit to Dig.  If any excavation or breaking of ground is to be carried out, the contractor must request a permit to dig at the Pre-Start meeting.  Should any excavation be conducted without a permit, the contractor may be removed from site.

- Hot Works Permit.  The contractor is to establish at the Pre-Start meeting if hot work permits will be required for his location of work.

- AP’s.  The following table shows details of Authorise Person (AP) in their respective discipline.

| Discipline | CAP | Contact No |
| --- | --- | --- |
| Electrical | Mr Ezekiel | 0722931926 |
| Mechanical | Mr Patrick | 0724405915 |
| Petroleum | Mr Ezekiel/Mr Patrick | 0722931926/0724405915 |
| Confined Spaces | Mr Mbilo/Mr Julius | 0720562961/0723236489 |
| Working at Height | Mr Mbilo | 0720562961 |

- Skilled Persons & Persons in Charge (PIC).  Any works required to be completed under a JSP 375 permit must have a dedicated PIC and the work carried out by registered skilled persons.  At the Pre-Start meeting the contractor must establish if any of his works require a permit, and if so, arrange for currently registered personnel to conduct the works, or registration of the contractor’s personnel.

- CDM 2015.  The Contractor shall submit a CPP file to the Authority for approval, including all risk assessments, method statements, hazardous material procedures etc to comply fully with Construction, Design Management Regulations 2015 (CDM 2015) & appropriate ACOP.

Quality of Work

- Quality Standards/Control.  The contractor will provide evidence to the authority of his quality standards and controls and will produce a plan detailing Quality Control (QC) activities for the authority to plan for witnessing of critical activities.

  - General Quality of Products.  All products shall conform to the following subparagraphs:

    - Products to be new unless otherwise specified by the Authority.

    - For products specified to a BS or EN obtain certificates of compliance from manufacturers when requested.

    - Where a choice of manufacturer or source is allowed for any product, the whole quantity required must be of the same type, manufacture and/or source unless otherwise approved.  Produce written evidence of sources of supply when requested by authority.

    - Ensure that the whole quantity of each product required to complete the work is of consistent kind, size, quality and overall appearance.

    - Where consistency of appearance is desirable ensure consistency of supply from the same source.  Do not use different colour batches where they can be seen together.

    - If products are prone to deterioration or have a limited shelf life, order in suitable quantities to a programme and use in appropriate sequence.  Do not use if there are any signs of deterioration, setting or other unsatisfactory condition.

  - Proprietary Products.   All products shall conform to the followings:

    - Handle, store, prepare and use or fix each product in accordance with its manufacturer’s current printed or written recommendations/instructions.  Inform authority if these recommendations/instructions conflict with any other specified requirement. Submit copies to authority when requested.

    - The tender will be deemed to be based on the products specified and recommendations on their use given in the manufacturer’s literature current at the date of tender.

  - Obtain confirmation from manufacturers that the products specified and recommendations on their use have not been changed since that time.  Where such change has occurred inform authority and do not place orders for or use the affected products without further instructions.

  - Checking Compliance of Products.  The Contractor shall check all delivery tickets, labels, identification marks and where appropriate the products themselves to ensure that all products comply with the project documents. Check that the products comply with the following sub-paragraphs.

    - The sources, types, qualities, finishes and colours are correct, and match any approved samples.

    - All accessories and fixings that should be supplied with the products have been supplied.

    - Sizes are correct.  Where tolerances are critical, measure a sufficient quantity to ensure compliance.

    - The delivered quantities are correct, to ensure that shortages do not cause delays in the work.

    - The products are clean, undamaged and otherwise in good condition.

    - Any products with a limited shelf life are not out of date.

  - Protection of Products.  All products shall be protected to ensure that they remain in the condition they are required to be in.  The contractor is to ensure that products are to be prevented from overstressing, kept clean, protected from the elements and kept in original wrappings until required for the project.

- Prohibited Products.  The Contractor shall not employ on or incorporate in the Works any of the following products and shall impose a like obligation upon all Sub-Contractors.

  - Asbestos materials as described in the Asbestos Prohibitions Regulations 1985 and the Asbestos Products (Safety) Regulations 1985.

  - Lead or any products containing lead for use in connection with drinking water.

  - Materials that are generally composed of mineral fibres either manmade or naturally occurring which have a diameter of 3 microns or less and a length of 200 microns or less or which contain any fibres not scaled or otherwise stabilised to ensure that fibre migration is prevented.

  - Other products or substances generally known to be deleterious to health and safety at the time of use or to the durability of the property in the circumstances in which they are being used.

- Hazardous, Aggressive or Unstable Materials.  The Contractor is not to import or use fill materials which would either in themselves or in combination with other material or ground water, give rise to health hazards, damage buildings or structures.  The construction materials should not include any finishes that may lead to shedding of particles.

- Defects in Existing Construction/Services.  This shall be reported to the authority without delay. Obtain instructions before proceeding with work which may be covered up or otherwise hinder access to the defective construction or be rendered abortive by the carrying out of remedial work.  This is particularly relevant in relation to the expansion of the existing service runs.

- Proposals for Rectification of Defective Work/Products.  As soon as possible after any part(s) of the work or any products are known to be not in accordance with the Contract, or appear that they may not be in accordance, the Contractor is to submit proposals to the authority for opening up, inspection, testing, making good, or removal and re-execution. Such proposals may be unacceptable to the authority and he may issue contrary instructions.

- Quality Control.  The Contractor is to establish and maintain procedures to ensure that the works, including the work of all Subcontractors, comply with specified requirements.  This is to include all testing of materials that are to be incorporated into the project (e.g. concrete).  The Contractor is to maintain full records, keep copies on site for inspection by the authority, and submit copies of parts of the records on request.  The records must include the following:

  - Identification of the element, item, batch or lot including location in the works.

  - The nature and dates of inspections by the Contractor or authority, tests and approvals.

  - The nature and extent of any non-conforming work found.

  - Details of any corrective action.

- Materials Testing.  It is the Contractor’s responsibility to carry out all materials testing and present all test results to the Authority on request and within the H&S file.  The Authority will carry out concurrence quality control material tests at regular intervals.

- Notification.  The Authority requires to be informed in writing at least 10 days in advance of any tests and commissioning being carried out.  Access must be available to the Authority to carry out testing as deemed necessary by the Authority.

Annex D to

Contract/KEN/GE/2104/BK/3/Spec

Dated 28 May 2021.

Generic Points - Post Construction

Completion / Handover

- Commissioning Period.  Within the tender submission the Contractor shall submit a Works Commissioning Plan, setting out his commissioning proposals including the preparation of handover documentation.

- Notice of Completion.  The Contractor is to provide the authority at least five days’ notice of the anticipated dates of Practical Completion of the whole or parts of the Works.

- Mechanical and Electrical Services.  Mechanical and Electrical Services must have final tests and commissioning carried out by the Contractor so that they are in full working order at Practical Completion.  This includes buried but not connected cables and pipelines.

- Timing of Tests and Inspections.  The Contractor is to agree dates and times of tests and inspections with authority four days in advance, to enable the authority and other affected parties to be present.  On the previous working day to each such test or inspection the Contractor is to confirm to the authority that the work or sample in question will be ready or, if not ready, agree a new date and time.

- Test Certificates.  The Contractor is to submit a copy of each certificate to the authority as soon as practicable and keep copies of all certificates on site.  Copies should be included in the Health and Safety File on handover of the works.

- Work at or After Completion.  The Contractor is required to undertake the following works prior to handover.

  - Make good all damage consequent upon the work.

  - Remove all temporary markings, coverings and protective wrappings unless otherwise instructed.

  - Clean the works thoroughly inside and out including all accessible ducts and voids; remove all splashes, deposits, efflorescence, rubbish and surplus materials consequent upon the execution of the work.

  - Cleaning materials and methods to be as recommended by manufacturers of products being cleaned, and to be such that there is no damage or disfigurement to other materials.

- Security at Completion.  The Contractor is to leave the Works secure with all accesses locked.  Account for and adequately label all keys and hand over to the authority with itemised schedule, retaining duplicate schedule signed by the authority as a receipt.

- Making Good Defects.  The Contractor is to decide with the authority and give reasonable notice of the precise dates for access to the various parts of the Works for purposes of making good defects.  The authority is to be informed by the Contractor when remedial works to the various parts of the Works are completed and ready for approval.

- Inspection, Testing and Commissioning.  The installations shall be tested and inspected in accordance with but not limited to the current CIBSE Codes, BS, EN where appropriate, etc.  Advance notice of tests shall be given (minimum of 7 days prior to notification).

- Test and inspection certificates are to be approved by the Authority; preferred document templates will be provided by the Authority on request.  Test certificates shall serve as a record that the item referred to has been shown under test to meet the requirements of the specifications and of BS as applicable and shall be dated, numbered and clearly referenced to the item tested by means of serial, chassis or other manufactures reference number permanently marked in a conspicuous position.

- The calibration certificates for the testing of the equipment are to be available on request to be shown to the Authority for scrutiny.  The Contractor shall ensure all calibrations are in date.  The Authority reserves the right to have an independent electrician available during the test and inspection phase.

- Any defects of workmanship, materials or non-compliance with the specifications or other irregularities which become apparent during the tests shall be rectified by the Contractor, at his own expense, until the whole work is free from defects and in full working order to the complete satisfaction of the SO.

- All materials used for construction of permanent works shall have suppliers’ specifications and/or testing certificates available.  Where materials are used as part of a whole or in conjunction with other materials, and in any case where site testing is required by best practice, verification of quality and specifications should be allowed for the parts / items / products (suppliers’ specification) as well as the whole (site testing).

- Defects Liability Period.  A defects liability period shall apply for the works as detailed above.  The Contractor will be responsible for making good at his own expense any defects in the works arising within that period.  The contractor is to ensure that a defects inspection is conducted 2-4 weeks prior to the end of the liability period in order to release the contract retention.

- Operations and Maintenance Documentation.  Upon completion of the works the Contractor shall forward all manufacturers’ details relating to equipment/materials used to the Authority for inclusion into the O&M Manual/H&S File.  Refer also to CDM 2015 & appropriate ACOP, this documentation less ‘As Built Drawings’ is to be made available at the Pre-Board of Officers not less than 10 days before the due project handover date.  A full list of snagging items shall be produced and presented to the Authority with a rectification programme at this very same board.

Health and Safety File

- Upon project completion the H&S file shall be presented to the Authority before the Board of Officers is convened and in compliance with (CDM 2015) & appropriate ACOP.

- Presentation of Health and Safety File.  The Contractor is to provide the authority with three copies of the H&S File.  The Manual is to be contained in a series of A4 size, plastic covered, loose leaf, four ring binders with hard covers, each indexed, divided and appropriately cover titled.  Selected drawings needed to illustrate or locate items mentioned in the Manual, where larger than A4, are to be folded and accommodated in the binders so that they may be unfolded without being detached from the rings.  The main set(s) of as-built drawings will form Annex(es) to the Manual.

- The Health and Safety File.  The Contractor shall be required to complete the Project Health and Safety File on completion of the works, three copies of which will be provided to the Authority at handover. Advice can be sought from the Authority if required.  The H&S File provides information required for future construction work, which includes cleaning, maintenance, alterations, refurbishment and demolition.  The Manual is to consist of the following parts, sub-sectioned as appropriate.

  - Section 1: H&S.  The Contractor is to provide a description of the site and the buildings thereon. This is to include details of construction methods and materials, which may present significant residual hazards in the future.

  - Section 2: Certificates.  The Contractor is to provide a copy of all Test Certificates (including but not limited to electrical circuit tests, start and commissioning tests) for the installations and plant, equipment, valves, etc, used in the installations. Warranty Certificates and guarantees are also to be included in this section.

  - Section 3: As-built Drawings.  The Contractor is to provide as-built drawings recording details of all construction, electrical and mechanical work. A fire strategy for the site should also be included with drawings showing emergency escape routes, location of emergency and fire fighting systems, services shut-off valves, switches, etc.

  - Section 4: Operation & Maintenance (O&M) Schedules.  The Contractor is to provide recommendations as to the preventative maintenance, frequency and procedures to be adopted to ensure the most efficient operation of the systems. Manufacturer’s O&M schedules are to be included. Diagrammatic drawings of each system indicating principal items of plant, equipment, and valves are also to be included.

  - Section 5: O&M Manuals.  The Contractor is to provide copies of manufacturers’ current literature for all products for which the proprietary brand has been chosen by the Contractor, including COSHH data sheets, catalogue list numbers and manufacturers recommendations for cleaning and maintenance.  The mechanical and electrical systems section shall contain a full description of each of the systems installed, written to ensure that the client fully understands the scope and facilities provided.  All manufacturers technical literature for items of plant and equipment, assembled specifically for the project, including detailed drawings, electrical circuit details and operating and maintenance instructions are to be included.

- Draft Health and Safety File.  A complete H&S file in draft must be submitted by the Contractor, not less than 4 weeks before the date for submission of the final copies of the Manual.  This is to be amended in the light of any comments and resubmitted to the authority.  Do not proceed with production of the final copies of the Manual until authorised to do so b the authority.

DIO is the Authority for this Contract.

# BS 5228-1:2009+A1:2014 - Code of practice for noise and vibration control on construction and open sites.

BS EN 858-2:2003 Separators systems for light liquids- part 2: selection of nominal size, installation, operation and maintenance

BS EN 60079-10- hazardous area classification and control of ignition.

Spec 34 for defence estate electrical installations.

Spec 39 for Fuse Pillars

Spec 39 for Fuse Pillars

defence estate Spec 34 for electrical installations.

BS EN 806-3 Specification for installation inside buildings

BSEN752:2017 Drain and sewer systems outside buildings

BSEN752:2017 Drain and sewer systems outside buildings

BSEN752:2017 Drain and sewer systems outside buildings

Construction (Design & Management) Regulations 2015 (CDM2015).

ACOP-Approved Code of Practice

British Standard

Euro Norm

Control Of Substance Hazardous to Health.