## Sheet1
Electrical Installations - Guidance Document
Generally
A | The Contractor is referred to the Conditions of Contract and Preliminaries and to make
allowance for due and proper compliance therewith.
B | All Electrical Work must be undertaken by a member of the National Inspection Council for
Electrical Installation Contracting (N.I.C.E.I.C.) and be enrolled as an Approved Contractor.
C | The Contractor is advised to visit the dwellings and ascertain site conditions and existing layouts,
as no extra will be allowed for any alleged omissions in this respect at the time of tender. The
Contractor should note that the electrical layout drawing is provisional and must allow in their
price for inspecting each property with the Contract Administrator, or their Representative,
before work commences, to agree the electrical layout required.
D | Prices for stripping out existing wiring, fittings and accessories shall include for making good all
work disturbed in doing so include testing of any relevant modified circuits.
E | The whole of the Electrical Work shall be guaranteed for 12 months against faulty materials and
workmanship, fair wear and tear excepted. Such a guarantee to date from the day of completion
of the Contract and the Contractor is to reinstate at his own expense to the satisfaction of the
Contract Administrator any defective work discovered within the period of guarantee. The
Contractor should also provide their 24 Hr 7 Day a week Call-out details for the period.
F | Supervisor
The Contractor is to appoint a competent Supervisor to whom instructions may be given by the
Contract Administrator. The Supervisor should be available to attend weekly Electrical Q.A.
Inspections.
G | Regulations
The whole of the work to be carried out under this specification is to comply with the current
edition of BS7671:2008+A3:2015 IET Wiring Regulations and with the relevant Parts of the
Building Regulations, to the satisfaction of the Electrical Services Manager, including inspection,
testing and providing the appropriate Electrical Installation Certificates. Test Certification should
include a paper and/or a pdf file. A duplicate Building Regulations compliance certificate should
also be provided where required.
H | Cables
The Contractor should note that the practice of running cables within cavities is expressively
forbidden. All cables must be in chases or, with agreement with the Electrical Services Manager,
in surface mounted conduit or trunking.
EI/1
Electrical Installations (Continued)
A/2 | Wiring
All wiring is to be carried out in BASEC - PVC insulated PVC sheathed 300/500 volt grade cable
to BS 6004. Any flexible cables to BS 6007.
| Lighting/Fan Circuits 1.5 mm2 |  |  |  | (to BS 6004 Table 5)
| Smoke Alarm/Heat Detector Circuit 1.5 mm2 |  |  |  | (to BS 6004 Table 5)
| Air Handling Unit Circuit 1.5 mm2 |  |  |  | (to BS 6004 Table 5)
| Central Heating Circuit 1.5 mm2 |  |  |  | (to BS 6004 Table 5)
| Electric Fire Circuit 2.5 mm2 |  |  |  | (to BS 6004 Table 5)
| Ring Main Circuits 2.5 mm2 |  |  |  | (to BS 6004 Table 5)
| Cooker Circuit 10 mm2 |  |  |  | (to BS 6004 Table 5)
| Shower Circuit 10 mm2 |  |  |  | (to BS 6004 Table 5)
B/2 | Supply Conductors and Main Earthing Conductor
The Consumer Unit Supply Conductors are to be BASEC - PVC insulated and PVC sheathed 300/
500 volt grade, 25 mm2, single core cable (to BS 6004 Table 4) incorporating a EATON AN2EBD
100 Amp double pole isolator at the suppliers meter position. The minimum size for the Main
Earthing Conductor shall be 16 mm2 and if the Electrical Installation earthing arrangements are
TT the earth rod shall be installed outside enclosed in a Furse Inspection Kit Model No: PT - 205
C/2 | Conduits
Wiring to sockets, switches in unplastered areas shall be run in a rigid PVC conduit to comply
with BS 4607, BS EN 60423 or BS EN 61386 series.
D/2 | Main Protective Bonding Conductors
The main earth terminal shall be bonded to the main incoming services as near as possible to
their entry into the building by separate Main Protective Bonding Conductors, which are to be
made identifiable at the consumer unit.
The main services which will require bonding could include the following:-
Main Water Service Pipes
Main Gas Service Pipes
Other Service Pipes
Exposed Structural Steelwork
Central Heating Risers
The minimum size of the Main Protective Bonding Conductors up to 100 amp capacity shall be
10 mm2 and connection shall be made using a Crimp Lug and tool.
The connection to the Gas pipe shall be made on the consumer's side of the gas meter, unused
gas service pipes shall not be bonded. The water service main protective bonding conductor
shall be accessible for inspection purposes.
EI/2
Electrical Installations (Continued)
E/2 | Supplementary Equipotential Bonding
The purpose of supplementary equipotential bonding is to reduce the voltage between the
various exposed - conductive parts and extraneous conductive parts of a location during a fault
to earth. Continuity tests shall be made to ensure a good connection between the exposed
conductive parts and any other extraneous parts. If the resistance exceeds 0.05Ω then further
tests would be needed to establish if they require bonding.
Supplementary Equipotential Bonding: Other Situations - In the kitchen and at the boiler location
a 4 mm2 bond shall be made between/across all hot and cold water pipes, gas pipes and
continuity tests applied to ensure a low resistance connection (under 0.05Ω) exists.
In all other situations where extraneous conductive parts are simultaneously accessible with
other conductive parts, e.g. Tank cupboards, metal bath, etc, tests shall be carried out to verify
a low resistance ( under 0.05Ω ) connection exists.
Additional 4 mm2 supplementary bonds shall be installed where the test is unsatisfactory or if
the existing connection is to be considered unreliable by the Electrical Services Manager or their
representative.
Cables, Routes and Conductors
F/2 | Cables buried in plaster, in a wall or which may be subject to mechanical damage shall be
protected by a 30mA RCD/RCBO and vertically or horizontally, but not diagonally with zonal
concept of cable runs.
G/2 | All fixings screws shall be fixed into correct sizes of approved proprietary 'plugs' set into
pre-drilled holes. Wood plugs shall not be used.
H/2 | Conduits or cables are to be fixed at least 150 mm clear of any pipe carrying Water or Gas.
Should this be impractical the conduit or cable is to be protected in a suitable manner and each
and every case is to be approved by the Electrical Services Manager or their representative
.
I/2 | When the cables pass through joists they shall pass through holes drilled at least 50 mm from
the top or bottom of the joist. If the existing notches are used the cables shall be protected by
purpose made metal protectors. No cables shall be buried under concrete floors.
J/2 | All circuit connections must be made at switches, ceiling roses, sockets or junction boxes.
Junction boxes are to be maintenance free and should be readily accessible, the location should
be noted on the relevant test certification.
M/2 | All cable entries into metal boxes of any description shall be through suitable rubber grommets.
EI/3
Electrical Installations (Continued)
Circuits
A/3 | Cooker Circuit
The cooker circuit shall be installed by means of a 10 mm2 twin & earth PVC insulated/sheathed
cable and will run from the consumer unit to the cooker switch extending to a cooker connection
unit. The cables forming this circuit must not be cut or joined. No junction boxes are allowed in
this circuit.
B/3 | Shower Circuit
The shower circuit shall be installed by means of a 10 mm2 twin & earth PVC insulated and
sheathed cable and will run from the consumer unit to a 50 Amp pull switch and if required
extend to an Shower Unit. The cables forming this circuit must not be cut or joined. No
junction boxes are allowed in this circuit.
C/3 | House Ring Main Circuit(s)
The house ring main circuit(s) to 13 Amp switched socket outlets shall be installed by means of a
2.5 mm2 twin & earth PVC insulated/sheathed cable. The cables forming this circuit must be
continuous and must not be cut or joined. No junction boxes are allowed on this circuit.
No spurring deviations from the ring main circuit are allowed.
D/3 | Kitchen Ring Main Circuit
The kitchen ring main circuit to 13 Amp switched socket outlets shall be installed by means of a
2.5 mm2 twin & earth PVC insulated/sheathed cable. Also the washing machine, fridge, freezer
dishwasher, tumble dryer and cooker hood (where installed) shall be fed via a 13 Amp switched
fused connection unit (engraved with relevant appliance) to a 13 Amp single switched socket
outlet position determined by Contract Administrator. The cables forming this circuit must not be
cut or joined. No junction boxes are allowed on this circuit. No spurring deviations from the ring
main circuit are allowed.
E/3 | Fire Circuit
The fire circuit shall be installed by means of a 2.5 mm2 twin & earth PVC insulated/sheathed
cable and will run from the consumer unit to a 13 Amp switched fused connection unit. The
cables forming this circuit must not be cut or joined. No junction boxes are allowed in this circuit.
F/3 | Smoke Alarm/Heat Detector Circuit
Smoke Alarm/Heat Detector circuit shall be installed by means of a 1.5 mm2 twin & earth PVC
insulated/sheathed cable. All Smoke Alarms/Heat Detectors to be interlinked by means of a three
core and earth PVC insulated/sheathed cable. Relevant Test Certification shall be provided.
EI/4
Electrical Installations (Continued)
G/3 | Lighting Circuit(s) Incorporating Extract Fans
Lighting Circuits shall incorporate the extract fans - The lighting/fan circuits shall be installed by
means of a 1.5 mm2 twin & earth PVC insulated/sheathed cable, except in wiring between two
way switches, where 1.5 mm2 three core & earth PVC insulated/sheathed cable shall be used.
Where two lighting circuits are used, the supply for the upper landing light shall be taken from the
upper floor. Fans are to be fed from the local lighting circuit via a 13 Amp unswitched fused
connection unit mounted at ceiling height incorporating a 3 Amp fuse. Outside lights are to be
fed from the local lighting circuit via a 13 Amp switched fused connection unit engraved
" Outside Light" and incorporating a 3 Amp fuse.
H/3 | Central Heating Circuit
The central heating circuit shall be installed by means of a 1.5 mm2 twin & earth PVC insulated/
sheathed cable and will run from the consumer unit to a 13 Amp switched fused connection unit
incorporating a 3 Amp fuse. The contractor should allow for wiring to all circuit system controls.
The cables forming this circuit must not be cut or joined. No junction boxes are allowed in this
circuit.
I/3 | Positive Input Ventilation Unit Circuit
The Anti Condensation and Positive Ventilation Unit circuit shall be installed by means of a 1.5
mm2 twin & earth PVC insulated/sheathed cable and will run from the consumer unit to a 13
Amp switched fused connection unit incorporating a 3 Amp fuse in the Loft area. The cables
forming this circuit must not be cut or joined. No junction boxes are allowed in this circuit.
Consumer Unit, Wiring Devices, Fittings and Accessories
A/4 | Consumer Unit
The contractor will install Wylex consumer units in all properties at, or local to the meter
position, or as instructed by the Electrical Services Manager or their Representative,
manufactured by Electrium Sales Limited - A Siemens Company - Registered office, Faraday
House, Sir William Siemens Square, Frimley, Camberley, GU16 8QD as follows:
For all systems the contractor shall install:-
14 Way Wylex Metal Clad Main Switch Consumer Unit (Ref: NM1406) incorporating a pattrass
(Ref: MNSPE-6462/ENR and Supply Conductor Gland Kit (Ref EIU).
Note: If the Supply Conductors to the Consumer Unit are greater than 3 metres in length, the
contractor shall also install a Click Scolmore Fused Main Switch (Ref: DB700 c/w DB980 cable
shroud) at the meter position.
B/4 | Circuit Protection Devices
The circuit protection shall be by means of Wylex NSBS RCBO single module combined MCB/RCD
device.
EI/5
Electrical Installations (Continued)
B/4 | Circuit Protection Devices (Continued)
14 - Way
1 No.6 amp NHXSBS1B06 RCBO to protect the air handling unit circuit
1 No.6 amp NHXSBS1B06 RCBO to protect the smoke alarm circuit
1 No.6 amp NHXSBS1B06 RCBO to protect the central heating circuit
2 No.6 amp NHXSBS1B06 RCBO to protect the lighting circuits
1 No.16 amp NHXSBS1B16 RCBO to protect the electric fire circuit
2 No.32 amp NHXSBS1B32 RCBO to protect the ring main circuits
1 No.40 amp NHXSBS1B40 RCBO to protect the shower circuit
1 No.40 amp NHXSBS1B40 RCBO to protect the cooker circuit
3 No. NHB1PP Blanking Plate
C/4 | Wiring, Fittings and Accessories
Wiring, Fittings and Accessories shall be those manufactured by Electrium Sales Limited,
Commercial Centre, Lakeside Plaza, Walkmill Lane, Bridgtown, Cannock WS11 0XE.
D/4 | Light Fittings
In all rooms except the Bathroom - light fittings shall be a Crabtree 3450 Standard Pendant Set,
and in the Kitchen a Crabtree 3422 Standard Batten Lamp holder c/w Home Office Skirt. The
Bathroom light fitting shall comprise of an ASD Centro CE3/WL100-4/DWH enclosed light fitting
E/4 | External Lights
External Dusk to Dawn light fitting shall be ASD Mini Square AMS/BP316C 16w 2D fitting c/w
photocell, as manufactured by ASD Lighting plc, Mangham Road, Barbot Hall Industrial Estate,
Rotherham, S61 4RJ.
F/4 | Wall Light Switches
To be 10 amp single pole flush insulated plate switches Crabtree 4070 one-way and Crabtree
4170 two-way and in gangs grouped as Crabtree 4172 and 4173 with 16mm plaster depth steel
box or 47mm dry line box as appropriate.
G/4 | Shower Ceiling Switch
To be Crabtree 2167 50 ampere double insulated surface cord operated type with mechanical
"off" indicator, neon indicator and ivory mounting box.
H/4 | Ceiling Switches
To be 6 ampere single pole insulated surface cord operated type with ivory mounting blocks.
Crabtree 2041 one-way switch and Crabtree 2141 two-way switch.
EI/6
Electrical Installations (Continued)
I/4 | Socket Outlets
To be 13 amp double pole twin switched socket outlet Crabtree 4306/D and 13 amp double pole
single switched socket outlet Crabtree 4304/D, Mounting boxes shall be a 25mmm steel box or
47mm dry lining box as appropriate.
J/4 | Fused Connection Units
To be 13 amp double pole switched with neon indicator fused connection unit Crabtree 4827/3
engraved where appropriate. Extract Fans fed via 13 amp un-switched with neon indicator fused
connection unit Crabtree 4828/3. Mounting boxes shall be 25mm steel or 47mm dry lining box as
appropriate.
K/4 | Cooker Control Unit
To be 45 ampere double pole 'slim-line' cooker control unit c/w neon indicators Crabtree 4521/
31, supplying a cooker connecting outlet, Crabtree 4506. Mounting boxes shall be 47mm steel or
dry lining box as appropriate.
L/4 | Anti-condensation and Positive Input Ventilation Unit
To be the Envirovent PIV - Loft Mounted Unit as manufactured by Envirovent Ltd. Envirovent
House, Hornbeam Business Park, Harrogate, HG2 8PA. This shall be installed via a 13 amp double
pole switched with neon indicator fused connection unit Crabtree 4827/3 incorporating a 3
ampere fuse and engraved 'Air Unit', all fitted as per manufacturer's instructions.
M/4 | Extract Fans
To be the Filterless Extract Fan as manufactured by Envirovent Ltd., Envirovent House,
Hornbeam Business Park, Harrogate, HG2 8PA. Model EFHT2S-230. The Contract Administrator
may request the installation of the Ceiling Mounted Model EFHTCM-230 or the Wireless Model
EFHT2S-230WL in the event of location restrictions.
N/4 | Smoke Alarms/Heat Detectors
Smoke Alarms to be Ei166e Optical, Heat Detectors to be Ei164e - 230 volt mains powered,
c/w 10 year rechargeable lithium battery back-up, as manufactured by AICO Ltd, Mile End
Business Park, Maesbury Road, Oswestry, SY10 8NN.
Units shall be ceiling mounted in circulation areas within 7 metres of the doors of rooms where
fire is likely to start ( e.g. Kitchen or living room ), and within 3 metres of bedroom doors,
measured horizontally, interconnected in full accordance with the manufacturer's
recommendations. They shall be conveniently mounted within safe reach for maintenance and
cleaning. Units shall be fixed centrally within the circulation area, a minimum of 300mm from
any wall, light fitting or the positive input ventilation unit and also situated in a location where
steam, condensation or fumes will not cause false alarms. If this is not possible then the exact
location must be agreed with the Electrical Services Manager or their representative.
EI/7
Electrical Installations (Continued)
A/5 | Central Heating and Hot Water Control Systems for Gas Installations, where required shall be as
follows:
| (i) | Integral programmer shall be 24 hour plug-in time clock Ref 306741, as manufactured
by Vaillant Limited, Vaillant House, Medway City Estate, Trident Close, Rochester,
Kent, ME2 4EZ.
| (ii) | Room Thermostat shall be Drayton RTS2 as manufactured by Drayton Controls,
401, Southway Drive, Plymouth, PL6 6QT.
B/5 | Prices for Installing Electrical Circuits shall include for all cables, conduits, fittings and
accessories as well as the marking, cutting and making good of all holes, mortices, chases and
the like required. Where flooring is to be lifted, it should be completed in such a manner that will
allow the lifted flooring to be replaced without damage. Where the flooring is already damaged,
the contractor must inform the Contract Administrator, or their representative, for inspection.
C/5 | Mounting Heights of Electrical Accessories
Houses and Flats
| Consumer Unit |  | 1200mm
| House Sockets |  | 530mm
| Kitchen Sockets |  | 1150mm
| Switches |  | 1150mm
Bungalows
| Consumer Unit |  | 1200mm
| House Sockets |  | 680mm
| Kitchen Sockets |  | 1150mm
| Switches |  | 1150mm
All heights are to the top of the accessory from FFL.
Cooker Hood Socket height to align with top of Kitchen Wall Units.
Under-bench Sockets and Cooker Outlet 680mm from FFL.
All accessories must be positioned a minimum 3500mm away from a room corner.
EI/8