## Sheet1
Southampton Drawings - Conversion to CAD and Update
2017
VERSION 2
Number | Existing Drawing Ref | Existing Drawing name | Service Covered | Service Type | Notes | Known Changes
1 | MHL(61)SKM014 | LV Distribution Diagram | LV Network | Electrical | High level showing building arrangement and generator with split between essential and non essential services and VOD units. | Addition of VOD units & PV. Services pit moved above ground. Changes at boards level - additonal DB boards in: Library, MRIC, 342 mezzanine, S1/55, pontoon, small boats area, A1, A3, A8 & A10 buildings
2 | BMS Topology | BMS Route Layouts | Building Management System | Data/Electrical | Showing building layout to outstation level but including detail on the scope of each outstation.
3 | CAT 5 network | CAT 5 network | CAT 5 network | Data | High level to network cabinets. Combine to one drawing
4 | CAT 6 Network | CAT 6 Network | CAT 6 Network | Data | High level to network cabinets. Combine to one drawing
5 |  |  | Site Direct Current network | Electrical | New drawing required for PV | PV panels
6 | (53)SKM001 | Energy Centre Water Services Schematic | Drinking Water | Water | Including main storage tanks and outlet feeds. PDF drawing available from zetasafe | Removal & addition of some water fountains
7 | (53)SKM002 | Raw Water and Softened Water Schematic | Domestic Cold Water | Water | Including main storage tanks and outlet feeds. | Drawing needs to be split for each service. Tanks have been rationalised
8 |  |  | Domestic Hot Water | Water | Including main storage tanks and outlet feeds. | Level 5 now has 1 calorifier per node (except node 3) Drawing needs to be split for each service
9 | (53)SKM006 | Science Building Laboratory Cold Water Schematic | Laboratory Cold Water | Water | Including main storage tanks and outlet feeds. | New tank sizes
10 | (53)SKM005 | Science Building Laboratory Hot Water Schematic | Laboratory Hot Water | Water | Including main storage tanks, calorifers, solar interface and outlet feeds. | Solar thermal interface, colorifiers, pre heat tank
11 | (53)SKM004 | Pure Water System Schematic Whole Site | Reverse Osmosis Water | Water | Including node 6 plant. | New heat exchanger, new side stream pumps on RO plant.
12 | (53)SKM003 | Whole Site - All Levels Seawater Schematic | Sea Water Supply | Water | Including aquarium and main building. | New heat exchanger in 492. Local sand filters in the aquarium
13 | MHL(56)SKM009 | Chilled Water Schematic All Nodes | Chilled Water | Water | Including level 7 chiller plant and Sea Water Cooling. | Interface with seawater cooling. Installation of PICT valves. Water fountains are now chilled water. A3 spur
14 | MHL(56)SKM-001, MHL(56)SKM-002, MHL(56)SKM-003, MHL(56)SKM-004, MHL(56)SKM-005, MHL(56)SKM-006, MHL(56)SKM-007, MHL(56)SKM-011 |  | Constant Temperature Circuit | Heating | Including centralised boiler plant, softener and A9. | A new survey is required, including the boilers to the coils and taps. New areas: A3 spur, MRIC, library
15 |  | Heating Schematic | Variable Temperature Circuit | Heating | Combine to a single drawing. Including centralised boiler plant, softener and A9. | A new survey is required, including the boilers and building radiators.
16 | NEW DRAWING REQUIRED |  | Solar thermal systems | Heating | New drawing for solar arrays. | New drawing required including interface. MRIC only
17 | SKM(54)002SHT1-2 & SKM(54)002SHT2-2 | Medical Gases Schematic | Nitrogen | Medical Gases | Including supply gas stores and outlets. Split out the drawings, one per gas.
18 |  |  | Helium | Medical Gases | Including supply gas stores and outlets. Split out the drawings, one per gas.
19 |  |  | Hydrogen | Medical Gases | Including supply gas stores and outlets. Split out the drawings, one per gas.
20 |  |  | Argon | Medical Gases | Including supply gas stores and outlets. Split out the drawings, one per gas.
21 | MHL(5-)(6-)(CD)EC1-002 | Energy Centre Level 1 External Water/Oil Storage Tanks & Generator Co-Ordination Plan. | Diesel | Fuel | Supplies to generator and pontoon. | The tank is now smaller. Requires the supply feed adding for the pontoon
22 | E-101 | External Drainage (Sheet 1 of 3) | Drainage | Water | Combine to a single drawing. | 2x interceptors (waste managmeent area & wash down area). 1x interceptor removed (yard, by the A8 building)
23 | E-102 | External Drainage (Sheet 2 of 3)
24 | E-103 | External Drainage (Sheet 3 of 3)
25 | (52)256-001, (52)341-001, (52)344-001, (52)431-001, (52)434-001, (52)436-001, (52)521-001, (52)NW2-001, (52)NW3-001, (52)NW4-001, (52)NW5-001, (52)121-001, (52)123-001, (52)161-001, (52)166-001, (52)231-001, (52)232-001, (52)251-001, (52)254-001, (52)524-001, (52)526-001, (52)611-001, (52)616-001, (52)233-001, (52)236-001 | Soil & Waste Pipework | Foul Water | Water | Combine the set so create a single drawing. | A1 building, Yard, Workshop, pipework in front of the MRIC building

## Sheet2
Number | Existing Drawing Ref | Existing Drawing name | Disc folder | Drawing type | Service Covered | Service Type | Notes | Known Changes
1 | (54)SKM001 | Natural Gas Schematic | 008, 1 Negatives AOC 2156 | Building Schematic Layout | Natural Gas | Medical Gases | Including supply gas stores and outlets. No changes. Part of PGR Survey
2 | (65)SKM002 | Schematic Diagram Fire Alarms | D22 & G34 & 19AO & 6 Negatives | Building Schematic Layout | Fire Management System | Data | Showing building layout to fire panel level but including detail on areas captured. Part of PGR Survey
3 | (61)SKM-013 & (61)SKM011 | HV Schematic Diagram & Schematic Diagram H.V. Switchboard & Network Whole Site | X_1 & 12AO, DU, G34 | Building Schematic Layout | HV Network | Electrical | Including A9 main incomer. Add VOD units & PV