## ITT for Pricing Schedule
Schedule of Works
MCA - SCHEDULE OF WORKS
Site Address: |  | HMCG, Marine House, Blaikie's Quay, Aberdeen, AB11 5EZ
Project Type: |  | Desk Upgrade/Uplift & Associated Works
Tenderers for the above contract should complete the tables below, indicating what they would charge for each required element. Prices must: • Be stated in Pounds Sterling; • Include all other charges and overheads associated with the element being priced. • Be Exclusive of Value Added Tax (VAT), however suppliers must include VAT in the total by completing the relevant line item.
General Works, Site Conditions and Prelims: |  |  | Tender: £
Notes
** | Works are to be undertaken inside normal working hours 0700hrs to 1900hrs Monday to Sunday.
** | All works are to comply with current standards, legislative regulations and best practice guidance.
** | For additional information please refer to: Appendix B - Site Photographs Appendix C - Floor Plans Appendix D - Contractor Supplied Items
1 | Health, Safety & Environment
1.01 | Allow for the provision of all pre-construction safety file documentation including risk assessments, method statements, COSHH assessments, Asbestos Surveys and Fire Safety Approval on behalf of the client (if appropriate). |  | 0
1.02 | Allow for all safety related equipment including such items as barriers, working at height access and lifting equipment to enable the works to be carried out with minimal risk to operatives and local unit users. |  | 0
1.03 | Allow for all appropriate waste transportation licences and ensure all arisings are removed from site and disposed of in an environmentally approved manner. |  | 0
2 | Design Works
2.01 | Allow for a full survey of the works/investigation of the existing equipment and validation of drawings to enable the new facility to function as required on completion of the project. |  | 0
2.02 | Allow for the design/replacement of the existing distribution board supporting the Operational Desks |  | 0
2.03 | Allow for the design/modification of the existing electrical distribution to provide individual circuits to each Operational Desk |  | 0
3 | Statement of Requirement
3.01 | Disconnect and remove existing desk door power radial. Desk door radial is supplied from single cleaners socket in a floor box behind the main double doors to the MRCC. Once disconnected confirm dead at each desk and remove circuits and sockets. |  | 0
3.02 | Disconnect and remove redundant cleaners socket on far side of MRCC adjacent to the printers. |  | 0
3.03 | Replace existing Distribution Board in Communications Room with minimum 14 way board. Allow one circuit for each of the 10 Operational Desks and sufficient spare ways for future circuits.
3.04 | Relocate existing underfloor power to provide one commando surface socket per desk. |  | 0
3.05 | Supply and fit new power (containment, cabling and commando socket) for two desks. Approx.20m from DB to each desk. |  | 0
3.06 | Where possible reuse existing floor tiles with pre-drilled holes for the new desk layout. Supply and fit new brush cable grommets to the existing tiles. |  | 0
3.07 | Supply and fit new floor tile for the additional desk (or locations where existing tiles could not be reused) Core drilling to be a minimum of 100mm (or as directed by the manufacturer) maintained from the edge of the raised floor tile to maintain the integrity and load capability of the installation. |  | 0
3.08 | Supply and fit new CAT 5 Patch Panel in the existing communications cabinet |  | 0
3.09 | Supply and fit 6 x new data cables to be installed from the small 4th Floor communications room at the front of the building to each desk. New cabling will be CAT5 UTP (unshielded) LSOH type cables, terminated in 6 way GOP box with sufficient spare cable and flexible conduit to allow final positioning (60 cables, 6 cables to each GOP box, 10 GOP boxes in total). Nearest desk is 9m from cabinet to GOP box location, furthest desk 20m. |  | 0
3.1 | Replace existing 20A Cleaners Socket circuit with 32A MCB. This change will facilitate works listed at serials 3.11 and 3.12 below. |  | 0
3.11 | Supply and fit 5 x new floor tiles cut and fitted with power and data floor boxes (2 x UK Power + 4 Data Sockets). Core drilling to be a minimum of 100mm (or as directed by the manufacturer) maintained from the edge of the raised floor tile to maintain the integrity and load capability of the installation. |  | 0
3.12 | Supply and fit new 32A ring main circuit supplying 5 new power and data floor boxes (locations as shown on Proposed Floor Plan and Raised Floor Plan) |  | 0
3.13 | Supply and fit 2 x new data cables to each new floor box. New cabling will be CAT5 UTP (unshielded) LSOH type cables. Allow for additional containment and flexible conduit to final termination. |  | 0
3.14 | Supply and fit 3 x new double sockets and 3 x single brush cable entry/exit faceplate mounted high level on the North wall of the Operations Room as shown on the Proposed Floor Plan. To support 3 x screens (supplied by client) |  | 0
3.15 | Supply and fit 2 x 15m Active HDMI cables CL2 Rated. One cable from the 2 x proposed screens locations to desk AB 03 and AB08 as shown on the Proposed Floor Plan. |  | 0
3.16 | Supply and fit 3 x Swivel and Tilt wall mounted 55" TV brackets as shown on the Proposed Floor Plan (Display screens to be free issue by client) See Appendix D - Contractor Supplied Items |  | 0
3.17 | Allow for existing services associated with the works and new electrical, pipework, ductwork penetrations through fire compartments including walls, barriers, floors, ceilings (to both sides) are correctly fire stopped using approved/certified fire rated/fire stopping material/collars/dampers to prevent fire spread in accordance with Approved Document B and BS9999. All works to fire stopping to be undertaken by 3rd party accredited and certified sub-contractors. Confirmation of sub-contractor to be provided at pre-start meeting by the main principal contractor. |  | 0
3.18 | Relocate existing main MRCC double door to new location (central to room) as shown on 4th Floor - Proposed Floor Plan. |  | 0
3.19 | Where possible relocate existing lighting controls and temperature sensor to suit new door configuration. |  | 0
3.2 | Where possible remove any redundant wall mounted services |  | 0
3.21 | Make good and decorate all walls: - Plasterboard walls to be Matt Emulsions – colour white - All architraves, skirtings, linings, frames, etc.to be Trade High Gloss – colour white - All window sills to be sanded and re-varnished |  | 0
3.22 | Supply and fit new ironmongery to the relocated double door. |  | 0
3.23 | Supply and fit new carpet tiles to the whole Operations Room (Milliken - Light Trail/Dusk Titanium Light Print DR01349556) |  | 0
4 | Completion
4.01 | Allow for making good. Making good shall be executed with materials to match the surrounding work. The term making good includes for removal of damaged and / or defective parts of existing structure, finishing's and components; filling; dressing down; piecing in; patching; forming flush, smooth joint to existing; extending existing finishing's; all requisite minor repairs and adjustments all to match existing. Making good shall be carried out wherever required by the Specification and / or Drawings and where required as a consequence of any other works of removal, alteration, extension or maintenance required under this Contract. Making good shall be deemed to include decorating new work or redecorating disturbed areas as required. |  | 0
4.02 | O&M Package: Allow for the provision of one electronic copy and one printed hard copy of all commissioning certification, test sheets, guarantees, manufacturers installation, user operation and engineers service and maintenance guides, suppliers contact information, disposal information etc. to include full set of As Built drawings in DWG. & PDF showing modifications and all fire stopping locations suitably referenced. This information is to be presented in a post-construction health and safety file format. |  | 0
4.03 | On completion the Contractor is to undertake a specialist deep clean (sparkle clean) of working areas and leave the premises clean and tidy, free from dirt and dust to the satisfaction of the Project Manager. Including but not limited to clearing away builders material, cleaning down glazing, mopping vinyl floors, vacuuming all floors etc. |  | 0
5 | Other Costs
5.01 | Prelims | Any other preliminaries not included above - All MUST be itemised | 0
5.02 | Miscellaneous | Any other costs not included above - All MUST be itemised | 0
| TENDER TOTAL |  | 0
| VAT |  | 0
| TOTAL INCLUSIVE OF VAT |  | 0

## Schedule of Work (SoW)
Schedule of Works
MCA - SCHEDULE OF WORKS
Site Address: |  | HMCG, Marine House, Blaikie's Quay, Aberdeen, AB11 5EZ
Project Type: |  | Desk Upgrade/Uplift & Associated Works
Tenderers for the above contract should complete the tables below, indicating what they would charge for each required element. Prices must: • Be stated in Pounds Sterling; • Include all other charges and overheads associated with the element being priced. • Be Exclusive of Value Added Tax (VAT), however suppliers must include VAT in the total by completing the relevant line item.
General Works, Site Conditions and Prelims: |  |  | Tender: £ | Tenderer Comments | Quality Evaluation Weighting
Notes
** | Works are to be undertaken inside normal working hours 0700hrs to 1900hrs Monday to Sunday.
** | All works are to comply with current standards, legislative regulations and best practice guidance.
** | For additional information please refer to: Appendix B - Site Photographs Appendix C - Floor Plans Appendix D - Contractor Supplied Items
1 | Health, Safety & Environment |  |  |  | Sub-Weightings Overall - 20%
1.01 | Allow for the provision of all pre-construction safety file documentation including risk assessments, method statements, COSHH assessments, Asbestos Surveys and Fire Safety Approval on behalf of the client (if appropriate). |  | 0 |  | 8%
1.02 | Allow for all safety related equipment including such items as barriers, working at height access and lifting equipment to enable the works to be carried out with minimal risk to operatives and local unit users. |  | 0 |  | 5%
1.03 | Allow for all appropriate waste transportation licences and ensure all arisings are removed from site and disposed of in an environmentally approved manner. |  | 0 |  | 7%
2 | Design Works |  |  |  | Overall - 25%
2.01 | Allow for a full survey of the works/investigation of the existing equipment and validation of drawings to enable the new facility to function as required on completion of the project. |  | 0 |  | 5%
2.02 | Allow for the design/replacement of the existing distribution board supporting the Operational Desks |  | 0 |  | 10%
2.03 | Allow for the design/modification of the existing electrical distribution to provide individual circuits to each Operational Desk |  | 0 |  | 10%
3 | Statement of Requirement |  |  |  | Overall - 40%
3.01 | Disconnect and remove existing desk door power radial. Desk door radial is supplied from single cleaners socket in a floor box behind the main double doors to the MRCC. Once disconnected confirm dead at each desk and remove circuits and sockets. |  | 0 |  | 1%
3.02 | Disconnect and remove redundant cleaners socket on far side of MRCC adjacent to the printers. |  | 0 |  | 1%
3.03 | Replace existing Distribution Board in Communications Room with minimum 14 way board. Allow one circuit for each of the 10 Operational Desks and sufficient spare ways for future circuits. |  |  |  | 4%
3.04 | Relocate existing underfloor power to provide one commando surface socket per desk. |  | 0 |  | 2%
3.05 | Supply and fit new power (containment, cabling and commando socket) for two desks. Approx.20m from DB to each desk. |  | 0 |  | 2%
3.06 | Where possible reuse existing floor tiles with pre-drilled holes for the new desk layout. Supply and fit new brush cable grommets to the existing tiles. |  | 0 |  | 1%
3.07 | Supply and fit new floor tile for the additional desk (or locations where existing tiles could not be reused) Core drilling to be a minimum of 100mm (or as directed by the manufacturer) maintained from the edge of the raised floor tile to maintain the integrity and load capability of the installation. |  | 0 |  | 2%
3.08 | Supply and fit new CAT 5 Patch Panel in the existing communications cabinet |  | 0 |  | 2%
3.09 | Supply and fit 6 x new data cables to be installed from the small 4th Floor communications room at the front of the building to each desk. New cabling will be CAT5 UTP (unshielded) LSOH type cables, terminated in 6 way GOP box with sufficient spare cable and flexible conduit to allow final positioning (60 cables, 6 cables to each GOP box, 10 GOP boxes in total). Nearest desk is 9m from cabinet to GOP box location, furthest desk 20m. |  | 0 |  | 3%
3.1 | Replace existing 20A Cleaners Socket circuit with 32A MCB. This change will facilitate works listed at serials 3.11 and 3.12 below. |  | 0 |  | 2%
3.11 | Supply and fit 5 x new floor tiles cut and fitted with power and data floor boxes (2 x UK Power + 4 Data Sockets). Core drilling to be a minimum of 100mm (or as directed by the manufacturer) maintained from the edge of the raised floor tile to maintain the integrity and load capability of the installation. |  | 0 |  | 2%
3.12 | Supply and fit new 32A ring main circuit supplying 5 new power and data floor boxes (locations as shown on Proposed Floor Plan and Raised Floor Plan) |  | 0 |  | 2%
3.13 | Supply and fit 2 x new data cables to each new floor box. New cabling will be CAT5 UTP (unshielded) LSOH type cables. Allow for additional containment and flexible conduit to final termination. |  | 0 |  | 2%
3.14 | Supply and fit 3 x new double sockets and 3 x single brush cable entry/exit faceplate mounted high level on the North wall of the Operations Room as shown on the Proposed Floor Plan. To support 3 x screens (supplied by client) |  | 0 |  | 2%
3.15 | Supply and fit 2 x 15m Active HDMI cables CL2 Rated. One cable from the 2 x proposed screens locations to desk AB 03 and AB08 as shown on the Proposed Floor Plan. |  | 0 |  | 1%
3.16 | Supply and fit 3 x Swivel and Tilt wall mounted 55" TV brackets as shown on the Proposed Floor Plan (Display screens to be free issue by client) See Appendix D - Contractor Supplied Items |  | 0 |  | 1%
3.17 | Allow for existing services associated with the works and new electrical, pipework, ductwork penetrations through fire compartments including walls, barriers, floors, ceilings (to both sides) are correctly fire stopped using approved/certified fire rated/fire stopping material/collars/dampers to prevent fire spread in accordance with Approved Document B and BS9999. All works to fire stopping to be undertaken by 3rd party accredited and certified sub-contractors. Confirmation of sub-contractor to be provided at pre-start meeting by the main principal contractor. |  | 0 |  | 1%
3.18 | Relocate existing main MRCC double door to new location (central to room) as shown on 4th Floor - Proposed Floor Plan. |  | 0 |  | 2%
3.19 | Where possible relocate existing lighting controls and temperature sensor to suit new door configuration. |  | 0 |  | 1%
3.2 | Where possible remove any redundant wall mounted services |  |  |  | 1%
3.21 | Make good and decorate all walls: - Plasterboard walls to be Matt Emulsions – colour white - All architraves, skirtings, linings, frames, etc.to be Trade High Gloss – colour white - All window sills to be sanded and re-varnished |  | 0 |  | 2%
3.22 | Supply and fit new ironmongery to the relocated double door. |  | 0 |  | 1%
3.23 | Supply and fit new carpet tiles to the whole Operations Room (Milliken - Light Trail/Dusk Titanium Light Print DR01349556) |  | 0 |  | 2%
4 | Completion |  |  |  | Overall - 10%
4.01 | Allow for making good. Making good shall be executed with materials to match the surrounding work. The term making good includes for removal of damaged and / or defective parts of existing structure, finishing's and components; filling; dressing down; piecing in; patching; forming flush, smooth joint to existing; extending existing finishing's; all requisite minor repairs and adjustments all to match existing. Making good shall be carried out wherever required by the Specification and / or Drawings and where required as a consequence of any other works of removal, alteration, extension or maintenance required under this Contract. Making good shall be deemed to include decorating new work or redecorating disturbed areas as required. |  | 0 |  | 3%
4.02 | O&M Package: Allow for the provision of one electronic copy and one printed hard copy of all commissioning certification, test sheets, guarantees, manufacturers installation, user operation and engineers service and maintenance guides, suppliers contact information, disposal information etc. to include full set of As Built drawings in DWG. & PDF showing modifications and all fire stopping locations suitably referenced. This information is to be presented in a post-construction health and safety file format. |  | 0 |  | 3%
4.03 | On completion the Contractor is to undertake a specialist deep clean (sparkle clean) of working areas and leave the premises clean and tidy, free from dirt and dust to the satisfaction of the Project Manager. Including but not limited to clearing away builders material, cleaning down glazing, mopping vinyl floors, vacuuming all floors etc. |  | 0 |  | 4%
5 | Other Costs |  |  |  | (No Quality Score)
5.01 | Prelims | Any other preliminaries not included above - All MUST be itemised | 0
5.02 | Miscellaneous | Any other costs not included above - All MUST be itemised | 0
| TENDER TOTAL |  | 0
| VAT |  | 0
| TOTAL INCLUSIVE OF VAT |  | 0