C0036

Specification for

Roof replacement and Solar Photovoltaic installation project

At BAS Cambridge site

1.	Project particulars	3

1.1	Project	3

1.2	Description of the Works	3

1.3	Client	4

1.4	Description of the Site	4

1.5	Drawings and additional documents	4

Tender	5

1.6	5

1.7	Insurances	5

1.8	Programme	5

1.9	Defects Period	5

1.10	Health & Safety	5

1.11	System Signage	6

1.12	Asbestos	7

1.13	CDM	7

2.	CONTRACT INFORMATION	7

2.1	Schedule of Works	7

2.2	Variations	7

3.	OBLIGATIONS AND RESTRICTIONS IMPOSED BY THE EMPLOYER	7

3.1	Operation and Maintenance Manuals	7

3.2	Verification of Sizes, etc.	8

3.3	Inspections and Tests	8

3.4	Building information modelling	8

3.5	Government Soft Landings	8

3.6	Access to and Possession or Use of Site	8

3.7	Prevention of Nuisance and Trespass	8

3.8	Speed Limits	9

3.9	Vehicle Parking	9

3.10	Overtime	9

3.11	Working Hours	9

3.12	Advertising Rights	9

3.13	Maintenance of Existing Services, etc.	9

3.14	Site Specific Restrictions	10

3.15	Waste	10

3.16	Supervision	10

3.17	Water for the Works	11

3.18	Lighting and Power for the Works	11

3.19	Temporary Accommodation	11

3.20	Mess Canteen Facilities	11

3.21	Toilet Facilities	11

3.22	Transistor Radios	11

3.23	Attendance	11

3.24	Scaffolding	11

3.25	Treasure Trove etc.	11

3.26	Data Protection Act	12

4.	FIRE PRECAUTIONS	12

4.1	Existing Structures	12

4.2	Fire Precautions Generally	12

5.	MATERIALS, GOODS AND WORKMANSHIP	12

5.1	Compliance	12

5.2	Electrical Works	13

5.3	Tolerances	13

5.4	Setting out the Works.	13

5.5	Dust Sheets and Protection	13

5.6	Making good	13

5.7	Plant, Tools and Vehicles	13

5.8	Temporary Fencing, Hoarding, etc.	13

5.9	Inclement weather	13

5.10	Fixings generally	13

5.11	Commissioning	14

6.	Design	14

6.1	Overview	14

6.2	Scope of construction elements involved with roof upgrade project and phases	15

6.3	Asbestos removal and disposal	15

6.4	Replacement of existing roof sheets to logistics building	15

6.5	Re-rendering of east side of logistics building (Phase 1)	15

6.6	Replacement of all existing windows and doors to east side of logistics building (Phase 2)	15

6.7	Preparation of roof on logistics building and Science building 2 to carry solar PV’s	15

6.8	Location and areas of building work	15

6.9	Asbestos removal and disposal (phase 1)	16

6.10	Asbestos contactor or sub-contractor requirements	16

6.11	Temporary boarding	16

6.12	Testing and potential contamination	16

6.13	RPE and PPE	16

6.14	Asbestos waste containment and disposal	16

6.15	Hygiene facility	17

6.16	Removal of existing roof sheets (West Side of Logistics Building)	17

6.17	Roof purlins	17

6.18	Replacement roof system performance	17

6.19	Guttering system	18

6.20	Personnel Doors	18

6.21	Windows	18

6.22	Roller shutters	18

6.23	External wall render	19

6.24	Solar PV specification	19

6.25	Component 1: Solar Panels	19

6.26	Component 2: Inverters	20

6.27	Component 3: Mounting System	20

6.28	Electrical Supply characteristics.	21

6.29	Protection against electric shock	21

6.30	System losses	21

6.31	Monitoring	21

6.32	Electrical design considerations	21

6.33	DC system	22

6.34	DC connectors	22

6.35	DC isolation and circuit protection	22

6.36	AC system	23

6.37	AC Isolation and circuit protection	23

6.38	Cabling	23

6.39	System earthing and bonding	24

6.40	Metering	24

6.41	Lighting and surge protection	24

6.42	Decommissioning plan – End of life considerations	24

# Project particulars

## Project

The project scope comprises the replacement of an existing roof, the removal of asbestos, supporting infrastructure and modifications and the installation of solar panels on 1) the newly replaced roof of the BAS Supply Chain Logistics building and 2) the existing roof of the BAS Science Building 2.

The British Antarctic Survey (BAS) has recently committed to achieve Net Zero Carbon Emissions by 2040 from its directly managed operations. As part of this commitment, this project will facilitate the low carbon transition of BAS offices in Cambridge by increasing the solar capacity of the site and reducing our environmental impact. This project aims to provide a minimum additional 450kW of solar photovoltaic power generation installed in both roofs which will meet 17% of the site’s electricity demands and will contribute to a reduction of 90 tonnes of CO2e.

.

## Description of the Works

The works are to be carried out across two buildings on the same Cambridge site:

The logistics building will require removal and replacement of the existing roof. Along with installation of new doors, windows and roller shutters and the re-rendering of external walls to provide greater thermal efficiency. Finally, an installation of solar cells and infrastructure will complete works to this building.

Figure 1: Supply Chain Logistics roof to be replaced and support the installation of solar panels.

On Science building 2 solar cells are to be fitted to the existing roof, along with all necessary infrastructure.

Figure 2: Science Building 2 roof to support the installation of solar panels.

Both solar arrays will be connected to the existing site electrical distribution, and a 200kW exportation limitation device shall be installed as specified by the Distribution Network Operator (DNO).

## Client

British Antarctic Survey

High Cross, Madingley Road, Cambridge, CB3 0ET.

Tel: 01223 221400

## Description of the Site

The British Antarctic Survey, Cambridge, is part of the Natural Environment Research Council. The primary use for the site is polar scientific research, and therefore the site contains many laboratories, cold rooms, workshops, as well as office accommodation.

This site can be occupied 24 hours a day. All buildings will be occupied throughout the works. The Contractor must take all reasonable care not to interfere with all other activities on the site.

The Tenderers are recommended to visit the site before submitting his Tender to acquaint themselves with local conditions, means of access, the full extent and character of the Works and any other matters which might affect the execution of the Works.

## Drawings and additional documents

The drawings and additional documents issued with the Tender will form the Contract Drawings and are listed below:

- Site plan

- Asbestos register

- DNO approval

- Planning approval

- Structural Engineers report

## Tender

The Contractor is required to examine the drawings and related documents prior to submitting his Tender and notify the Employer of any conflicting or inadequate information contained therein.  On submitting his Tender, the Contractor shall be deemed to have satisfied himself as to the sufficiency of the information provided to enable him to carry out and complete the contract.  No subsequent claim for consequential loss upon the Contractor’s failure to comply with these provisions will be entertained.

The Contractor is to visit and inspect the site prior to Tendering as no claim will be allowed on the grounds of ignorance of the conditions under which the work will be executed, the character of the work and all that is involved in carrying out this Contract.  No claim will be entertained for the Contractor's failure to comply with this Clause.

The Employer does not bind himself to accept the lowest of any tender or any section of same; neither do they hold themselves responsible for any expense the Contractor may incur in the estimating or in the adjustment of accounts.

The Employer will not be liable for any costs incurred in the preparation and submission of a tender.

The contract will be awarded on the basis of best value for money taking account of price, technical merit and quality

This shall be a fixed all-inclusive priced based upon the contract documents and a careful inspection of the site including for handing over the works clean, functional and complete, fit for immediate occupation and use as intended.

## Insurances

£1,000,000 Public Liability Insurance.

The Employer will require sight of a valid insurance certificate prior to entering into a contract.

## Programme

The project is to be split into two phases as detailed below:

Phase 1. To be completed and invoiced by mid-March 2021

- Complete Installation and integration of solar array on SB2.

- Roof and window replacement, complete solar installation and re-render external walls on east section of Logistics building.

Phase 2. To be completed and invoiced by mid- March 2022

- Roof, window and door replacement and complete solar installation on west section of Logistics building, re render external walls.

It is intended that work on site shall commence As soon as possible. All units shall be commissioned, tested and handed over by the end of March 2022 at the latest.

The ambition is to have seamless transition between the phases.

## Defects Period

All installations will be warrantied for a period of at least 12 months from the date of system handover to the client. During this period, the principle contractor will be responsible for correcting any emergent defects, unless caused by negligent system operation or causal factors outside of the design specification.

## Health & Safety

The contractor will be formally appointed as principal contractor.

To uphold stringent health and safety standards during the construction phase, all health, safety and welfare provisions for persons at work must be provided as well as upholding the responsibilities ensconced within the Construction Design and Management Regulations 2015 (CDM). CDM covers civil and engineering works of any scale including construction, retrofitting, repair and decommissioning stages, applying to all life cycle phases.

Under CDM, consideration must be given to the planning and co-ordination of maintenance and repair of all components. Adequate site security should be provided to guard against theft and limit the danger of unauthorised persons causing self-inflicted injury.

CDM regulations documentation, specific risk assessments etc. shall be provided as follows:

1.	In electronic format and the Services Contractor shall agree number of paper copies to be issued for comment with the Principal Contractor/Principle engineer, for tender purposes assume 4.

2.	Manufacture / installation works shall not commence until the documentation has been returned without any outstanding comments from the Principle Contractor/Principle Designer, all comments shall be addressed prior to final copy being issued for inclusion in the Health and Safety File.

Installation and maintenance of the PV modules must be carried out in accordance with the Work at Height Regulations (2005) and the guidelines presented in Health and Safety in Roof Work (2012). Ensuring that only designated competent persons carry out removals and replacement of damaged PV modules. Risks and hazards posed by fracture of the PV modules themselves mean that a response plan must be put in place to ensure that any breakage is swiftly communicated to, and handled by an appropriately appointed competent person.

Methods of installation and maintenance that negate the requirement to work at height should be considered. Further guidance on glazing at height as well as risk assessment examples and mitigation measures are provided in BRE publication BR471: Sloping glazing, Understanding the risks.

Monitoring for signs of corrosion and/or deformation of steel members should be conducted to ensure that the structural integrity is maintained. The design working life, accommodating for issues such as corrosion, is to be designed in accordance with BS EN 1990 and therefore the timeline of use for structural members including anticipated maintenance can be developed.

Consideration should be given to the health and safety risks arising from electrical connections and components. Safe working practices should be defined and observed with the electrical system of the solar carport. Particular attention should be taken of the risks posed by the DC side of the system. Each solar array should have a bespoke maintenance and monitoring plan. During operation, health and safety is to be upheld through constant monitoring of correct system functionality and maintenance of safety and protective equipment.

Fire risk and prevention should be considered at all stages of the development. Under law a nominated person will be responsible for fire safety. It is recommended that a fire risk assessment is completed by a competent person/organisation and reviewed at installation and commissioning stages. Consideration should be given to the location of any system components with respect to any existing fire escape routes, mustering points etc. that may already be located in the area. Any walk-in enclosures should feature hard-wired fire detection systems.

## System Signage

System signage is critically important for informing users, maintenance engineers and emergency services of the system, its operation and any potential hazards it may introduce. Drawing attention to the presence of a hazard or potential danger is a minimum requirement for mitigation of most health and safety risks associated with construction. Signage should be appropriate, effective and well maintained.

Signs warning of multiple electrical sources should be installed at the point of connection with the distribution network, any distribution boards or switchgear that are connected to the solar array (directly or indirectly) and at the inverter. Electrical schematics showing how the system is connected and the location of all key components and isolation devices should also be durably affixed at these locations. In addition, labels should be affixed adjacent to each circuit RCD and any isolation devices explaining their operation.

It is recommended that DC cable runs are labelled every 5 – 10m.

Guidance on appropriate signage for each part of the multifunctional system can be found in the corresponding IET Code of Practice Guides.

## Asbestos

The Contractors attention is drawn to the fact that Asbestos can be found on the site, an Asbestos register is held by the Employer, and can be viewed by the Contractor upon request.

Previous surveys have indicated asbestos is contained in the roof of the logistics building, and will need to be removed and disposed of as per current UK regulations.

## CDM

CDM will apply and the HSE needs to be notified. The Employer requires sight of all risk assessments, method statements and COSHH assessments prior to work being carried out. Work will not be able to commence without these been in place.

Should the Contractor believe that this project is “non-notifiable” then he should advise this in the tender return.

# CONTRACT INFORMATION

## Schedule of Works

Before a Tender is accepted the Contractor must submit to the Employer a fully priced quantified priced schedule of works upon which the Contractor's Tender has been based.

Should the Contractor not have included in the said documents specific costs for any of the work, services or obligations described in the Specification or shown on Tender drawings and schedules, he shall be deemed to have considered that the rates and/or sums for the work services or obligations included in the said documents are sufficient to enable him to carry out and complete the Works.

Rates and/or sums included in the said documents shall be deemed to include all related work which is not separately identified.

Changes in programme will require notification in writing to the employer.

## Variations

The Contractor shall execute any variation to the work or additional work, as may be ordered in writing by the Employers Representative. No work shall be carried out or be paid for, without such written authority.

# OBLIGATIONS AND RESTRICTIONS IMPOSED BY THE EMPLOYER

## Operation and Maintenance Manuals

Prior to Practical Completion the contractor shall provide a digital set of the completed O&M manuals to the Employers Representative. They are to include as a minimum:

- As built drawings showing details of all new installations, including solar panel layouts and any structural modifications made to the roof

- Wiring diagrams of all new plant and equipment

- Operating manuals for all new equipment

- Safety aspects in relation to the CDM regulations

- Frequency and details of routine maintenance requirements, including any spare components and manufacturer recommended site held spares

- Manufacturer’s literature for all components

- Statutory testing/inspection certificates, installation certificates and commissioning information as appropriate

## Verification of Sizes, etc.

The Contractor is advised not to scale from the drawings and verify all dimensions on site.

The Contractor, sub-contractors and suppliers must verify all sizes, quantities, descriptions, etc. from the Works, drawings and other documents before ordering materials or putting work in hand.

Imperial equivalents are to be used for any materials included in the Specification that is not available in metric sizes.

## Inspections and Tests

All new installations should be tested as stated in BS7671:2008 +A3:2015 Requirements for electrical installations.

The Contractor must give adequate notice to the Employer during the progress of the Works to enable any inspections, tests, commissioning, witnessing etc. to be carried out by the Employer.

## Building information modelling

BIM Level 2 is required by the Government on all public sector construction projects. Therefore, organisations in the construction industry must demonstrate compliance before the Treasury will release funding.

## Government Soft Landings

BS8536 parts 1 and 2 should be followed enabling a smooth transition from construction to operation.

## Access to and Possession or Use of Site

The Contractor must not use the site for any purpose other than that of executing the Works.  The Contractor must obtain the approval of the Employer to the proposed siting of all temporary structures, plant, materials, roads, paths, spoil heaps, etc.

On completion of the Works, the Contractor must remove from the site all temporary works plant, surplus materials, etc. and make good any disturbance or damage, including damage to the ground or structures, to the satisfaction of the Contract Administrator.

Any deliveries are to be via the Service Yard, which is accessed via the electronic security controlled gates to the West of the site. The Contractor is to become familiar with the restrictions concerning this access. Any deviation from this will need to be verified by the employer.

The storage of any flammable materials required for the works, is to comply strictly with all current UK legislation and shall not be stored within any building.

## Prevention of Nuisance and Trespass

The Contractor must take all necessary precautions to prevent any trespass on property adjoining the site by workmen, plant or materials under his control, and to prevent nuisance arising from the execution of the Works.

The Contractor must take all necessary precautions for the prevention of nuisance arising from dust, excessive noise and vibration.  The Contractor must discuss with the Employers Representative the measures he proposes to adopt to counter nuisances described above and must give notice of, and agree periods when, noisy operations and operations causing vibrations are to be executed.

The Contractor must allow for dealing with any complaints in connection with alleged nuisance arising from the execution of the Works and for making such arrangements and negotiations as may be necessary, including temporarily suspending any portion of the Works, and must include for everything required to enable the Works to be completed and handed over on the Contract completion date.

## Speed Limits

The Contractor must ensure that all vehicles are driven at safe speeds and in conformity with any speed restriction signs within the grounds.

## Vehicle Parking

Limited parking for the Contractors vehicles and those of all his staff will be advised by BAS. General parking is not permitted within the BAS Service Yard or Main Entrance car park.

## Overtime

The Contractor must obtain the written permission of the Employer before any overtime is worked.  The Contractor will not be reimbursed for the additional cost of any overtime unless it is specifically instructed by the Employers Representative.  Should such an instruction be given the Contractor will be allowed the net additional cost incurred, in accordance with the rules or decisions of the recognised wage fixing body concerned, in respect of working tradesmen and labourers only.

## Working Hours

Normal working hours are between 7am and 7 pm; however, the site will be occupied 24 hrs.

Noisy, dust and disruptive work that prevents the normal function of the space / building must be carried out, out of hours.

Access to the site outside of normal working hours will only be allowed through prior discussion with the Employer, as security arrangements are required to be made.

The Contractor is to include in his tender for all reasonable out of hours working.

A fully operational system must be active when work is completed each day.

## Advertising Rights

The Contractor must not permit or display advertisements on the site without the consent of the Contract Employer.

## Maintenance of Existing Services, etc.

The Contractor must protect, uphold and maintain all existing structures, live drainage, ducts, water, gas and other mains or power services and if any such items are damaged he shall be liable for and shall indemnify the Employer against any expense, liability, loss, claim or proceedings provided always that the damage is due to any negligence, omission or default of the Contractor's workpeople or those of his sub-contractors.

The Contractor must not make connections or interfere with the operation of existing services such as live drainage, water, gas or other mains or power services without the written permission of the Employer.

The Contractor must give ten days’ notice before any service is interrupted.

Isolation of services, i.e. water, electricity, gas – not without Employers Representative approval

## Site Specific Restrictions

Prior to the daily commencement of any works and at the end of each working day, all contract staff are to report to BAS reception and ‘sign in’ or ‘sign out’, using the Contractors Pass scheme.

No Smoking Policy – only permitted within agreed areas

Noise - The Contractor will be working, in close proximity to scientific research facilities. In most instances these facilities require low levels of noise disturbance, which may be in excess of those specified in the Noise at Work Regulations 1989. Work must therefore be scheduled to take account of this requirement.

The site has some restricted access areas including laboratories and clean rooms. This must be taken into consideration when programming the works. A change in programme will require 3 days notification in writing to the employer.

## Waste

Disposal of all waste produced from the works is to be disposed of offsite by the Contractor in a responsible and legal manner in accordance with all relevant Health & Safety and Environmental Regulations. The use of the BAS waste disposal system is not permitted.

The Contractor is requested to recycle as much waste as is practically possible.

The Contractor must remove all rubbish, debris, etc. at regular intervals as it accumulates and must remove all protective casings and coverings and clean the Works internally and externally. On final completion, all areas are to be given a ‘deep clean’ and left in a condition satisfactory to the Employers Representative.

The Contractor must keep a log containing the following information for each waste & debris disposal trip. This must also include all waste transfer notes from any skip hire that may be required for the duration of the works

•	Skip Hire Company and Disposal Site.

•	Contract Name and Disposal Site.

•	Vehicle ID – License Number.

•	Date of Disposal.

•	Time of Disposal.

•	Origin of Debris.

•	Location of tip

•	Net Weight. of Load.

The Contractor will hand over a copy of all waste tickets, fully completed to the Employers Representative each time waste is removed from site. All tickets must be handed to the Employers Representative by Practical completion. Practical completion may be withheld if all waste tickets have not been copied to the Employer.

The Employer reserves the right to audit the waste disposal process

## Supervision

All work must be carried out by, or closely supervised by workmen skilled in the appropriate trade.

The Contractor shall allow for all on and off site management costs and shall keep on the Works a competent General Foreman at all times and always in charge, who shall be considered the Contractor's representative on site and shall carry out the instructions of the Contract Administrator.  The presence of the Foreman on site from commencement to completion is obligatory and no departure from this condition or substitution for him by a Trade or Working Foreman can be permitted excepting on the written agreement of the Employers Representative.

## Water for the Works

The Contractor may connect to the existing supply.  However, it is the contractor’s responsibility to provide all necessary connections.

## Lighting and Power for the Works

The Contractor may use the site power supply, free of charge, to carry out the works. However, it is the Contractor’s responsibility to ensure sufficient power supplies and provide all equipment to provide the correct voltage.

The Contractor must provide temporary electric lighting and power distribution supplies for the Works. The temporary installations must be in accordance with BS and the current IEE Regulations.  Extension outlet units for portable tools must be provided within 20 metres of the point where the tool is to be used, measured by the actual route taken.  The Contractor must provide lighting for any temporary hoarding and the like.

All Equipment shall have a current PAT test certificate and be safe to use

## Temporary Accommodation

No temporary office accommodation will be provided by The Employer for the Contractor

The Contractor will not be permitted to use the existing building telephones.  The Contractor must provide any temporary telephone facilities that he may require.

## Mess Canteen Facilities

The Contractor may be permitted to use Canteen facilities when available on site, but must note the wearing of overalls or dirty work clothes is not permitted in the canteen.

## Toilet Facilities

The Contractor may be allowed to make use of an existing toilet, but this must be left and maintained in a clean state.

## Transistor Radios

The use of radios etc. by the Contractor's workmen will not be allowed.

## Attendance

The Contractor shall make all necessary allowances for attendance on his subcontractors including obtaining full particulars of requirements with regard to chases, holes, recesses, etc.; supplying all necessary dimensions and other information for the proper execution of the sub-contract work; free use of temporary roads and paving, standing scaffold, standing power operated hoisting plant; the provision of temporary lighting and water supplies; clearing away rubbish, provision of space for the sub-contractor's own offices and for the storage of his plant and materials, the use of mess rooms, sanitary accommodation and welfare facilities.

## Scaffolding

The Contractor is to allow for all necessary scaffolding, ladders, trestles, etc., for the due and proper completion of the job, and at all times complying with the appropriate Safety Regulation.

## Treasure Trove etc.

Any treasure trove, coins, or objects of antiquity, which may be found on the site, are to become the property of the Employer.

## Data Protection Act

The Contractor hereby undertakes that he and his Employees or Agents will treat as confidential and will not hold or publish in any form any personal data, as defined by the Data Protection Act, which they become aware of during the execution of this Contract and will not pass on such data to any other person or body.

The Contractor further undertakes that he will indemnify the Employer against all liability under the Act, arising from the failure of the Contractor or his Employees or Agents to comply with this undertaking.

# FIRE PRECAUTIONS

## Existing Structures

The Contractor must take all reasonable precautions to avoid the outbreak of fire, particularly in work involving the use of naked flames: such work must be examined at short intervals immediately following its completion.  Before any works of maintenance, adaptation or extension to existing buildings or services are carried out or connections to existing services are made, the Contractor must discuss his proposals with the Employers Representative responsible for fire precautions to ensure that the extent of any fire hazards in the Works are known fully to both the Contractor and the Employer.  The Contractor must draw the attention of all workpeople on the site to the dangers involved in the careless use of naked flames in proximity to combustible materials, disposal of matches, cigarettes, tobacco ash, etc., and of the accumulation of rubbish must be fully impressed on them. Smoking must not be permitted in roof spaces, service voids and other similar locations having a high probability of fire and workpeople must be required strictly to conform to all "No Smoking" rules applicable in specific areas of the site and existing buildings.

Fire protection compartments must be maintained and fire escape routes must remain unobstructed and where necessary illuminated.  The Contractor must provide and maintain suitable fire extinguishers.  The building's fire alarm system(s) must be maintained by the Contractor at all times.

## Fire Precautions Generally

The attention of the Contractor is drawn to the current HMSO Publication "Standard Fire Precautions P5 - to be taken by Contractors engaged on building and engineering works and maintenance for the Department of the Environment" and he must observe its recommendations where relevant to the Works.

Fire extinguishers and hydrants must not be obstructed and access to them must be maintained at all times.

The Contractor must remove all cylinders containing inflammable gases from buildings or enclosed spaces at the end of each working day.

Safe unobstructed escape from the building must be maintained at all times.

# MATERIALS, GOODS AND WORKMANSHIP

## Compliance

All work shall comply with the Building Regulations and the Regulations of the Local Authority and Statutory Authorities.

Materials and components shall be new, shall comply with BS or BBA documentation where such exists and shall be delivered to site in the manufacturers' wrappings where they are provided.

All self-finished and decorative materials and components shall be subject to selection and approval.

Workmanship shall comply with the appropriate CP where such exists and with other relevant authoritative documentation such as that published by the BRE.  Work of an aesthetic significance shall always be undertaken with particular care and attention.

Should any materials, components and workmanship be not fully specified the Contractor shall comply with good building practice and produce work fit for its designed purpose.

## Electrical Works

All Electrical works shall be carried out in accordance with the IEE Wiring Regulations 18th Edition BS 7671:2008.

## Tolerances

The Contractor shall work within dimensional limits that are suited to the structural stability and final appearance of the building; this requirement shall overrule any published or specified tolerances which refer to work in isolation (e.g. normally acceptable tolerances for structural concrete may be unsuited to the application of finishing work). Adjust the positions of the components and joints etc. within specified limits in order that the finished work has a uniform appearance.

## Setting out the Works.

Allow for all expenditure in connection with setting out the Works.  The Contractor shall be responsible for the setting out of the Works and shall, entirely at his own cost, amend any errors arising from his own inaccurate setting out.

## Dust Sheets and Protection

The Contractor is to supply and fix all necessary dustsheets and temporary screens to adequately protect all adjoining areas, furnishings, etc. during the execution of the work and he is to allow for clearing up and leaving clean each evening.

## Making good

The making good of structures after cutting away and similar work will be deemed to be included in every instance.

## Plant, Tools and Vehicles

The Contractor must provide all plant, tools, vehicles, implements and machinery necessary for the execution of the Works.

## Temporary Fencing, Hoarding, etc.

The Contractor must provide temporary fencing, hoarding, screens, fans, planked footways, guard-rails, gantries and similar items as may be necessary for protecting the public and others for the execution of the Works.  The Contractor must provide all necessary lighting

## Inclement weather

The prices shall include for working during any type of weather which is averse to the progress of the Works, subject to and including taking all precautionary and protective measures that can reasonably and practicably be taken.

## Fixings generally

Any packing slips or additional grounds etc. to those detailed and sundry minor improvisation needed to ensure dimensionally correct and secure fixings shall be deemed to be included in the prices of all components fixed into the building.

Visible fixings shall be complementary to the finished work and all fixings shall be compatible to the work being fixed and the background, proof against rust, electrolysis and any other form of corrosion.

Fixings involving drilling into backgrounds (e.g. plugging and screwing, expansion bolting) are not separately described for new and old backgrounds.

## Commissioning

The whole system is to operate in accordance with BS 7671:2008 +A3:2015

•	All equipment operates correctly as per manufacturer’s instructions.

•	Installation work is, as far as reasonably ascertained, of an acceptable standard.

•	The entire system has been inspected and tested

# Design

## Overview

The works are to be carried out across two buildings on the same Cambridge site:

The logistics building requires removal and replacement of the existing roof. Along with installation of new doors, windows and roller shutters. Finally, an installation of at least 200 kWp of solar cells and infrastructure will complete works to this building.

On Science building 2. At least 140 kWp of solar cells are to be fitted to the existing roof, along with all necessary infrastructure.

Both solar arrays will be connected to the existing site electrical distribution, and a 200kW exportation limitation device shall be installed as specified by the DNO.

## Scope of construction elements involved with roof upgrade project and phases

The building works involved within the project are split over two phases, phase 1 works are to be completed by March 31st 2021 and phase 2 works completed by March 31st 2022. To minimise the disruption to users, it is BAS’s intention to complete the building works on an east side and west side, half and half basis. With the east side being complete over phase 1 and west side over phase 2.

## Asbestos removal and disposal

It is the intention of BAS to remove and dispose of any asbestos identified in a 2020 asbestos survey report, which will require to be disturbed during the roof upgrade project.

## Replacement of existing roof sheets to logistics building

It is the intention of BAS to remove all existing roofing panels and replace with insulated roofing panels. This is planned for the entire logistics building, this includes renewing with facia, eaves board, barge boards and soffit board. However, to minimise the disruption to users, BAS is intention is to complete the building works on east side and west side, half and half basis.

## Re-rendering of east side of logistics building (Phase 1)

The scope of this project also includes the re-rendering of all external wall space of the logistics building, the preferred option is to overcoat the existing wall render with thermal enhancing coating.

## Replacement of all existing windows and doors to east side of logistics building (Phase 2)

Part of the project scope is to enhance the insulating properties of windows and doors. Therefore, BAS has seen fit to replace all doors and windows (including roller shutters) with products that have improved thermal efficiency – roller shutter doors to match existing new door.

## Preparation of roof on logistics building and Science building 2 to carry solar PV’s

Given the main aim of the project is to enhance the solar efficiency of the site, all structural preparations needed for the roof must be made ready for solar PV install are included within the scope of this project.

## Location and areas of building work

- Area of planned roofing works   - Roof panels containing asbestos

## Asbestos removal and disposal (phase 1)

During a R&D asbestos survey carried out between December 2019 – February 2020 on our logistics building, a number of areas and materials were identified as potentially containing asbestos fibres. These areas and materials were tested by Thames Laboratories and resulted in a positive test for Chrysotile. Some areas of the site were seen as ‘low potential to release asbestos fibres’, however no areas were seen as above low risk (please see attached asbestos survey report for risk/score matrix).

Although no areas were deemed to be an immediate risk to staff health and safety, BAS has seen it appropriate to include the removal of the asbestos roof sheeting identified in the recent survey, in the project scope for the solar roof upgrade.

## Asbestos contactor or sub-contractor requirements

The successful contractor or sub-contractor must provide the following as minimum requirement

- Relevant insurance documents.

- Detailed plan of work or method statement.

- Training records or certifications for all staff and personnel directly involved with asbestos removal.

- All other documentation in accordance with the Control of Asbestos Regulations 2012.

- Risk assessments and COSHH assessments.

- A clearance and/or waste transfer certificates for the record keeping purposes of the client.

- Inspection/test records for any plant and/or heavy machinery that may be used on site.

- The contactor shall be able to produce any of the above documents upon request of the client.

- Where the asbestos removal contractor becomes aware of/or creates any significant hazards which have not been highlighted in the R&D survey client immediately.

- Any scaffolding, edge protection and fall arrests etc. are provided by the contractor or sub-contractor.

- On completion of asbestos removal, a deep clean and air test of internal areas and workspaces below the asbestos roofing

## Temporary boarding

The workshops and offices within the logistics building all contain very sensitive and expensive equipment, this equipment MUST be protected at all times during the project. The ideal solution to minimize this risk would be to encapsulate the working area using Ply sheeting fixed to the underside of the existing steel rafters, however if the contractor of subcontractor proposes a similar solution, this will be considered by the client.

## Testing and potential contamination

Though there is no requirement to carry out a daily air or surface test for potential contamination, the contractor must carry out tests if there is reason to believe contamination has occurred. The contractor must also inform the client immediately if contamination of the below surfaces or workspace is to believe to have occurred

## RPE and PPE

The asbestos contractor or sub-contractor will provide correct RPE and PPE for all staff directly involved with the asbestos removal in compliance with Asbestos: The Licensed contractors’ guide. The contractor/sub-contractor is always responsible for the upkeep and suitability of RPE and PPE.

## Asbestos waste containment and disposal

The following assumptions have been made regarding asbestos waste;

- All waste material involved or disturbed with the removal of roof sheets in logistics building shall be treated as contaminated.

- All waste materials should be encapsulated by means that keeps the risk of spillage to lowest practically possible.

- All areas of removal works shall be free of waste material at the end of each working day.

- Waste material shall be transferred by vehicles provided by the contractor or sub-contractor for transport to a licenced asbestos waste-tipping site.

- The transfer of waste from site to should be in accordance with the Control of Pollution Act 1974 and the Hazardous Waste Regulations 2009.

## Hygiene facility

The contractor or sub-contractor must provide a hygiene facility for those who are directly involved with the removal of asbestos or will come into the zone where asbestos may have disturbed. Due to the lack of services and suitable drainage, the facility must be modular/ self-contained. The location of the hygiene facility shall be agreed between the contractor and project board on site at a later date.

The contractor is responsible for the upkeep and maintenance of the hygiene facility. Also, the contractor shall ensure the facility is secure when not in use.

## Removal of existing roof sheets (West Side of Logistics Building)

Removal of existing roof sheeting on the East side of logistics building is covered in sections 6.9-6.15. This section will cover assumptions and requirements for the west side of the logistics building. The requirements and assumptions for the removal of existing roof sheets NOT containing asbestos are as follows;

- Any scaffolding, edge protection and fall arrests etc. are provided by the contractor or sub-contractor.

- The disposal of any roof sheets or any components associated with the roof sheets will be disposed of in the correct manner correctly and arranged by the contractor or sub-contractor. Copies of any waste transfer documentation will be supplied by the contractor to the client.

- The contactor shall provide any and all temporary coverings needed to protect the internal equipment of the logistics building, whilst removal works are happening.

- When transporting the existing sheets from the roof to ground level, a safe and suitable method of handling should be adhered to at ALL times.

## Roof purlins

It is preferred by the client that the existing purlins remain in place to reduce the timescale and cost of the project. However, if the new roof sheet system requires the existing purlins to be replaced, the contractor or sub-contractor should propose this into the tender bid.

## Replacement roof system performance

The requirements for the new roof system are as follows;

- The new roofing sheets MUST have thermal enhancing performance. A pre-manufactured, corrugated profile, insulated roof panel is the desired option by the client.

- The roof system shall take into consideration all loading factors associated with the facility and the surrounding environment. In particular the new solar PV panel loading. As the contractor or sub-contractor, the client assumes the PV panel loadings will be calculated and shown in the design proposal. Structural engineers report will be provided to the successful bidder upon completion of the tender.

- There is no requirement, by planning authorities, for the aesthetics of the new roofing system to conform to any particular architectural style of the existing facility, the new roofing system should be harmonious with the surroundings and aesthetically pleasing.

- The logistics building roof changes pitch roughly halfway along. This is the divide between east and west side. The two sides MUST match regarding corrugation profile and colour, this should be considered by the contractor as the two sides are split over two phases of the project.

Quality assurances are as follows;

- The proposed Manufacturer, of the roof sheeting, should be a reputable roofing product manufacturer. This is to ensure that the procured product is of a consistent and acceptable standard that has been tested and proven.

- The contractor should provide technical/product data within the tender bid of the proposed roofing product.

- The contractor shall be an experienced installer of panelled roof systems having a portfolio of past projects.

- Pre-Construction meeting should be conducted prior to the start of the roof installation to finalize any outstanding issues, questions or details regarding the installation of the roof.

- The roof should withstand a heavy rain test after installation to ensure correct installation, before any PV panel installation work goes ahead.

- Install roof panels in accordance with manufacturer’s installation manual, recommendations and advice. All roof panels MUST also be without waves, warps, buckling, fastener stress, or distortion.

## Guttering system

The logistics building has an internal guttering system with the downpipes being located inside of the building. To reduce the impact of building works to site users, BAS intends to maintain the current internal guttering system. The contractor should familiarise themselves with the guttering system during a site visit.

## Personnel Doors

These are the requirements for the replacement external doors,

- All personnel doors that are to be replaced should be uniform across the logistics building.

- All doors are to be heavy duty steel, with thermal enhancing qualities.

- All door furniture is to be renewed with heavy duty door furniture.

## Windows

These are the requirements for the replacement windows in the logistics building,

- All windows that are to be replaced should be uniform across the logistics building.

- All windows are to be coated aluminium frame with double glazing to enhance the insulating properties of the building.

## Roller shutters

A number of roller shutter doors will also be required to be replaced, the following requirements are to be met,

- All roller shutters are to match newly replaced roller shutter doors.

- All roller shutters should be electronically operated, but should have a manual override and anti-trapping capabilities.

- All roller doors are required to have personnel access door.

## External wall render

The requirement for the wall render is as follows

- All external walls of the logistics building are to be re-rendered, however this will be over two phases.

- The render must be able to overcoat onto the existing render.

- The new render coating must enhance the insulating properties of the building.

- The new render coating must be aesthetically pleasing.

- The contractor will adapt any light fittings, alarm sounders, cable tray and any other external fittings when re-rendering the building.

## Solar PV specification

The Contractor will design, supply, install and commission two PV installations across site.

## Component 1: Solar Panels

The Contractor should propose specific type of solar panels based on the following parameters:

•	Quality criteria, including Tier 1 products

•	Panel efficiency

•	Cloudy days and low light performance

•	Product performance (power output) after lifespan

•	Manufacturer reliability (solid reputation, test results, warranty, service) ensuring product continuity to backup any warranty issues.

It is important that the Contactor shall receive specific recommendations from the Manufacturer of the panels for earthing arrangements for the DC system to reduce or reverse the effects of the PID. This is mainly because of particular types of PV modules can be prone to potential induced degradation (PID), a voltage potential between the PV module and the ground that can reduce PV module performance. The effects of the PID can worsen in PV systems that experience high levels of humidity, temperature and soiling.

The PV module casing and pre-fitted connector cables should be double insulated (safety class ll) as recommended by BS 7671 for any system where the string voltage (VocSTC) exceeds 120Vdc in order to minimise the risk of fire and electric shock.

Using polarised connectors prevents incorrect polarity connections in the system. It is important that polarised connectors from different manufacturers are not coupled together and all connectors are suitably rated to ensure safe operation of the system.

A suitable bypass diode configuration should be selected with respect to the carport array layout (e.g. PV modules in landscape or portrait) and with respect to any potential shading to reduce the effect of shade on the output of a module.

Any PV module selected should be certificated to ‘BS EN 61730. Photovoltaic (PV) Module Safety Qualification’. Any structural glazing materials used in the construction of PV modules (as a superstrate or substrate) must also comply with the standard for safety glazing in ‘ANSI Z97.1-93. American National Standard for Safety Glazing Materials Used in Buildings’. If further safety testing of glazing is needed, reference to the BS 5516 Series ‘Patent Glazing and Sloping Glazing for Buildings’ should be made. In addition, further certification of PV modules under the Microgeneration Certification Scheme (MCS) product standard MCS 005 is welcomed.

All solar systems should use certified & CE marked PV modules. Crystalline modules should be certified to IEC 61215 & IEC 61730 and thin-film modules should be certified to IEC 61646 & IEC 61730.

## Component 2: Inverters

In order for the system to integrate with our current PV monitoring and fault detection system, all Inverters and power optimisers should be manufactured by SolarEdge and be fully compatible with the SolarEdge monitoring system.

Solar inverters should optimise output from the PV modules by using maximum-power point tracking of the string voltage.

Performance should be optimised delivering more energy for the system lifetime by controlling the PV system at module level. This way differences related to individual set of characteristics of each panel is accommodated. Monitoring each panel individually is essential in order to detect errors by the monitoring system. The inverters system should minimise the risk of reduced output due to shading or different orientation.

All panel level DC electricity should be kept next to the panels. Only when the inverters send a control signal should the system operate. In the event of a fire, or grid failure the fire brigade should be reassured that only the panels are ‘live’. Automatic shutdown feature of the system in the event of a fire alarm triggering and not just waiting for the main electrical isolator to be shut off should be included. All communication within the system should be performed through existing DC cabling which is the most reliable method of transmitting data.

Essential inverter beneficial elements required:

•	Automatic shutdown of each module for maximum safety

•	Wired communication, not wireless for better reliability

•	Incorporates all communication and system control in optimisers and inverter

•	Safe DC

•	Individual module performance visibility

•	Automatic alerts on system issues text/email

•	Easy access online monitoring of individual panel performance and faults via computer, smartphone or tablet

•	Centralised single point contact for onsite support and troubleshooting

The Contractor should advise on the available options for positioning location for inverters and electrical connections, taking into account the need for clear access to the car parking space. Safety and security of inverters should be considered when selecting technology options.

Inverters should be from SolarEdge and to be open protocol (BacNet or something similar) to allow potential connection to building management system.

In addition to the electrical characteristics of the PV array, the solar inverter(s) should be selected with respect to the distribution network connection capacity available.

All inverters should be CE marked, comply with BS EN 62109 Series. ‘Safety of power converters for use in photovoltaic power systems’ and BS EN 62116 ‘Utility-interconnected photovoltaic inverters’ and must be either type tested to the relevant Engineering Recommendation (G83/ G59/ G98/ G99) or have an additional G59 relay which has been witness tested by the DNO.

Type testing provides evidence that the inverter will provide the following protection to the distribution network:

•	Under-voltage

•	Over-voltage

•	Under-frequency

•	Over-frequency

•	Loss of mains

## Component 3: Mounting System

The PV glazing system should be well executed as such to reduce the use of materials and project costs. The system should also ensure water tightness, structural strength and fire resistance.

The design of the solar installation should include wind loading and wind induced effects (correct pressure coefficients chosen), self-weight of the PV module and mounting frame, snow loads, and loads imposed during construction .In the absence of existing standards, certification of a solar carport mounting system can be achieved under MCS product standard, MCS 012, demonstrating resistance to external fire spread, weather tightness and wind uplift resistance.

## Electrical Supply characteristics.

The Electrical supply on site is 3 Phase and Neutral. Voltages are L-L 400V, L-N 230V at a frequency of 50Hz.

## Protection against electric shock

The 17th Edition of the I.E.E. Wiring Regulations allows alternative methods of protection against electric shock. For the purpose of this Specification, protection against direct contact with live parts shall generally be by the use of the following measures:

- Protection by insulation of live parts.

- Protection by enclosures.

The basic protection measure for protection against indirect contact shall be by earth equipotential bonding and automatic disconnection of the supply. All necessary earth bonding as is detailed in the Wiring Regulations (Section 413) shall be carried out.

Protection devices providing automatic disconnection shall generally be fuses to B.S. 88, Part II, and/or miniature circuit breakers to B.S. 3871. The characteristics of these devices, the earthing arrangement and the circuit impedances shall be co-ordinated to provide protection against indirect contact with live parts. Where residual current devices are specified, they shall be to B.S. 4293.

## System losses

The system design, component selection and system maintenance plan should take into account a number of system losses involved in the functions and processes of the multifunctional solar car park system in order to mitigate their impact. System losses can be categorised as follows:

•	Solar conversion losses (solar cell temperature, PV module quality, PV module mismatch, soiling, shading, internal wiring losses)

•	DC/AC Conversion losses (inverter efficiencies, MPPT losses50, EV charging efficiencies) – Distribution losses (resistive connections, I2 R losses51)

•	Auxiliary system losses (power consumption for ventilation/ monitoring/ control systems, inverter power consumption at night)

•	Downtime losses (grid conditions, faults, component failure, maintenance, restricted distribution network connection) Current guidance on voltage drop in conductors should be observed i.e. maximum 5% for AC distribution circuits, 3% for DC circuits, 1% for AC inverter circuits and 1% for solar circuits.

## Monitoring

Appropriate monitoring and control systems should be selected and installed for the safe operation of the whole system.

A number of the components installed will have their own inbuilt monitoring systems, such as the inverters and DC combiner boxes.

It is a requirement that the proposed system includes the capability of remote monitoring of each panel performance individually through an online platform in order to identify potential issues.

## Electrical design considerations

There are a number of safety legislation, standards and considerations that should be factored in to the system design. All components should be designed, manufactured and tested in accordance with relevant safety standards (see Appendix A for more details). The electrical system as a whole will need to comply with the following regulations;

•	Electricity at Work Regulation 1989

•	Electrical Safety, Quality and Continuity Regulations 2002

•	Electrical Equipment (Safety) Regulations 2016

•	Electromagnetic Compatibility Regulations 2016

•	Control of Electromagnetic Fields at Work Regulations 2016 – BS 7671 (IET Wiring Regulations)

•	ENA Engineering Recommendations G59, G83, G100, G98 or G99 (as appropriate)

•	BS7671:2008 Requirements for electrical installations

•	CIBSE Guide F 2012, Energy efficiency in buildings

•	CIBSE Guide K, electricity in buildings

•	Building Regulations Part L2A 2013 and associated Codes of Practice

•	The Health and Safety at Work, etc. Act 1974

•	The Health and Safety at Work Regulations 1992

## DC system

Unlike other DC circuits, PV arrays do not provide a fixed voltage and/ or current output, as this varies with the solar irradiance and operating temperature the PV modules are exposed to. It is therefore important to ensure that other components within the system are able to tolerate the maximum voltage (open-circuit voltage, Voc) and current (short-circuit current, Isc) that the PV modules, strings, and arrays can produce.

For PV circuits it is recommended that the minimum rating for all DC components should be established, using the crystalline PV module characteristics under standard test conditions (stc), as Voc (stc) x 1.15 and Isc (stc) x 1.25.

For non-crystalline PV modules, the Voc and Isc should be calculated from manufacturer’s data as the maximum value under the conditions of irradiance: 1,250 W/m2, temperature range: -15°C to 80°C, including any increased electrical rating expected during the ‘soaking in period’.

As PV modules generate electricity whenever exposed to daylight they should always be considered to be live, as should all connected DC components. Particular care needs to be taken to mitigate electrical shock and fire hazards during the installation, operation and maintenance of systems.

## DC connectors

DC solar connectors should be class II rated and certified in accordance with BS EN 50521 ‘Connectors for photovoltaic systems – safety requirements and tests’.

To ensure safe functionality, only DC solar connectors of the same type and from the safe manufacturer should be connected together and assembled as per the manufacturer’s specification. This is to avoid fire risk from poorly fitted, specified or mismatched DC solar connectors.

All live DC connections should be protected and located out of the reach of the general public.

All DC connections should be periodically checked to confirm that they are tight and secure (referring to manufacturer for torque setting).

## DC isolation and circuit protection

PV cells are current-limiting devices and therefore the short-circuit current of a PV module; string; or array is not much bigger than the operational current. DC isolation and circuit protection requires careful selection.

The selection and specification of DC safety equipment depends on the inverter configuration and earthing arrangements. Current discrete RCD technology is not suitable for the protection of DC circuits. All system components should be specified in line with BS 7671.

DC isolators are a safety-critical component. The poor design, selection and installation of DC isolators has been the cause of a number of system failures and on occasion leading to other more serious incidents, such as fire. Suitable methods should be used to isolate the system at; PV string, PV sub-array, PV array and battery level. Not all methods are suitable to break DC circuits under load, i.e. DC connectors and removable fuses.

Switch-disconnects provide both load-break-switching and isolations function. DC switch-disconnects must comply with BS EN 60947, shall not be polarity sensitive and must isolate all live conductors.

Suitably specified double pole DC isolation devices should be installed as close as possible to, or as part of, overcurrent protection devices for both PV arrays and batteries (regardless as to whether they are connected to the DC or AC side of a system).

Effective DC protective devices safeguard equipment against adverse operating conditions and help to ensure that the system is safe. The DC side of the system should be protected from overcurrent and overvoltage.

String fuses are required when the short-circuit current from a number of parallel PV strings is greater than the maximum series fuse rating of a single PV module. String fuses are installed at the point where PV strings are connected in parallel, typically a DC combiner box or inside the inverter. The earthing arrangement for the PV array will dictate whether one or both string cables require overcurrent protection.

DC combiner boxes provide easy access and simple arrangement of protective and isolation devices for larger systems. The DC combiner box should be rated for the maximum voltage and current conditions (under stc) of the system and take into consideration segregation between positive and negative parts, permitting safe installation and maintenance and to minimise the risks of arcs. All enclosures should be manufactured using insulating materials with self-extinguishing properties to help minimise the fire risks.

DC insulation faults can occur for a variety of reasons; water ingress, environmental damage to insulation, damage to cables etc. Selecting quality, robust components and following good installation practices will minimise the likelihood of problems developing; however, it is important to implement fault-detection measures. Earth insulation resistance and residual current monitoring devices should be utilised to detect insulation faults and trigger earth fault alarms; these can either be incorporated within inverters or provided by separate devices.

There are three types of DC arcs; series, parallel and ‘to ground.’ DC series arc fault detection is normally provided as a protective device integral to the inverter to reduce the risk of fire should a series arc develop. Rapid shutdown devices are also available that isolate the affected part of the circuit down to PV module level should a DC arc be detected. An assessment should be made of the risk posed by potential DC arc faults and how best to mitigate these within the system.

All DC isolation and circuit protection equipment should be easily accessible and clearly identified on electrical schematics and safe isolation procedures.

Access to any uninsulated conductors and batteries should be restricted and arranged so that it is not possible to touch simultaneously two uninsulated conductive parts with a potential difference of >120Vdc.

## AC system

As with any electrical installation in the UK, multifunctional solar car systems are required to be designed and installed in compliance with the current wiring regulations, BS 7671.

## AC Isolation and circuit protection

In order to facilitate safe installation and maintenance, the inverter must have its own accessible and lockable AC switch that isolates all phase and neutral conductors. This switch may be part of the inverter.

For multiple inverters, an additional ‘main’ AC isolator should be installed to disconnect all inverters simultaneously. Often this is facilitated as part of a dedicated sub-distribution board.

All AC isolators should be rated to break the circuits safely while under maximum load.

An over-current protective device should be provided for each inverter circuit, and RCD protection should be provided in accordance with BS 7671. All protective devices should be selected in accordance with the inverter manufacturer’s instructions.

## Cabling

Cables should be rated for the maximum voltage and current-carrying capacity for the circuit as per BS 7671 and specified to ensure safety, reliability and to minimise voltage drop and energy losses. Inverters continuously monitor the supply voltage and frequency, and nuisance tripping may occur if there is a significant voltage drop between the distribution network connection point and the inverter.

All cables should be identifiable by colour and alphanumeric marking and selected and installed so as to minimise the risk of earth faults and short-circuits, using double insulated or reinforced cables will help achieve this. PV cables are required to comply with BS EN 50618 ‘Electric cables for photovoltaic systems.’ Consideration should also be given to the routing of cables, ensuring selected cables provide adequate resistance to any environment that they may experience, i.e. moisture, sunlight, heat, chemicals, abrasion or animal damage. AC and DC cables should be separated and clearly identified.

Adequate space should be provided for the routing of cables to enable good installation practices. All cables and connections should be adequately supported using conduit, cable cleats, cable clips, cable ties etc. to minimise the stress from wind or thermal effects and to provide safe continual operation throughout the lifetime of the system.

## System earthing and bonding

Systems earthing must satisfy the requirements of the Distribution Licence issued by the DNO. The design and selection of suitable earthing and bonding arrangements will ensure hazards are minimised by providing an appropriately low impedance path for earth, fault and lightning currents.

Earthing and bonding of the AC side of the system should be completed in accordance with BS 7671, conform with the requirements of BS 7430 ‘Code of Practice for protective earthing of electrical installations and BS EN 50522 Earthing of Power Installations Exceeding 1kV AC,’ satisfy the DNOs requirements and comply with equipment manufacturer’s instructions.

As per BS 7671, the type of earthing arrangement on the supply circuit (i.e. TN-C, TN-S, TN-C-S or TT) will dictate how adequate protection against electric shock should be. The earthing and bonding arrangements detailed in Table 8.1 should be considered for all multifunctional solar systems, and the most demanding requirement applied. Earth cables should be laid parallel and in close contact to DC cables to reduce the risk of multiple paths to earth and should be appropriately sized to afford sufficient conductance.

## Metering

The energy metering system should include electrical meters for the:

•	Electricity generated (at point of generation) x 2

•	Electricity exported (at the point of connection between the installation and the distribution or transmission network) x 1 as specified by the DNO.

The works must include the incorporation of metering to monitor cumulative energy generation (kWh) and rated output (kW) which is compatible with the BAS Energy Monitoring System provided by Elcomponent.

## Lighting and surge protection

The possible effects of a direct or indirect lightning strike need to be considered. A lightning and surge protection risk assessment, including of data or control circuits and existing lightning protection system (LPS), should be carried out according to BS EN 62305.

If the risk assessment indicates the need for lightning and surge protection then appropriately rated devices must be selected and installed in the correct lightning protection zone (LPZ) as detailed in BS EN 62305. For multifunctional solar car parks this will normally mean the installation of Type 1 and/ or Type 2 surge protection devices (SPDs).

## Decommissioning plan – End of life considerations

The project should be designed with decommissioning and end of life responsibilities, in accordance with the good practice required by the CDM regulations. This should not only include the practicalities of dismantling and removing the infrastructure of the solar systems, but also detail how the waste will be dealt with, any associated environmental impacts and what restoration work is required/ will be completed.

The decommissioning plan should clearly state how the applicable waste regulations  will be met, identify any reusable or recyclable components of the system and how these will be managed (i.e. through compliant waste management services such as PV Cycle ), and detail how other waste will be segregated and disposed of.