Update to the Environmental Control Equipment Tender document

27/11/2017

NML would like to inform bidders of changes to some information in the tender document that may be pertinent to calculations for the tender responses.

Section 1.4 ‘Existing Solution’ states that…

‘…Throughout the duration of the exhibition the air-exchange rate will be 1 full change of approximately 5000m3 per hour…’

Bidders should be advised that the work and testing currently being carried out to the air handling system for this gallery indicates you should calculate for two air changes per hour for the whole gallery (5000m3) in your tender returns.

A majority of the air within gallery will be recirculated with a lesser quantity of fresh air added to air input to control CO2 levels. This should help retain a majority of the air treated by humidifiers or dehumidifiers. Work is currently being carried out to assess the percentage of fresh air feed required.

Section 5.3 ‘Additional  gallery design considerations:’

Explains that…

‘… • The maximum gallery ceiling height between ceiling beams is approximately 5.2m, the approximate height to the underside of the beams is 4.8m and the height of the inner display walls is 4.8m. This therefore leaves a maximum gap between ceiling beams and above the top of the side display walls of 0.4m. This wall lines both sides of the entire gallery…’

NML would like to ensure bidders consider and advise on whether 0.4m headroom above the top of display walls will provide sufficient space to allow for movement of conditioned air from voids behind these walls to the display area in the centre of the gallery.