## Drop Codes (hidden)
RoomClassification | IA | QualificationTest
Not Classified | Direct Impact | Yes
Grade A | Indirect Impact | No
Grade B | No Impact | n/a
Grade C
Grade D

## URS Document
User Requirement Specification |  |  | CPI Internal Tender Reference & Title:- | 1562 | Air Compressor Upgrade for CPI Darlington NBMC
| The evalution team will consider bidders combined responses below and give a single overall score based on the adjacent rating in column D, of which the total Quality element score of this sheet will equate to value in column G |  |  |  | The total percentage available which will contribute towards the Quality scoring element of this tender is contained within column G, of which the evaluation team will assess in the "Office Use Only" section below at the base of this form | 40%
USER REQUIREMENT |  |  |  |  | Tenderer Response
Requirement codes |  |  |  |  | Guidance: Tenderers must provide responses within the following Columns;
M | Mandatory. (This must be the minimum requirement for the usage for the equipment, any further performance requirements above the minimum, must be marked as Desirable) |  |  |  | 1. Column F - Please provide details of your equipment functionality in relation to CPI requirements specified in column E
O | Optional requirement which may be quoted for and an assessment made by CPI prior to purchase |  |  |  | 2. Column G - Please confirm if your product complies with CPI's functionality requirements specified in Column E, by providing a Yes (Y) or No (N) response
D | Desirable, but not necessary - if this can be supplied. Tenderer should suggest alternative if appropriate
Parameter |  | Requirement |  | Requirement (M/O/D) -see codes | Answer or Details with regards to meeting the Requirement | Complies? (Y/N)
System performance
1 | Compressed Dry Air (CDA Supply) | Compressed Dry Air (CDA) Quality requirement is Particulates, Moisture and Oil Content equivalent to ISO 8573-1 Compressed Air, Part 1 Contaminants and Purity Classes, Class 2 |  | M
2 | Compressor Type | The new compressor must be oil-free, rotary screw type, air cooled- variable speed, working Pressure 7.5 bar g, with Drive Motor and Electronic Control & Monitoring, Known Noise Level |  | M
3 | System Upgrade | A new variable speed compressor must be installed as the primary unit for routine operation with the existing fixed speed unit (CompAir D22H 125cfm unit) to become a backup |  | M
4 | New Primary Compressor Size | The current fixed speed CDA compressor unit is 22KW (CompAir D22H 125cfm unit), and the new variable speed compressor (which is to become the primary unit) is to be able to turndown to operate at ca. half the current duty i.e. ca. 11kW (compared to current 22kW). The upgraded system must also still be capable of operating to provide at least the original system capability. |  | M
5 | System Capability | The system must be able to retain the capability of the existing air compressor (CompAir D22H 125cfm), which will become a pure backup i.e. the upgraded system must still be capable of operating to provide at least the original system capability via this as a backup unit |  | M
Installation & Utilities
3 | Installation | Any installation works must be performed by qualifed engineers and meet required safety and regulatory standards for a validated Compressed Dry Air (CDA) Installation |  | M
4 | Siting | The new primary air compressor is to be sited in the ground floor plant room next to the existing CDA compressor (CompAir D22H) and drier unit |  | M
5 | Extract | Hot air extract will be connected into the current ductwork and a summer/winter damper is to be included for heat recovery |  | M
6 | Pipework | Compressed dry air (CDA) must be conveyed in de-greased copper or 316L stainless steel small bore pipe. Pipework shall be installed in a neat and tidy manner and independently bracketed with spacing’s to comply with HTM 02-01. The pipework infrastructure has been sized on the assumption that a maximum of 25% of the process outlets and 25% of the instrumentation outlets are operating at any one time. |  | M
7 | Non-metallic Contact Parts | Non-metallic materials in contact with the product such as elastomers (e.g. silicone rubber, etc.) or polymers (e.g. PTFE or EPDM) shall be of pharmaceutical grade sanitary construction and shall be in conformance with 21CFR 177.2600. |  | M
8 | Site requirements | A full site requirements guide for any new equipment is to be provided as part of the Tender response, including requirements for specialist lifting and manual handling equipment |  | M
9 | Utilities: Electrical Power | The system is expected to require a 3 phase supply |  | D
10 | Site downtime | The installation approach must be able to minimise down-time of the CDA system, as it provides the CDA both to instrument air and process air users across the whole CPI Darlington site |  | M
Software and Connectivity
11 | Connectivity | Alarms on equipment must connect to the CPI Facility Building Management System (BMS). |  | M
12 | Monitoring | Remote monitoring capability for the CDA supply system is required including system status |  | M
Regulatory, Support & Warranties
13 | Validation | The CDA system upgrade must be validated to the same level as the original system, using the requirements in this URS. The vendor must be able to provide a validaton package including Design Qualification, Installation Qualification, Commissioning and Operational Qualification. |  | M
14 | Regulatory Standard | As per the existing CDA system, the work shall be in accordance with the requirements and recommendations of the NHS Model Engineering Specification C11 'Medical Gases', the current edition of 'Hospital Technical Memoranda (HTM) No. 02-01 Medical Gas Pipeline Systems', Medical Compressed Air Installations, Pressure Systems Regulations and Health and Safety Regulations. |  | M
15 | Safety Standard | Equipment must comply with UK safety standards for Compressed Air Supply, namely compliance to the applicable BCGA Code of Practices |  | M
16 | CE Marking | Equipment shall be permanently CE Marked to confirm that it is in accordance with all relevant EU Directives, and a suitable conformance certificate shall be provided. This includes comformance to the Pressure Equipment Directive (PED) |  | M
17 | Pressure Systems | Equipment shall comply with the UK Pressure Systems Safety Regulations (PSSR). |  | M
18 | Manuals | Operational & Maintenance (O&M) manual is to be provided including drawings, with 2 copies in paper format and 1 in electronic format |  | M
19 | Training | Full training should be provided along with access to technical support |  | D
20 | Warranties | Warranty period is to cover at least 12 months from installation |  | M
21 | Extended warranty | Extended warranty of up to 6 years |  | D
22 | Service support | On site support within 12 hours of requesting assistance. Please provide details of expected call-out charges. |  | D
23 | Service support | Details of preventative maintenance programmes required (if any) above Warranty requirements |  | D
OFFICE USE ONLY - This section below this line is for CPI Evaluation and Internal USE only
| Notes for Evaluation Team: |  | Name of Bidder to be inserted here | 1562 | Air Compressor Upgrade for CPI Darlington NBMC
Please assess all of the answers given, with particular attention to the Mandatory answers provided, taking into account, the Desirable and Optional answers too, however, you do not need to score each individual answer, but based on the scoring range 0-5, just give one singluar score (default set at "5" in the red and yellow box below, and as we have to provide feedback to bidders, you must also provide comments on which section(s) above where you felt that they did not meet the requirements.
| Evaluation Panel |  | Name of CPI Evaluator to insert here | dd/mm/yyyy | Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements | 5
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
|  |  | Name of CPI Evaluator to insert here | dd/mm/yyyy | Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements | 5
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
|  |  | Name of CPI Evaluator to insert here | dd/mm/yyyy | Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements | 5
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Comments on which section(s) they felt the Bidder did not meet fully or partially the above requirements
Head Office: CPI, Wilton Centre, Wilton, Redcar, Cleveland, TS10 4RF, UNITED KINGDOM
Tel: +44 (0)1642 455 340 Email: info@uk-cpi.com Web: www.uk-cpi.com