## SRH remaining P1s
2019 - 2020 Proposed remedial actions for SRH P1s.
Drawing Reference | Building | Level | Room | Hole size (mm) | Remedial Actions | Specific details | Photo Ref. | Photo no. | Priority
HS7-1 | Hospital Street 7 | 1st floor |  | 200 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1923.JPG | 43 | P1
HS7-2 | Hospital Street 7 | 1st floor |  | 1000 x 100 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1924.JPG | 44 | P1
HS7-3 | Hospital Street 7 | 1st floor |  | 250 x 200 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1926.JPG | 45 | P1
HS7-4 | Hospital Street 7 | 1st floor |  | 50 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. |  |  | P1
HS7-5 | Hospital Street 7 | 1st floor |  | 1000 x 420 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the cable tray using an intumescent batt and intumescent mastic. | IMG_1929.JPG | 48 | P1
HS7-6 | Hospital Street 7 | 1st floor |  | 200 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the cable tray using an intumescent batt and intumescent mastic. | IMG_1930.JPG | 49 | P1
HS7-7 | Hospital Street 7 | 1st floor |  | 200 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Suitably back-coat the cables with intumescent mastic. | IMG_1931.JPG | 50 | P1
HS7-8 | Hospital Street 7 | 1st floor |  | 450 x 150 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1932.JPG | 51 | P1
HS7-9 | Hospital Street 7 | 1st floor |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Suitably back-coat the cables with intumescent mastic. (2 no) | IMG_1934.JPG | 52 | P1
HS7-10 | Hospital Street 7 | 1st floor |  | 50 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_1935.JPG | 53 | P1
HS7-11 | Hospital Street 7 | 1st floor |  | 100 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_1936.JPG | 54 | P1
HS7-12 | Hospital Street 7 | 1st floor |  | 300 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_1937.JPG | 55 | P1
HS7-13 | Hospital Street 7 | 1st floor |  | 100 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_1938.JPG | 56 | P1
20-2-25 | West Block | Second Floor | 20-02-01-52 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0043 (Small).JPG | 43 | P1
CW-N-5 | Crawlways |  |  |  | Fire door is wedged open. Ensure that the door is not hindered by objects so that it can close fully into the frame to maintain 30 minute resisting construction. |  | IMG_0087.JPG | 87 | P1
01-02-1 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. Infill inside conduit with intumescent mastic. | IMG_0126 (Small).JPG | 1 | P1
01-02-2 | Main Hospital | Roof |  | 100 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove insulation and infill the opening using an intumescent batt and intumescent mastic. | IMG_0127 (Small).JPG | 2 | P1
01-02-3 | Main Hospital | Roof |  | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0128 (Small).JPG | 3 | P1
01-02-4 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. (2no) | IMG_0129 (Small).JPG | 4 | P1
01-02-5 | Main Hospital | Roof |  | 1500 x 10,000 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend the across the entire floor. Install 60 min FR fireboard structurally secured to existing construction elements. ( Problem was identified on most roof floors adjacent to wall edges) | IMG_0130 (Small).JPG | 5 | P1
01-02-6 | Main Hospital | Roof |  | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent batt and intumescent mastic. | IMG_0136 (Small).JPG | 11 | P1
01-02-7 | Main Hospital | Roof |  | 100 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic | IMG_0139 (Small).JPG | 14 | P1
01-02-8 | Main Hospital | Roof |  |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0148 (Small).JPG | 23 | P1
01-02-9 | Main Hospital | Roof |  |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend across the entire floor. Install 60 min FR fireboard structurally secured to existing construction elements. | IMG_0150 (Small).JPG | 25 | P1
01-02-10 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | IMG_0151 (Small).JPG | 26 | P1
01-02-11 | Main Hospital | Roof |  | 50 dia | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. | IMG_0152 (Small).JPG | 27 | P1
01-02-12 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. Add a supplementary layer of cavity barrier to cover around pipe. | IMG_0153 (Small).JPG | 28 | P1
01-02-13 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | IMG_0154 (Small).JPG | 29 | P1
01-02-14 | Main Hospital | Roof |  | 100 x 3000 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the across the entire floor. Install 60 min FR fireboard structurally secured to existing construction elements. | IMG_0155 (Small).JPG | 30 | P1
01-02-15 | Main Hospital | Roof |  | 50 x 70 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Add a supplementary layer of cavity barrier to cover around ductwork. | IMG_0156 (Small).JPG | 31 | P1
01-02-16 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. (2no) | IMG_0157 (Small).JPG | 32 | P1
01-02-17 | Main Hospital | Roof |  | 30 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill openings with intumescent mastic. (7no) | IMG_0158 (Small).JPG | 33 | P1
01-02-18 | Main Hospital | Roof |  | 100 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Add a supplementary layer of cavity barrier to cover around ductwork. | IMG_0159 (Small).JPG | 34 | P1
01-02-19 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. Add a supplementary layer of cavity barrier to cover around ductworks. (2no) | IMG_0160 (Small).JPG | 35 | P1
01-02-20 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with an intumescent batt and intumescent mastic | IMG_0161 (Small).JPG | 36 | P1
01-02-21 | Main Hospital | Roof |  | 100 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Add a supplementary layer of cavity barrier to cover around beam. | IMG_0162 (Small).JPG | 37 | P1
01-02-22 | Main Hospital | Roof |  | 10 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening with intumescent mastic | IMG_0163 (Small).JPG | 38 | P1
01-02-23 | Main Hospital | Roof |  | 100 x 350 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with an intumescent batt and intumescent mastic | IMG_0164 (Small).JPG | 39 | P1
01-02-24 | Main Hospital | Roof |  | 100 x 15,000 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the across the entire floor. Install 60 min FR fireboard structurally secured to existing construction elements. | IMG_0165 (Small).JPG | 40 | P1
01-02-25 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | IMG_0166 (Small).JPG | 41 | P1
01-02-26 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. Infill around pipes using an intumescent mastic. (2no) | IMG_0167 (Small).JPG | 42 | P1
01-02-27 | Main Hospital | Roof |  | 60 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (2no) | IMG_0168 (Small).JPG | 43 | P1
01-02-28 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. Add supplementary layers of cavity barrier to cover around pipes. (2no) | IMG_0170 (Small).JPG | 45 | P1
01-02-29 | Main Hospital | Roof |  |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. | Repair damaged door frame. | IMG_0171 (Small).JPG | 46 | P1
01-02-30 | Main Hospital | Roof |  | 10 x 600 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Insert intumescent pillows into the gap to allow access to fire damper. | IMG_0172 (Small).JPG | 47 | P1
01-02-31 | Main Hospital | Roof |  | 20 x 70 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Add a supplementary layer of cavity barrier to the opening. | IMG_0173 (Small).JPG | 48 | P1
01-02-32 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. Infill around pipes using an intumescent batt and intumescent mastic. (2no) | IMG_0175 (Small).JPG | 50 | P1
01-02-33 | Main Hospital | Roof |  |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Fire rating of roof could'nt be determined. Install 60 min FR roof structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0176 (Small).JPG | 51 | P1
01-02-34 | Main Hospital | Roof |  | 50 dia | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0177 (Small).JPG | 52 | P1
01-02-35 | Main Hospital | Roof |  | 50 dia | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (4no) | IMG_0178 (Small).JPG | 53 | P1
01-02-36 | Main Hospital | Roof |  |  | The indicated fire door does not fully self close into the frame. Tighten and adjust door hinges to ensure the door fully closes into frame. |  | IMG_0179 (Small).JPG | 54 | P1
01-02-37 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with intumescent mastic | IMG_0180 (Small).JPG | 55 | P1
01-02-38 | Main Hospital | Roof |  | 100 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Add a supplementary layer of cavity barrier to cover around opening. | IMG_0181 (Small).JPG | 56 | P1
01-02-39 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. (2no) | IMG_0182 (Small).JPG | 57 | P1
01-02-40 | Main Hospital | Roof |  |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars. (2no) | IMG_0183 (Small).JPG | 58 | P1
01-02-41 | Main Hospital | Roof |  |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. |  | IMG_0184 (Small).JPG | 59 | P1
01-02-42 | Main Hospital | Roof |  | 20 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill openings with intumescent mastic. (3no) | IMG_0185 (Small).JPG | 60 | P1
01-02-43 | Main Hospital | Roof |  | 100 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with an intumescent batt and intumescent mastic (2no) | IMG_0186 (Small).JPG | 61 | P1
01-02-44 | Main Hospital | Roof |  | 100 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0187 (Small).JPG | 62 | P1
01-02-45 | Main Hospital | Roof |  | 50 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill between floor and wall using intumescent mastic. | IMG_0188 (Small).JPG | 63 | P1
01-02-46 | Main Hospital | Roof |  |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Insert cavity barriers under the roof, between the timber beams. | IMG_0189 (Small).JPG | 64 | P1
01-02-47 | Main Hospital | Roof |  |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0190 (Small).JPG | 65 | P1
01-02-48 | Main Hospital | Roof |  |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the across the entire floor. Install 60 min FR fireboard structurally secured to existing construction elements. | IMG_0191 (Small).JPG | 66 | P1
01-02-49 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with an intumescent batt and intumescent mastic. (2no) | IMG_0192 (Small).JPG | 67 | P1
01-02-50 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with intumescent mastic | IMG_0193 (Small).JPG | 68 | P1
01-02-51 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe with an intumescent batt and intumescent mastic | IMG_0194 (Small).JPG | 69 | P1
01-02-52 | Main Hospital | Roof |  |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. |  | IMG_0195 (Small).JPG | 70 | P1
01-02-53 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0196 (Small).JPG | 71 | P1
01-02-54 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0197 (Small).JPG | 72 | P1
01-02-55 | Main Hospital | Roof |  | 20 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0198 (Small).JPG | 73 | P1
01-02-56 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0199 (Small).JPG | 74 | P1
01-02-57 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (2No) | IMG_0200 (Small).JPG | 75 | P1
01-02-58 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (2No) | IMG_0201 (Small).JPG | 76 | P1
01-02-59 | Main Hospital | Roof |  | 100 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. | IMG_0202 (Small).JPG | 77 | P1
01-02-60 | Main Hospital | Roof |  | 70 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. | IMG_0203 (Small).JPG | 78 | P1
01-02-61 | Main Hospital | Roof |  | 10 x 10 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. (3no) | IMG_0204 (Small).JPG | 79 | P1
01-02-62 | Main Hospital | Roof |  | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0205 (Small).JPG | 80 | P1
01-02-63 | Main Hospital | Roof |  | 100 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable tray using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). | IMG_0206 (Small).JPG | 81 | P1
01-02-64 | Main Hospital | Roof |  | 100 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Provide uPVC pipes with pipe collars. Infill around pipes using an intumescent mastic. (2no) | IMG_0207 (Small).JPG | 82 | P1
01-02-65 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (7no) |  |  | P1
01-02-66 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (10no) |  |  | P1
01-02-67 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (11no) |  |  | P1
01-02-68 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (14no) |  |  | P1
01-02-69 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (1no) |  |  | P1
01-02-70 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (17no) |  |  | P1
01-02-71 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (12no) |  |  | P1
01-02-72 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (13no) |  |  | P1
01-02-73 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (10no) |  |  | P1
01-02-74 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (16no) |  |  | P1
01-02-75 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (18no) |  |  | P1
01-02-76 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (14no) |  |  | P1
01-02-77 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (12no) |  |  | P1
01-02-78 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (10no) |  |  | P1
01-02-79 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (11no) |  |  | P1
01-02-80 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (14no) |  |  | P1
01-02-81 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (9no) |  |  | P1
01-02-82 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (6no) |  |  | P1
01-02-83 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (8no) |  |  | P1
01-02-84 | Main Hospital | Roof |  | Various | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around duct with an intumescent batt and intumescent mastic (10no) |  |  | P1
01-01-05-1 | Main Hospital | First Floor | 01-01-05-29 | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. (3no) | IMG_0250 (Small).JPG | 1 | P1
01-01-05-2 | Main Hospital | First Floor | 01-01-05-23 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0251 (Small).JPG | 2 | P1
01-01-05-3 | Main Hospital | First Floor | 01-01-05-12 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0252 (Small).JPG | 3 | P1
01-01-05-4 | Main Hospital | First Floor | 01-01-05-12 | 300 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0253 (Small).JPG | 4 | P1
01-01-05-5 | Main Hospital | First Floor | 01-01-05-12 | 150 x 150 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0254 (Small).JPG | 5 | P1
01-01-05-6 | Main Hospital | First Floor | 01-01-05-12 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0255 (Small).JPG | 6 | P1
01-01-05-7 | Main Hospital | First Floor | 01-01-05-12 | 40 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0256 (Small).JPG | 7 | P1
01-01-05-8 | Main Hospital | First Floor | 01-01-05-12 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0257 (Small).JPG | 8 | P1
01-01-05-9 | Main Hospital | First Floor | 01-01-05-12 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0258 (Small).JPG | 9 | P1
01-01-05-10 | Main Hospital | First Floor | 01-01-05-12 | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0259 (Small).JPG | 10 | P1
01-01-05-11 | Main Hospital | First Floor | 01-01-05-12 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0260 (Small).JPG | 11 | P1
01-01-05-12 | Main Hospital | First Floor | 01-01-05-10 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0261 (Small).JPG | 12 | P1
01-01-05-13 | Main Hospital | First Floor | 01-01-05-10 | 60 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0262 (Small).JPG | 13 | P1
01-01-05-14 | Main Hospital | First Floor | 01-01-05-10 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0263 (Small).JPG | 14 | P1
01-01-05-15 | Main Hospital | First Floor | 01-01-05-10 | 40 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0264 (Small).JPG | 15 | P1
01-01-05-16 | Main Hospital | First Floor | 01-01-05-10 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | IMG_0265 (Small).JPG | 16 | P1
01-01-05-17 | Main Hospital | First Floor | 01-01-05-10 | 10 dia. 60 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. Infill around cable tray using an intumescent batt and intumescent mastic. | IMG_0266 (Small).JPG | 17 | P1
01-01-05-18 | Main Hospital | First Floor | 01-01-05-10 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduits using an intumescent mastic. (2no) | IMG_0267 (Small).JPG | 18 | P1
01-01-05-19 | Main Hospital | First Floor | 01-01-05-01 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. | The indicated fire door is not provided with intumescent backed cold smoke seals along the top egde. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. | IMG_0268 (Small).JPG | 19 | P1
01-01-05-20 | Main Hospital | First Floor | 01-01-05-01 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0269 (Small).JPG | 20 | P1
01-01-05-21 | Main Hospital | First Floor | 01-01-05-01 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0270 (Small).JPG | 21 | P1
01-01-05-22 | Main Hospital | First Floor | 01-01-05-01 | 40 x 100 (2No) 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0271 (Small).JPG | 22 | P1
01-01-05-23 | Main Hospital | First Floor | 01-01-05-02 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0272 (Small).JPG | 23 | P1
01-01-05-24 | Main Hospital | First Floor | 01-01-05-02 |  | Pipe was observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | IMG_0273 (Small).JPG | 24 | P1
01-01-05-25 | Main Hospital | First Floor | 01-01-05-02 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. (2no) | IMG_0274 (Small).JPG | 25 | P1
01-01-05-26 | Main Hospital | First Floor | 01-01-05-03 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. | IMG_0275 (Small).JPG | 26 | P1
01-01-05-27 | Main Hospital | First Floor | 01-01-05-03 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0276 (Small).JPG | 27 | P1
01-01-05-28 | Main Hospital | First Floor | 01-01-05-50 | 5 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill above cable tray using an intumescent mastic. | IMG_0277 (Small).JPG | 28 | P1
01-01-05-29 | Main Hospital | First Floor | 01-01-05-38 | 10 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill above cable tray with intumescent mastic. | IMG_0278 (Small).JPG | 29 | P1
01-01-05-30 | Main Hospital | First Floor | 01-01-05-38 | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the openings using an intumescent mastic. (2no) | IMG_0279 (Small).JPG | 30 | P1
01-01-05-31 | Main Hospital | First Floor | 01-01-05-38 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0280 (Small).JPG | 31 | P1
01-01-05-32 | Main Hospital | First Floor | 01-01-05-38 | 10 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill above cable tray with intumescent mastic. | IMG_0281 (Small).JPG | 32 | P1
01-01-05-33 | Main Hospital | First Floor | 01-01-05-38 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. |  | IMG_0282 (Small).JPG | 33 | P1

## Worthing P1s
Worthing Hospital remedial actions fire stopping P1s
Drawing Reference | Building | Level | Room | Hole size (mm) | Remedial Actions | Specific details | Priority
02-02-01-1 | Critical Care Unit (ITU) | Second Floor | 2.43 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-2 | Critical Care Unit (ITU) | Second Floor | 2.43 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-01-3 | Critical Care Unit (ITU) | Second Floor | 2.43 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent batt and intumescent mastic. | P1
02-02-01-4 | Critical Care Unit (ITU) | Second Floor | 2.43 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduits using an intumescent mastic. (2no) | P1
02-02-01-5 | Critical Care Unit (ITU) | Second Floor | 2.102 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P1
02-02-01-6 | Critical Care Unit (ITU) | Second Floor | Duct 2 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-02-01-7 | Critical Care Unit (ITU) | Second Floor | Duct 2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P1
02-02-01-8 | Critical Care Unit (ITU) | Second Floor | 2.45 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-01-9 | Critical Care Unit (ITU) | Second Floor | 2.45 | 5 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-02-01-10 | Critical Care Unit (ITU) | Second Floor | 2.45A |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | infill the small opening using an intumescent sealant. | P1
02-02-01-11 | Critical Care Unit (ITU) | Second Floor | 2.45A | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduits using an intumescent mastic. (2no) | P1
02-02-01-12 | Critical Care Unit (ITU) | Second Floor | 2.45A | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduits using an intumescent mastic. (2no) | P1
02-02-01-13 | Critical Care Unit (ITU) | Second Floor | 2.45A | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduits using an intumescent mastic. (2no) | P1
02-02-01-14 | Critical Care Unit (ITU) | Second Floor | 2.45A | 100 x 250 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-02-01-15 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent mastic. (2no) | P1
02-02-01-16 | Critical Care Unit (ITU) | Second Floor | 2.46 | 30 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around cables using an intumescent batt and intumescent mastic. | P1
02-02-01-17 | Critical Care Unit (ITU) | Second Floor | 2.46 | 20 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-01-18 | Critical Care Unit (ITU) | Second Floor | 2.46 | 30 x 60 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-01-19 | Critical Care Unit (ITU) | Second Floor | 2.46 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-20 | Critical Care Unit (ITU) | Second Floor | 2.46 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (3no) | P1
02-02-01-21 | Critical Care Unit (ITU) | Second Floor | 2.47 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-02-01-22 | Critical Care Unit (ITU) | Second Floor | 2.47 | 40 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around cables using an intumescent mastic. | P1
02-02-01-23 | Critical Care Unit (ITU) | Second Floor | 2.47 | 20 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-01-24 | Critical Care Unit (ITU) | Second Floor | 2.47 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-25 | Critical Care Unit (ITU) | Second Floor | 2.34 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P1
02-02-01-26 | Critical Care Unit (ITU) | Second Floor | 2.34 | 100 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the pipes using an intumescent batt and intumescent mastic. | P1
02-02-01-27 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 40 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray and cables using an intumescent mastic. | P1
02-02-01-28 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent mastic. (3no) | P1
02-02-01-29 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P1
02-02-01-30 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent mastic. (3no) | P1
02-02-01-31 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 20 D, 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cable and cable tray using an intumescent mastic. (2no) | P1
02-02-01-32 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 100 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening above ductwork using an intumescent batt and intumescent mastic. | P1
02-02-01-33 | Critical Care Unit (ITU) | Second Floor | 2.C8 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill openings around cables using an intumescent mastic. (2no) | P1
02-02-01-34 | Critical Care Unit (ITU) | Second Floor | 2.49 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-35 | Critical Care Unit (ITU) | Second Floor | 2.49 | 40 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-02-01-36 | Critical Care Unit (ITU) | Second Floor | 2.49 | 40 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around duckwork and cables using an intumescent batt and intumescent mastic. | P1
02-02-01-37 | Critical Care Unit (ITU) | Second Floor | 2.49 | 20 x 1000 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-02-01-38 | Critical Care Unit (ITU) | Second Floor | 2.C9 | 10 D, 20 D, 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduit and cables using an intumescent mastic (3no). | P1
02-02-01-39 | Critical Care Unit (ITU) | Second Floor | 2.C9 |  | The intumescent / intumescent backed cold smoke seals to the indicated fire door are defective. Replace the existing seals with new intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing intumescent smoke seal and dispose. (b) Remove existing fire door from its frame. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-02-01-40 | Critical Care Unit (ITU) | Second Floor | 2.56 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-02-01-41 | Critical Care Unit (ITU) | Second Floor | 2.51 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
02-02-01-42 | Critical Care Unit (ITU) | Second Floor | 2.51 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-43 | Critical Care Unit (ITU) | Second Floor | 2.51 | 20 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove insulation and infill the opening around the cable tray using an intumescent batt and intumescent mastic. | P1
02-02-01-44 | Critical Care Unit (ITU) | Second Floor | 2.51 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-45 | Critical Care Unit (ITU) | Second Floor | 2.51 | 50 x 70 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-01-46 | Critical Care Unit (ITU) | Second Floor | 2.51 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit and cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-02-01-47 | Critical Care Unit (ITU) | Second Floor | 2.51 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-01-48 | Critical Care Unit (ITU) | Second Floor | 2.50 | 100 x 500 | The construction at high level was not present. Install a new batt or fire board sutiable support for the batt or fire board along the opening. Where cables or pipes pass through the new batt, ensure the openings are infilled using a suitable intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt or fire board in the opening, structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | P1
02-02-04-1 | Courtlands | Second Floor | 2.70 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-04-2 | Courtlands | Second Floor | 2.70 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-04-3 | Courtlands | Second Floor | Duct 3 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-04-4 | Courtlands | Second Floor | Duct 3 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-04-5 | Courtlands | Second Floor | Duct 3 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-02-04-6 | Courtlands | Second Floor | 2.74a | 300 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated foam and infill opening around ductwork using an intumescent batt and intumescent mastic. | P1
02-02-04-7 | Courtlands | Second Floor | 2.C7 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables and pipe using an intumescent mastic (4no). Infill the opening using an intumescent mastic (2no). | P1
02-02-04-8 | Courtlands | Second Floor | 2.C7 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam and infill openings around pipe using an intumescent mastic. | P1
02-02-04-9 | Courtlands | Second Floor | 2.C7 | 60 x 60 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent batt and intumescent mastic. | P1
02-02-04-10 | Courtlands | Second Floor | 2.C7 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing self closing device and ensure positive self closure into the frame. |  | P1
02-02-04-11 | Courtlands | Second Floor | 2.C7 | 500 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove insulation and infill the opening using an intumescent batt and intumescent mastic. | P1
02-02-04-12 | Courtlands | Second Floor | 2.C7 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic (2no). | P1
02-02-04-13 | Courtlands | Second Floor | 2.C7 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-02-04-14 | Courtlands | Second Floor | 2.89 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated insulation and infill opening around cable tray using an intumescent batt intumescent mastic. | P1
02-02-04-15 | Courtlands | Second Floor | 2.89 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-04-16 | Courtlands | Second Floor | 2.89 | 50 x 70 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around coduit and cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-02-04-17 | Courtlands | Second Floor | 2.71 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduits using an intumescent mastic. (3no) | P1
02-02-04-18 | Courtlands | Second Floor | 2.71 | 5 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-04-19 | Courtlands | Second Floor | 2.90 | 150 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening in soffit using an intumescent batt and intumescent mastic. | P1
02-02-04-20 | Courtlands | Second Floor | 2.90 | 150 D | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P1
02-02-04-21 | Courtlands | Second Floor | 2.90 | 20 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. | P1
02-02-04-22 | Courtlands | Second Floor | 2.90 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-02-04-23 | Courtlands | Second Floor | 2.90 | 20 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. | P1
02-03-02-1 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-2 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-3 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-02-4 | West Wing Lift Lobby | Third Floor | 3.C6 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-5 | West Wing Lift Lobby | Third Floor | 3.96 | 5 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-02-6 | West Wing Lift Lobby | Third Floor | 3.97 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-7 | West Wing Lift Lobby | Third Floor | 3.97 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-8 | West Wing Lift Lobby | Third Floor | 3.97 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-03-02-9 | West Wing Lift Lobby | Third Floor | 3.97 | 200 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-03-02-10 | West Wing Lift Lobby | Third Floor | 3.97 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. | P1
02-03-02-11 | West Wing Lift Lobby | Third Floor | 3.97 | 20 D 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated insulation and infill openings around cables using an intumescent batt and intumescent mastic. (2no) | P1
02-03-02-12 | West Wing Lift Lobby | Third Floor | 3.97 | 10 D, 30 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure the cables are suitably back coated with instumescent mastic (3no) | P1
02-03-02-13 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-03-02-14 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-15 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-16 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-17 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-18 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-19 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-20 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-21 | West Wing Lift Lobby | Third Floor | 3.C6 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-03-02-22 | West Wing Lift Lobby | Third Floor | 3.C6 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-03-02-23 | West Wing Lift Lobby | Third Floor | 3.C6 | 40 x 40 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill openings around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-03-02-24 | West Wing Lift Lobby | Third Floor | 3.C6 | 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated insulation and infill around cable tray using an intumescent mastic. | P1
02-03-02-25 | West Wing Lift Lobby | Third Floor | 3.C6 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-26 | West Wing Lift Lobby | Third Floor | 3.C6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-27 | West Wing Lift Lobby | Third Floor | 3.C6 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing self closing device and ensure positive self closure into the frame. |  | P1
02-03-02-28 | West Wing Lift Lobby | Third Floor | 3.C6 |  | The existing self closing device has been disconnected from the door. Repair and reconnect the existing self closing device to the door and ensure that the door has positive self closure into the frame. |  | P1
02-03-01-1 | Downlands Suite & Dixon | Third Floor | Duct 2 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-03-01-2 | Downlands Suite & Dixon | Third Floor | Duct 2 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent batt and intumescent mastic. | P1
02-03-01-3 | Downlands Suite & Dixon | Third Floor | Duct 2 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-03-01-4 | Downlands Suite & Dixon | Third Floor | Duct 2 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-5 | Downlands Suite & Dixon | Third Floor | Duct 2 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening in soffit using an intumescent batt and intumescent mastic. | P1
02-03-01-6 | Downlands Suite & Dixon | Third Floor | Duct 2 |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill around cable using an intumescent mastic. | P1
02-03-01-7 | Downlands Suite & Dixon | Third Floor | Duct 2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-8 | Downlands Suite & Dixon | Third Floor | 3.45B | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-9 | Downlands Suite & Dixon | Third Floor | 3.45B | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-10 | Downlands Suite & Dixon | Third Floor | 3.45 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-11 | Downlands Suite & Dixon | Third Floor | 3.45 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-12 | Downlands Suite & Dixon | Third Floor | 3.45 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduits using an intumescent mastic. (2no) | P1
02-03-01-13 | Downlands Suite & Dixon | Third Floor | 3.46 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-14 | Downlands Suite & Dixon | Third Floor | 3.46 | 10 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-03-01-15 | Downlands Suite & Dixon | Third Floor | 3.46 | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove the piece of parper and non- fire rated foam. Infill opening around cable using an intumescent batt and intumescent mastic. | P1
02-03-01-16 | Downlands Suite & Dixon | Third Floor | 3.46 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-17 | Downlands Suite & Dixon | Third Floor | 3.46 | 60 D | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cable using an intumescent and intumescent mastic. | P1
02-03-01-18 | Downlands Suite & Dixon | Third Floor | 3.46 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
02-03-01-19 | Downlands Suite & Dixon | Third Floor | 3.47 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-20 | Downlands Suite & Dixon | Third Floor | 3.47 | 100 D | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill around cable using an intumescent mastic. | P1
02-03-01-21 | Downlands Suite & Dixon | Third Floor | 3.47 | 100 D | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill around cable using an intumescent mastic. | P1
02-03-01-22 | Downlands Suite & Dixon | Third Floor | 3.C8 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | P1
02-03-01-23 | Downlands Suite & Dixon | Third Floor | 3.C8 | 1000 x 2000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent batt and intumescent mastic. | P1
02-03-01-24 | Downlands Suite & Dixon | Third Floor | 3.C8 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-25 | Downlands Suite & Dixon | Third Floor | 3.56 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-26 | Downlands Suite & Dixon | Third Floor | 3.48 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-27 | Downlands Suite & Dixon | Third Floor | 3.48 | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. | P1
02-03-01-28 | Downlands Suite & Dixon | Third Floor | 3.48 | 50 D | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cables using an intumescent mastic. | P1
02-03-01-29 | Downlands Suite & Dixon | Third Floor | 3.49C |  | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt or fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | P1
02-03-01-30 | Downlands Suite & Dixon | Third Floor | 3.49B |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P1
02-03-01-31 | Downlands Suite & Dixon | Third Floor | 3.49B | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-32 | Downlands Suite & Dixon | Third Floor | 3.49B | 10 D, 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam and infill around cables using an intumescent mastic. (2no) | P1
02-03-01-33 | Downlands Suite & Dixon | Third Floor | 3.49B | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. (2no) | P1
02-03-01-34 | Downlands Suite & Dixon | Third Floor | 3.50 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-03-01-35 | Downlands Suite & Dixon | Third Floor | 3.50 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-36 | Downlands Suite & Dixon | Third Floor | 3.50 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P1
02-03-01-37 | Downlands Suite & Dixon | Third Floor | 3.50 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cables using an intumescent mastic. (2no) | P1
02-03-01-38 | Downlands Suite & Dixon | Third Floor | 3.50 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cables using an intumescent mastic. (2no) | P1
02-03-01-39 | Downlands Suite & Dixon | Third Floor | 3.50 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-03-01-40 | Downlands Suite & Dixon | Third Floor | 3.51 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. (2no) | P1
02-03-01-41 | Downlands Suite & Dixon | Third Floor | 3.51 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-42 | Downlands Suite & Dixon | Third Floor | 3.51 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening in soffit using an intumescent batt and intumescent mastic. | P1
02-03-01-43 | Downlands Suite & Dixon | Third Floor | 3.C9 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-01-44 | Downlands Suite & Dixon | Third Floor | 3.C9 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around cables using an intumescent mastic. (2no) | P1
02-03-01-45 | Downlands Suite & Dixon | Third Floor | 3.C9 | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-03-01-46 | Downlands Suite & Dixon | Third Floor | 3.C9 | 20 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. | P1
02-03-01-47 | Downlands Suite & Dixon | Third Floor | 3.C9 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
02-03-01-48 | Downlands Suite & Dixon | Third Floor | 3.C9 | 20 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-03-04-1 | Ditchling | Third Floor | 3.69 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the lock and existing self closing device and ensure positive self closure into the frame. |  | P1
02-03-04-2 | Ditchling | Third Floor | 3.69 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable and pipes using an intumescent mastic. (3no) | P1
02-03-04-3 | Ditchling | Third Floor | 3.69 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P1
02-03-04-4 | Ditchling | Third Floor | 3.69 | 600 x 1000 | The construction at high level was not present.Install a new intumescent batt or fire rated board and suitable support for the batt or fire rated board along the opening. Where cables or conduits pass through the new batt or fire rated board, ensure they are suitable back coated with intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | P1
02-03-04-5 | Ditchling | Third Floor | 3.69 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-04-6 | Ditchling | Third Floor | 3.69 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-04-7 | Ditchling | Third Floor | 3.69 |  | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt or fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | P1
02-03-04-8 | Ditchling | Third Floor | 3.69 |  | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt or fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | P1
02-03-04-9 | Ditchling | Third Floor | 3.69D | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using anintumescent batt and intumescent mastic. (3no) | P1
02-03-04-10 | Ditchling | Third Floor | 3.69D | 40 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around pipe using an intumescent mastic. | P1
02-03-04-11 | Ditchling | Third Floor | 3.69D | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P1
02-03-04-12 | Ditchling | Third Floor | 3.69D |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-03-04-13 | Ditchling | Third Floor | 3.69D |  | The indicated door was found to have an opening where an old lock had been removed. Carry out repair to door to restore the fire integrity of door. Splice in new section of timber, glued and screwed to the door. |  | P1
02-03-04-14 | Ditchling | Third Floor | 3.69D |  | The intumescent / intumescent backed cold smoke seals to the indicated double fire doors are defective. Replace the existing seals with new intumescent backed cold smoke seals to head and edges of both doors. To the existing fire doors undertake the appropriate preparatory works. (a) Remove existing intumescent smoke seals and dispose. (b) Remove existing fire doors from their frame. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the doors). Re-hang existing fire doors ensuring that they fully self close into the frame. |  | P1
02-03-04-15 | Ditchling | Third Floor | 3.69C |  | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Install intumescent batt or fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | P1
02-03-04-16 | Ditchling | Third Floor | 3.69A | 100 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-03-04-17 | Ditchling | Third Floor | 3.69A |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-03-04-18 | Ditchling | Third Floor | 3.70B | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. | P1
02-03-04-19 | Ditchling | Third Floor | 3.70B | 70 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around pipe using an intumescent batt and intumescent mastic. | P1
02-03-04-20 | Ditchling | Third Floor | 3.70B | 100 x 3000 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic, structurally secured to existing construction elements. | P1
02-03-04-21 | Ditchling | Third Floor | 3.70B | 1500 x 1500 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening between the two adjacent walls using an intumescent batt and intumescent mastic. | P1
02-03-04-22 | Ditchling | Third Floor | 3.70B | 1000 x 1000 | The construction at high level was not present. Install a new intumescent batt or fire rated board and suitable support for the batt and fire rated along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic or fireboard, structurally secured to existing construction elements. | P1
02-03-04-23 | Ditchling | Third Floor | 3.70B | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. (2no) | P1
02-03-03-1 | Durrington | Third Floor | 3.89 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated insulation and infill the opening in floor using an intumescent batt and intumescent mastic. | P1
02-03-03-2 | Durrington | Third Floor | 3.89 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-03-3 | Durrington | Third Floor | 3.74C |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | P1
02-03-03-4 | Durrington | Third Floor | 3.74C | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-03-5 | Durrington | Third Floor | 3.74C |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P1
02-03-03-6 | Durrington | Third Floor | 3.74C | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-03-7 | Durrington | Third Floor | 3.73 | 10 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
02-03-03-8 | Durrington | Third Floor | 3.73 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-03-03-9 | Durrington | Third Floor | 3.72 | 150 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening in soffit using an intumescent batt and intumescent mastic. | P1
02-03-03-10 | Durrington | Third Floor | 3.72 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent batt and intumescent mastic. | P1
02-03-03-11 | Durrington | Third Floor | 3.72 | 50 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around ductwork using an intumescent batt and intumescent mastic. | P1
02-03-03-12 | Durrington | Third Floor | 3.71A | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
02-03-03-13 | Durrington | Third Floor | 3.76 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-03-03-14 | Durrington | Third Floor | 3.76 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-03-15 | Durrington | Third Floor | 3.76 | 100 x 1000 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an new intumescent batt and intumescent mastic. | P1
02-03-03-16 | Durrington | Third Floor | 3.92 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-03-03-17 | Durrington | Third Floor | 3.C7 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing self closing device and ensure positive self closure into the frame. |  | P1
02-03-02-29 | West Wing Lift Lobby | Third Floor | Duct 1 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
02-03-02-30 | West Wing Lift Lobby | Third Floor | Duct 1 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
06-02-08-1 | Coombes/Castle Wards | Second Floor | 2/F/57 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-2 | Coombes/Castle Wards | Second Floor | 2/F/05 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-3 | Coombes/Castle Wards | Second Floor | 2/F/05 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
06-02-08-4 | Coombes/Castle Wards | Second Floor | 2/F/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-5 | Coombes/Castle Wards | Second Floor | 2/F/50 |  | The door is kept open. If it is desired to keep the door open to allow easier movement of beds, then consider installing a magnetic hold on the door linked to the local fire alarm. |  | P1
06-02-08-6 | Coombes/Castle Wards | Second Floor | 2/F/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-7 | Coombes/Castle Wards | Second Floor | 2/F/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-8 | Coombes/Castle Wards | Second Floor | 2/F/07 |  | The door is kept open. If it is desired to keep the door open to allow easier movement of beds, then consider installing a magnetic hold on the door linked to the local fire alarm. |  | P1
06-02-08-9 | Coombes/Castle Wards | Second Floor | 2/F/15 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-10 | Coombes/Castle Wards | Second Floor | 2/F/22 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-11 | Coombes/Castle Wards | Second Floor | 2/F/22 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-12 | Coombes/Castle Wards | Second Floor | 2/F/07 |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cables using an intumescent mastic. | P1
06-02-08-13 | Coombes/Castle Wards | Second Floor | 2/F/07 |  | The door is kept open. If it is desired to keep the door open to allow easier movement of beds, then consider installing a magnetic hold on the door linked to the local fire alarm. |  | P1
06-02-08-14 | Coombes/Castle Wards | Second Floor | 2/F/07 | 40 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic. | P1
06-02-08-15 | Coombes/Castle Wards | Second Floor | 2/F/28 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-16 | Coombes/Castle Wards | Second Floor | 2/F/44 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-17 | Coombes/Castle Wards | Second Floor | 2/F/44 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cable using an intumescent mastic. | P1
06-02-08-18 | Coombes/Castle Wards | Second Floor | 2/F/42 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-19 | Coombes/Castle Wards | Second Floor | 2/F/37 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-20 | Coombes/Castle Wards | Second Floor | 2/F/36 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-21 | Coombes/Castle Wards | Second Floor | 2/F/36 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-08-22 | Coombes/Castle Wards | Second Floor | 2/F/36 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-08-23 | Coombes/Castle Wards | Second Floor | 2/F/36 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. (4no) | P1
06-02-08-24 | Coombes/Castle Wards | Second Floor | 2/F/36 | 10 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
06-02-08-25 | Coombes/Castle Wards | Second Floor | 2/F/31 |  | The door is kept open. If it is desired to keep the door open to allow easier movement of beds, then consider installing a magnetic hold on the door linked to the local fire alarm. |  | P1
06-02-08-26 | Coombes/Castle Wards | Second Floor | 2/F/04 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-02-1 | Theatres | Second Floor | 2-B-54 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P1
06-02-02-2 | Theatres | Second Floor | 2-B-42 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-02-3 | Theatres | Second Floor | 2-B-28 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-02-4 | Theatres | Second Floor | 2-B-56 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-02-5 | Theatres | Second Floor | 2-B-55 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-02-6 | Theatres | Second Floor | 2-B-04 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-02-7 | Theatres | Second Floor | 2-B-59 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-02-8 | Theatres | Second Floor | 2-B-04 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-1 | Clapham / Chiltington | Second Floor | 2-E-02 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-2 | Clapham / Chiltington | Second Floor | 2-E-59 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-3 | Clapham / Chiltington | Second Floor | 2-E-09 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside conduit using an intumescent mastic. | P1
06-02-07-4 | Clapham / Chiltington | Second Floor | 2-E-15 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-07-5 | Clapham / Chiltington | Second Floor | 2-E-15 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-6 | Clapham / Chiltington | Second Floor | 2-E-22 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-7 | Clapham / Chiltington | Second Floor | 2-E-23 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-8 | Clapham / Chiltington | Second Floor | 2-E-23 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-07-9 | Clapham / Chiltington | Second Floor | 2-E-23 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
06-02-07-10 | Clapham / Chiltington | Second Floor | 2-E-30 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-11 | Clapham / Chiltington | Second Floor | 2-E-01 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-12 | Clapham / Chiltington | Second Floor | 2-E-01 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
06-02-07-13 | Clapham / Chiltington | Second Floor | 2-E-01 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-14 | Clapham / Chiltington | Second Floor | 2-E-46 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-15 | Clapham / Chiltington | Second Floor | 2-E-46 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-07-16 | Clapham / Chiltington | Second Floor | 2-E-38 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-07-17 | Clapham / Chiltington | Second Floor | 2-E-32a | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P1
06-02-07-18 | Clapham / Chiltington | Second Floor | 2-E-32a |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
06-02-05-1 | Plant Room | Second Floor | 2/D/09 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
46-02-02-1 | Plant Room | Second Floor |  | 50 x 200 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cable tray using an intumescent batt and intumescent mastic. | P1
46-02-02-2 | Plant Room | Second Floor |  | 50 x 200 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cable tray using an intumescent batt and intumescent mastic. | P1
46-02-02-3 | Plant Room | Second Floor |  | 50 x 400 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cable tray using an intumescent batt and intumescent mastic. | P1
46-02-02-4 | Plant Room | Second Floor |  | 70 x 150 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cable tray using an intumescent batt and intumescent mastic. | P1
02-04-02-1 | West Wing Lift Lobby | Fourth Floor | Duct1 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-02-2 | West Wing Lift Lobby | Fourth Floor | Duct1 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-3 | West Wing Lift Lobby | Fourth Floor | 4.C7 | 300 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around pipe using an intumescent batt and intumescent mastic. | P1
02-04-02-4 | West Wing Lift Lobby | Fourth Floor | 4.C7 | 50 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-04-02-5 | West Wing Lift Lobby | Fourth Floor | 4.C7 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-02-6 | West Wing Lift Lobby | Fourth Floor | 4.C7 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-7 | West Wing Lift Lobby | Fourth Floor | 4.87 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-8 | West Wing Lift Lobby | Fourth Floor | 4.87 | 50 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around cables using an intumescent batt and intumescent mastic. | P1
02-04-02-9 | West Wing Lift Lobby | Fourth Floor | 4.87 | 50 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-04-02-10 | West Wing Lift Lobby | Fourth Floor | 4.87 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-11 | West Wing Lift Lobby | Fourth Floor | 4.96 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. | Ensure intumescent cold seals/strips are replaced either on the door or door frame. | P1
02-04-02-12 | West Wing Lift Lobby | Fourth Floor | 4.97 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (2no) | P1
02-04-02-13 | West Wing Lift Lobby | Fourth Floor | 4.97 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (3no) | P1
02-04-02-14 | West Wing Lift Lobby | Fourth Floor | 4.97 | 50 x 50 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-04-02-15 | West Wing Lift Lobby | Fourth Floor | 4.97 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. (2no) | P1
02-04-02-16 | West Wing Lift Lobby | Fourth Floor | 4.97 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-02-17 | West Wing Lift Lobby | Fourth Floor | 4.97 | 50 x 50 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Remove non-fire rated foam and infill opening using and intumescent batt and intumescent mastic. Infill opening around cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-04-02-18 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-02-19 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 40 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P1
02-04-02-20 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-21 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (2no) | P1
02-04-02-22 | West Wing Lift Lobby | Fourth Floor | 4.101 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (2no) | P1
02-04-02-23 | West Wing Lift Lobby | Fourth Floor | 4.100A | 100 x 1500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic, structurally supported to existing construction elements. | P1
02-04-02-24 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-25 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 10 x 30 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-02-26 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-04-02-27 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 50 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P1
02-04-02-28 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 40 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic. | P1
02-04-02-29 | West Wing Lift Lobby | Fourth Floor | 4.C6 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-01-1 | Eastbrook | Fourth Floor | 4.43 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
02-04-01-2 | Eastbrook | Fourth Floor | Duct2 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-01-3 | Eastbrook | Fourth Floor | 4.47 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-01-4 | Eastbrook | Fourth Floor | 4.47 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-01-5 | Eastbrook | Fourth Floor | 4.48 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. | Ensure intumescent cold seals/strips are replaced either on the door or door frame. | P1
02-04-01-6 | Eastbrook | Fourth Floor | 4.48 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-01-7 | Eastbrook | Fourth Floor | 4.58 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-01-8 | Eastbrook | Fourth Floor | 4.59 | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the pipe using an intumescent batt and intumescent mastic. | P1
02-04-01-9 | Eastbrook | Fourth Floor | 4.59 | 30 x 100 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent batt and intumescent mastic. | P1
02-04-01-10 | Eastbrook | Fourth Floor | 4.65 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-01-11 | Eastbrook | Fourth Floor | 4.65 | 50 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the pipe using an intumescent batt and intumescent mastic. | P1
02-04-01-12 | Eastbrook | Fourth Floor | 4.65 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (2no) | P1
02-04-01-13 | Eastbrook | Fourth Floor | 4.65 | 50 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening aropund the pipe and cables using an intumescent batt and intumescent mastic. | P1
02-04-01-14 | Eastbrook | Fourth Floor | 4.C9 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P1
02-04-01-15 | Eastbrook | Fourth Floor | 4.C9 | 50 x 200 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around ductwork using an intumescent batt and intumescent mastic. | P1
02-04-01-16 | Eastbrook | Fourth Floor | 4.62 | 50 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P1
02-04-01-17 | Eastbrook | Fourth Floor | 4.62 | 20 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P1
02-04-04-1 | Eartham | Fourth Floor | 4.C10 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P1
02-04-04-2 | Eartham | Fourth Floor | 4.51 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-04-3 | Eartham | Fourth Floor | 4.51 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-04-4 | Eartham | Fourth Floor | 4.51 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P1
02-04-04-5 | Eartham | Fourth Floor | 4.52 | 40 x 40 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent batt and intumescent mastic. | P1
02-04-04-6 | Eartham | Fourth Floor | 4.52A | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent batt and intumescent mastic. (2no) | P1
02-04-04-7 | Eartham | Fourth Floor | 4.C10 |  | The construction at high level was not present. Install a new fire rated board (30minute FR) suitably fixed to the existing structure. Where cables or conduits pass through the new fire board, ensure that they are suitably infilled using an instumescent mastic. Infill openings using a sutiable instumescent mastic or similar to provide a minimum 30 minutes fire resistance. | Infill opening with a fire rated fire board and intumescent mastic, structurally supported to existing construction elements. | P1
02-04-04-8 | Eartham | Fourth Floor | 4.108 | 500 x 2000 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic, structurally supported to existing construction elements. | P1
02-04-04-9 | Eartham | Fourth Floor | 4.108 | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening around pipes using an intumescent batt and intumescent mastic. | P1
02-04-04-10 | Eartham | Fourth Floor | 4.90 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-04-03-1 | Erringham | Fourth Floor | 4.72 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P1
02-04-03-2 | Erringham | Fourth Floor | 4.72 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P1
02-04-03-3 | Erringham | Fourth Floor | 4.91 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-04-03-4 | Erringham | Fourth Floor | 4.92 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P1
02-04-03-5 | Erringham | Fourth Floor | 4.C7 |  | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Install an intumescent batt structurally secured to existing construction elements. | P1
02-04-03-6 | Erringham | Fourth Floor | 4.80 | 50 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around pipe using an intumescent batt and intumescent mastic. | P1

## Southlands P1s
Drawing Reference | Building | Level | Room | Hole size (mm) | Remedial Actions | Specific details | Priority
08-1-1 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 20 x 1600 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall between laboratory and plant room. Penetration of two ventilation ducts inadequately sealed at the perimeter. Seal using a combination of ablative batt and intumescent mastic. | 1
08-1-2 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 20 x 1100 x 2 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall between laboratory and plant room. Penetration of two smaller ventilation ducts inadequately sealed at the perimeter. Seal using a combination of ablative batt and intumescent mastic. | 1
08-1-3 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 20 x 1200 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Above emergency exit to rear. Penetration of ventilation duct inadequately sealed at the perimeter. Seal using a combination of ablative batt and intumescent mastic. | 1
08-1-4 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 80 x 70 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Above and to the right of inner room door. Open aperture where cables run through wall. Infill using intumescent pillows. | 1
08-1-5 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 150 x 150 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Above and to the left of inner room door. Aperture infilled with non fire rated expanding foam. Remove foam and infill using intumescent pillows. | 1
08-1-6 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 180 x 180 | 3m to the left of inner room door. Disruption to fire rated covering of ductwork. Reinstate fire rated covering. |  | 1
08-1-7 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 900 x 1200 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Inside service hatch 5A/14 Missing compartmentation above penetrating services. Encase area with ablative batt at ceiling level and use elastomeric intumescent cable collar to protect penetrating services. | 1
08-1-8 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | 900 x 1500 | The construction at high level was not present. Install a new plasteboar sheet to provide a minimum 60 minute fire resistance. | Mid way along service corridor 5A/14. Missing plasterboard. Infill area with 12mm plasterboard sheets (2 no) and seal perimeters of plasterboard with intumescent mastic. | 1
08-1-9 | Theatre / Pharmacy / DSU | First floor | Plant room 25 | Not applicable. | The indicated fire door is not fully self closing into the frame. Ease and adjust door to enable door to close in the event of fire. | Door leading into Service Corridor 5A/14 fails to close. Shave door on the leading stile. | 1
08-1-10 | Theatre / Pharmacy / DSU | First floor | Dirty Corridor. | 20 x 20 x 10 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Theatre one lighting cupboard furthest end. Penetration of services into ceiling unprotected. Seal apertures using intumescent mastic. | 1
08-1-11 | Theatre / Pharmacy / DSU | First floor | Dirty Corridor. | 15 x 400 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Theatre one lighting cupboard mid way. Penetration of services into ceiling unprotected. Seal apertures using intumescent mastic. | 1
08-1-12 | Theatre / Pharmacy / DSU | First floor | Dirty Corridor. | 20 x 20 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Theatre 2 lighting cupboard furthest end. Penetration of services into ceiling unprotected.Seal apertures using intumescent mastic. | 1
08-1-13 | Theatre / Pharmacy / DSU | First floor | Dirty Corridor. | 20 x 150 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Theatre two lighting cupboard mid way. Penetration of services into ceiling unprotected. Seal apertures using intumescent mastic. | 1
08-1-14 | Theatre / Pharmacy / DSU | First floor | Dirty Corridor. | 20 x 80 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | DB Cupboard 1/5A/52. Seal apertures using intumescent collar.Seal apertures using rated intumescent foam | 1
08-1-15 | Theatre / Pharmacy / DSU | First floor | Dirty Corridor. | 5 x160 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Storage Cupboard. Multiple Penetration of services into ceiling unprotected and unit in wall. Seal apertures using intumescent mastic. | 1
08-1-16 | Theatre / Pharmacy / DSU | First floor | Theatre Reception | Not applicable. | Supply and install new 60 minute double fire resistant door set complete with frame, glazed 60 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Doors to be decorated to match surrounding doors. | Doors missing between Theatre corridor 1/5A/16 and reception 1/5A/02 area. Reinstate 60 minute fire doors. | 1
08-1-17 | Theatre / Pharmacy / DSU | First floor | Theatre Reception | 10 x 200 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Electrical cupboard 1/5A/03 adjacent to reception area. Penetration of services above electrical distribution. Infill apertures using intumescent mastic. | 1
08-1-18 | Theatre / Pharmacy / DSU | First floor | Theatre Reception | 20 x 80 | The existing fire/smoke curtain was found to be damaged/open at high level. Contractor to undertake remedial work to reinstate the fire/smoke curtain. | Above entrance to Theatre reception, above fire doors. Curtain penetrated. Reinstate or cover over curtain fire stopping. | 1
08-1-19 | Theatre / Pharmacy / DSU | First floor | Theatre Reception | 900 x 1600 | The existing fire/smoke curtain was found to be damaged/open at high level. Contractor to undertake remedial work to reinstate the fire/smoke curtain. | Above cross corridor separation above false ceiling adjacent to Theatre reception entrance. Curtain join broken. Reinstate curtain join. | 1
08-1-20 | Theatre / Pharmacy / DSU | First floor | Theatre Reception | 60 x 400 | The existing fire/smoke curtain was found to be damaged/open at high level. Contractor to undertake remedial work to reinstate the fire/smoke curtain. | Above and to the left of doors accessing Theatre reception. Fire curtain damaged by penetratimng services. Overlay or replace fire curtain section wrapping around penetrating services. | 1
08-1-21 | Theatre / Pharmacy / DSU | First floor | Theatre Reception | Not applicable. | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt around rooms. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Above theatres / reception. No fire stopping or detection in ceiling voids. Build walls up to meet floor plate above surrounding compartment lines using 60 minute rated materials. | 1
10-G-1 | HV/MV Theatre Lifts | Ground floor | Plant Room 19 | 10 x 600 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Above door accessing street corridor. Multiple pipework penetrations. Seal apertures with intumescent mastic. | 1
08-G-1 | Theatre / Pharmacy / DSU | Ground floor | Plant Room 19 | 30 x 30 x 4 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Above and to the right of entrance on wall bordering DSU Reception. 4 copper pipes penetrating wall unsealed. Seal using intumescent mastic. | 1
10-G-2 | HV/MV Theatre Lifts | Ground floor | Plant Room 19 | 15 x 200 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Behind left hand Chlorifier. Penetrating pipework inadequately sealed. Infil perimeter of pipe using intumescent mastic. | 1
10-G-3 | HV/MV Theatre Lifts | Ground floor | Plant Room 19 | 80 x 80 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | To the left hand Chlorifier above the “Tardis”. Penetrating cable inadequately sealed. Infil aperture surrounding cable using elastomeric intumescent wrap. | 1
10-G-4 | HV/MV Theatre Lifts | Ground floor | Plant Room 19 | 180 x 150 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Behind and to the left of left hand Chlorifier. Penetrating pipework inadequately sealed. Infil perimeter of pipe using intumescent batt and intumescent mastic. | 1
10-G-5 | HV/MV Theatre Lifts | Ground floor | Plant Room 19 | 30 x 30 x 4 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall bordering lift lobby. Penetration of three pipes through wall unsealed. Infill perimeter with intumescent mastic. | 1
10-G-6 | HV/MV Theatre Lifts | Ground floor | HV Plant Room | 2400 x 600 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall bordering in store adjacent to door. Penetration of HV cable from plant room through lobby inadequately protected. Box in using 60 minute materials and seal using elastomeric intumescent collars at case of construction. | 1
07-G-02-14 | R&R North | Ground floor | Plant Room 07/G/04/67 | 30 x 100 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall bordering xray. Passage of services unstopped. Overboard area using 60 minute fire rated materials and seal perimeter using intumescent mastic. | 1
07-G-02-15 | R&R North | Ground floor | Plant Room 07/G/04/67 | 20 x 100 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall bordering xray. Passage of services unstopped. Overboard area using 60 minute fire rated materials and seal perimeter using intumescent mastic. | 1
07-G-02-16 | R&R North | Ground floor | Plant Room 07/G/04/67 | 20 x 800 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall bordering X-ray above battery isolator. Passage of service conduit unstopped. Infill aperture using ablative batt, seal perimeter using intumescent mastic. | 1
07-G-02-17 | R&R North | Ground floor | Plant Room 07/G/04/67 | 100 x 50 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Wall bordering disposal above UPS. Passage of cables inadequately stopped. Overboard area above existing fire seal using 60 minute fire rated materials and seal perimeter using intumescent mastic. | 1

## SRH P2As
Drawing Reference | Building | Level | Room | Hole size (mm) | Remedial Actions | Specific details | Photo Ref. | Photo no. | Priority
36-1-1 | Leslie Goldsmith Centre | First floor | Plant room | 200 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using a suitable instumescent mastic | IMG_2451.JPG | 61 | P2A
36-1-2 | Leslie Goldsmith Centre | First floor | Plant room | 250 x 250 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Pipes pass into floor below unprotected. Fill with intumescent mastic sealant. | IMG_2452.JPG | 62 | P2A
06-1-1 | Residential Block 1A | First floor | 06/01/05 | 100 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent batt and intumescent mastic. | IMG_2338.JPG | 6 | P2A
02-2-1 | Residential Block 2 | Second floor | Front door |  | A review of a sample number of doors found that they were not provided with intumescent backed cold smoke seals. It is recommended that intumescent backed cold smoke seals are provided to all of the doors to head and edges of door. Undertake a review of all of the doors and upgrade to them as required. To the existing fire doors without strips undertake the appropriate preparatory works. (a) Remove the existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. | Undertake a review of all flat entrance doors and upgrade as outlined. | IMG_2340.JPG | 7 | P2A
08-2-1 | Residential Block 1B | Second floor | C7 | 1000 x400 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 30 minute fire resistance. | Infill around opening using an intumescent batt and intumescent mastic. | IMG_2341.JPG | 8 | P2A
08-2-2 | Residential Block 1B | Second floor | C7 |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Replace the screen above the door with a new fire resistant board to provide 30 minutes fire resistance. | IMG_2342.JPG | 9 | P2A
08-2-3 | Residential Block 1B | Second floor | Kitchen F | 50 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around opening using an intumescent batt and intumescent mastic. | IMG_2343.JPG | 10 | P2A
08-1-1 | Residential Block 1B | First floor | 08/01/22 | 100 x100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_2344.JPG | 11 | P2A
08-1-2 | Residential Block 1B | First floor | 08/01/22 | 100 x100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent batt and intumescent mastic. | IMG_2345.JPG | 12 | P2A
08-1-3 | Residential Block 1B | First floor | 08/01/22 | 50d | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening using an intumescent batt and intumescent mastic. | IMG_2346.JPG | 13 | P2A
08-1-4 | Residential Block 1B | First floor | 08/01/22 | 100 x100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening using an intumescent batt and intumescent mastic. | IMG_2347.JPG | 14 | P2A
08-1-5 | Residential Block 1B | First floor | 08/01/22 | 50 x 150 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. | IMG_2348.JPG | 15 | P2A
08-1-6 | Residential Block 1B | First floor | S2 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. |  |  |  | P2A
36-R-1 | Leslie Goldsmith Centre | Roof void | Roof void |  | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill around opening using an intumescent batt and intumescent mastic. | IMG_2350.JPG | 17 | P2A
36-R-2 | Leslie Goldsmith Centre | Roof void | Roof void |  | The construction at low level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill gap between floor and wall with and instumescent batt and instumescent mastic | IMG_2351.JPG | 18 | P2A
HS4-69 | Hospital Street 4 | First floor | F / Duct / I | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Cable penetrating. Infill using a suitable intumescent mastic |  |  | P2A
HS4-70 | Hospital Street 4 | First floor | F / Duct / O |  | The indicated door frame was not suitably sealed between the door frame and surrounding wall. Infill the opening around the door frame using a suitable intumescent mastic. | Repair protection between doors | IMG_2365.JPG | 31 | P2A
HS4-71 | Hospital Street 4 | First floor | F / Duct / P |  | The indicated door frame was not suitably sealed between the door frame and surrounding wall. Infill the opening around the door frame using a suitable intumescent mastic. | Above door frame not sealed | IMG_2366.JPG | 32 | P2A
HS4-72 | Hospital Street 4 | First floor | F / Duct / R | 100 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Cables penetrating. Infill using a suitable intumescent mastic | IMG_2367.JPG | 33 | P2A
HS4-73 | Hospital Street 4 | First floor | F / Duct / T |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Pipe penetrating. Infill using a suitable intumescent mastic | IMG_2369.JPG | 35 | P2A
HS4-74 | Hospital Street 4 | First floor | F / Duct / C |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | 2 No cables penetrating. Infill around the cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_2370.JPG | 36 | P2A
HS4-75 | Hospital Street 4 | First floor | F / Duct / B |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Cables penetrating. Infill using a suitable intumescent mastic | IMG_2371.JPG | 37 | P2A
HS4-76 | Hospital Street 4 | First floor | F / Duct / B |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the openings using a new intumescent batt and intumescent mastic. | IMG_2372.JPG | 38 | P2A
HS4-77 | Hospital Street 4 | First floor | Door next to F / Duct / K |  | The indicated door frame was not suitably sealed between the door frame and surrounding wall. Infill the opening around the door frame using a suitable intumescent mastic. | Above door not sealed | IMG_2373.JPG | 39 | P2A
HS4-78 | Hospital Street 4 | First floor | F / Duct / K |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Cables penetrating. Infill using a suitable intumescent mastic | IMG_2374.JPG | 40 | P2A
HS4-79 | Hospital Street 4 | First floor | F / Duct / L | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around the coduit using a new intumescent batt and intumescent mastic. | IMG_2375.JPG | 41 | P2A
HS4-80 | Hospital Street 4 | First floor | Door next to F / Duct / J |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | 2 No coduits penetrating. Infill using a suitable intumescent mastic | IMG_2376.JPG | 42 | P2A
HS4-81 | Hospital Street 4 | First floor | F / Duct / M | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Cables penetrating. Infill using an intumescent batt and intumescent mastic | IMG_2377.JPG | 43 | P2A
HS4-82 | Hospital Street 4 | First floor | F / Duct / M | 100 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Pipe penetrating. Infill the openings using a new intumescent batt and intumescent mastic. | IMG_2378.JPG | 44 | P2A
HS4-84 | Hospital Street 4 | First floor |  |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around the cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_2380.JPG | 46 | P2A
HS4-85 | Hospital Street 4 | First floor |  |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around the cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_2381.JPG | 47 | P2A
HS6-1 | Hospital Street 6 | 1st floor |  |  | The existing automatic hold open device is not operating correctly. Overhaul existing hold open device and ensure that it releases correctly on operation of the fire alarm system. | Double doors from the West Wing to the link corridor |  |  | P2A
HS6-2 | Hospital Street 6 | 1st floor |  | 450 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around pipes and cables using an intumescent batt and intumescent mastic. | IMG_1857.JPG | 1 | P2A
HS6-3 | Hospital Street 6 | 1st floor |  | 2750 x 300 | The construction at high level was not present. Install new fire rated board (60mins FR) suitably fixed to the existing structure. Where cables or conduits pass through the new fire board, ensure that they are suitably infilled using an intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. |  | IMG_1858.JPG | 2 | P2A
HS6-4 | Hospital Street 6 | 1st floor |  | 400 x 300 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill using an intumescent batt, suitably coated and sealed with an intumescent mastic. | IMG_1859.JPG | 3 | P2A
HS6-5 | Hospital Street 6 | 1st floor |  | 250 x 200 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Cut out the existing non-fire resistant foam around the cable tray. Infill the opening using an intumescent batt and intumescent mastic. | IMG_1861.JPG | 5 | P2A
HS6-6 | Hospital Street 6 | 1st floor |  | 300 x 300 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1862.JPG | 6 | P2A
HS6-7 | Hospital Street 6 | 1st floor |  | 100 | Pipes were observed passing through the indicated compartmentation. Infill around the existing pipe using a suitable intumescent mastic and then provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. 2 no. | IMG_1866.JPG | 9 | P2A
HS6-8 | Hospital Street 6 | 1st floor |  | 40 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cable using an intumescent mastic. | IMG_1867.JPG | 10 & 11 | P2A
HS6-9 | Hospital Street 6 | 1st floor |  | Small | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. Infill plastic conduit using an intumescent mastic. (4 no.) | IMG_1870.JPG | 12 | P2A
HS6-10 | Hospital Street 6 | 1st floor |  | Small | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill holes using an intumescent mastic (3 no). | IMG_1871.JPG | 13 | P2A
HS6-11 | Hospital Street 6 | 1st floor |  | Small | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic (3 no). | IMG_1872.JPG | 14 | P2A
HS6-12 | Hospital Street 6 | 1st floor |  |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing locking device and ensure positive self closure into the frame. |  |  |  | P2A
HS6-13 | Hospital Street 6 | 1st floor |  | 200 dia. | Pipes were observed passing through the indicated compartmentation. Infill around the existing pipe using a suitable intumescent mastic and then provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Infill opening using an intumescent mastic. | IMG_1873.JPG | 15 | P2A
HS6-14 | Hospital Street 6 | 1st floor |  | 250 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1874.JPG | 16 | P2A
HS6-15 | Hospital Street 6 | 1st floor |  | 2000 x 20 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. |  |  | P2A
HS6-16 | Hospital Street 6 | 1st floor |  | 1800 x 20 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1875.JPG | 18 | P2A
HS6-17 | Hospital Street 6 | 1st floor |  | Small | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. (4 no) | IMG_1876.JPG | 19 | P2A
HS6-18 | Hospital Street 6 | 1st floor |  | Small | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2 no) | IMG_1877.JPG | 20 | P2A
HS6-19 | Hospital Street 6 | 1st floor |  | Small | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_1878.JPG | 21 | P2A
HS6-20 | Hospital Street 6 | 1st floor |  | 200 dia. | Pipes were observed passing through the indicated compartmentation. Infill around the existing pipe using a suitable intumescent mastic and then provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1880.JPG | 23 | P2A
HS6-21 | Hospital Street 6 | 1st floor |  | 400 x 300 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1881.JPG | 24 | P2A
HS6-22 | Hospital Street 6 | 1st floor |  | 300 x 300 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1882.JPG | 25 | P2A
HS6-23 | Hospital Street 6 | 1st floor |  | 200 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening around the cable tray using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). | IMG_1886.JPG | 26 | P2A
HS6-24 | Hospital Street 6 | 1st floor |  | 200 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening around the cable tray using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). | IMG_1887.JPG | 27 | P2A
HS6-25 | Hospital Street 6 | 1st floor |  | 200 x 150 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening around the tray using an intumescent batt and intumescent mastic. | IMG_1888.JPG | 28 | P2A
HS6-26 | Hospital Street 6 | 1st floor |  | 2500 x 20 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Cut out the existing non-fire resistant foam around the cable tray. Infill the opening using an intumescent batt and intumescent mastic. | IMG_1890.JPG | 30 | P2A
HS6-27 | Hospital Street 6 | 1st floor |  | 250 x 250 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Cut out the existing non-fire resistant foam around the cable tray. Infill the opening using an intumescent batt and intumescent mastic. | IMG_1891.JPG | 31 | P2A
HS6-28 | Hospital Street 6 | 1st floor |  | 1000 x 500 | The construction at high level was not present. Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure that they are suitable back coated with intumescent mastic. Infill openings using a suitable intumescent mastic or similar to provide a minimum 60 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1898.JPG | 32 | P2A
HS6-29 | Hospital Street 6 | 1st floor |  | 1000 x 500 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Cut out the existing non-fire resistant foam around the cable tray. Infill the opening using an intumescent batt and intumescent mastic. | IMG_1899.JPG | 32 | P2A
HS6-30 | Hospital Street 6 | 1st floor |  | 500 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening around the cable tray using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). | IMG_1900.JPG | 33 | P2A
HS6-31 | Hospital Street 6 | 1st floor |  | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1901.JPG | 34 | P2A
HS6-32 | Hospital Street 6 | 1st floor |  | 250 x 250 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1903.JPG | 35 | P2A
HS6-33 | Hospital Street 6 | 1st floor |  | 150 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1905.JPG | 36 | P2A
HS6-34 | Hospital Street 6 | 1st floor |  | 200 dia. | Pipes were observed passing through the indicated compartmentation. Infill around the existing pipe using a suitable intumescent mastic and then provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Infill the opening using an intumescent mastic. | IMG_1907.JPG | 38 | P2A
HS6-35 | Hospital Street 6 | 1st floor |  | 250 x 250 | Pipes were observed passing through the indicated compartmentation. Infill around the existing pipe using a suitable intumescent mastic and then provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. |  |  | P2A
HS6-36 | Hospital Street 6 | 1st floor |  | 3000 x 600 | The existing fire/smoke curtain was found to be damaged/open at high level. Contractor to undertake remedial work to reinstate the fire/smoke curtain. | Undertake remedial attention to the fire/smoke curtain. | IMG_1910.JPG | 39 | P2A
HS6-37 | Hospital Street 6 | 1st floor |  | 250 x 250 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. 2 no. | IMG_1912.JPG | 40 | P2A
HS6-38 | Hospital Street 6 | 1st floor |  | 100 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_1917.JPG | 41 | P2A
HS6-39 | Hospital Street 6 | 1st floor |  | 150 x 150 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_1921.JPG | 42 | P2A
20-1-1 | West Block | 1 | 20/01/03/43 | 2 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Two pipes pass into floor above unprotected. Fill with intumescent mastic sealant. 60 mins FR. | IMG_0003.JPG | 0 | P2A
20-1-2 | West Block | 1 | 20/01/03/43 | Unknown. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Large diameter black metal pipe passes into floor plate above surrounding area over boarded with timber. Remove timber plate to investigate and if required replace timber with mortar seal surrounding pipe to the depth of the floor plate. 60 mins FR | IMG_0004.JPG | 0 | P2A
20-1-3 | West Block | 1 | 20/01/03/43 | Unknown. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Protected lagged pipe passes into floor plate above surrounding area over boarded with timber. Remove timber plate to investigate and if required replace timber with mortar seal surrounding pipe to the depth of the floor plate. 60 mins FR. | IMG_0005.JPG | 0 | P2A
20-1-4 | West Block | 1 | 20/01/03/42 | 2 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Two plastic conduits pass through wall unprotected. Protective lagged pipework passes through wall through excessive diameter Aperture unsealed. Infill the plastic conduit with intumescent mastic. Overboard the area surrounding pipework using 30 minute fire rated material and seal the perimeter and the joint at the pipework using intumescent mastic. 30 mins FR. | IMG_0007.JPG | 0 | P2A
20-1-5 | West Block | 1 | 20/01/03/42 | 10 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Metal ventilation pipe work passes through excessive aperture in wall unprotected and without damper. Install and intumescent damper into the pipework and infill the area surrounding the pipework using intumescent sealant. 30 Mins FR. | IMG_0008.JPG | 0 | P2A
20-1-6 | West Block | 1 | 20/01/03/41 | 10 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Orange data cable passes through unsealed aperture. Infill aperture using intumescent mastic. 30 Mins FR. | IMG_0009.JPG | 0 | P2A
20-1-7 | West Block | 1 | 20/01/03/41 | 20mm x room perimeter | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Example of inadequate seal between wall and floor plate above. This exists at the perimeter of this room. Infill gap between head of wall and floor plate above using intumescent movement seal. 30 mins FR. | IMG_0010.JPG | 0 | P2A
20-1-8 | West Block | 1 | 20/01/03/41 | 100 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Fire alarm cable passing through 2 plastic conduits through excessive aperture. Infill conduits at the point they pass through the wall using intumescent sealant. Infill surrounding area using fire rated foam. Remove the surface excess and coat with a 3 mm layer of intumescent sealant. 30 Mins FR. | IMG_0011.JPG | 0 | P2A
20-1-9 | West Block | 1 | 20/01/03/41 | 100 x 100 x 5 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Five protective lagged pipes pass through excessive aperture in the wall. Infill aperture surrounding pipework using fire rated foam. Once dry remove surface Excess of foam and coat using a 3 mm layer of intumescent sealant. 30 Mins FR. | IMG_0012.JPG | 0 | P2A
20-1-10 | West Block | 1 | 20/01/03/41 | 300 x 15 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable trays carrying data cables and fire alarm cables pass through excessive aperture in the wall inadequately sealed using Rockwool. Remove previous attempts at Fire stopping and replace with ablative batt, cut to size and sealed at the perimeter / around services using intumescent sealant. It is recommended that a gap is left above the largest cable tray and infilled with an intumescent pillow so that this may be easily maintained for future use. 30 Mins FR. | IMG_0013.JPG | 0 | P2A
20-1-11 | West Block | 1 | 20/01/03/32 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Purple data cable passes through unprotected plastic conduit. Infill plastic conduit using intumescent mastic. 30 Mins FR. | IMG_0014.JPG | 0 | P2A
20-1-12 | West Block | 1 | 20/01/03/32 | 960 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Inspection hatches in place but no other evidence of fire dampers. Fire rated protection provided for ductwork. Investigate the presence of dampers. 30 Mins FR. | IMG_0015.JPG | 0 | P2A
20-1-13 | West Block | 1 | 20/01/03/27 | 40 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | White plastic Pipework passes through wall and adequately protected. Fit an intumescent corner collar to the pipe. 30 Mins FR. | IMG_0016.JPG | 0 | P2A
20-1-14 | West Block | 1 | 20/01/03/34 | 40 x perimeter of room | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Inadequate fire protection between head of wall and floor flat above. Overboard this immediate area and seal around the boarding using intumescent sealant. The remaining aperture at the head of the wall for the room should be sealed using an intumescent movement seal. 30 Mins FR. | IMG_0017.JPG | 0 | P2A
20-1-15 | West Block | 1 | 20/01/03/34 | 200 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Protective lagged pipework passes through excessive aperture in wall. Infill aperture surrounding pipework using fire rated foam. Once dry remove the surface excess and coat using a three mm layer of intumescent sealant. This should be undertaken for the entry and exit of this pipe. 30 Mins FR. | IMG_0018.JPG | 0 | P2A
20-1-16 | West Block | 1 | 20/01/03/34 | 30 x 20 x 3 penetrations | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Three plastic conduits pass through wall inadequately sealed. Infill plastic conduit's at that point they pass through the wall using intumescent sealant. The apertures surrounding the plastic conduits should be infilled using intumescent sealant. 30 Mins FR. | IMG_0019.JPG | 0 | P2A
20-1-17 | West Block | 1 | 20/01/03/34 | 120 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Open cable trays pass through unprotected aperture in wall. Infill area surrounding cable trays using intumescent pillows. Seal aperture surrounding encosed tray with intumescent mastic sealant. 30 Mins FR. | IMG_0020.JPG | 0 | P2A
20-1-18 | West Block | 1 | 20/01/03/34 | 120 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Open cable trays pass through unprotected aperture in wall. Infill area surrounding cable trays using intumescent pillows. Seal aperture surrounding encosed tray with intumescent mastic sealant. 30 Mins FR. | IMG_0021.JPG | 0 | P2A
20-1-19 | West Block | 1 | 20/01/03/34 | Numerous | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Multiple plastic conduits and a fire alarm cable pass through wall inadequately sealed. Infill plastic conduit's at that point they pass through the wall using intumescent sealant. The apertures surrounding the plastic conduits should be expanded to a 20mm radius surrounding the pipe and infilled using intumescent sealant rated to crush the pipe. The aperture surrounding the fire alarm cable should be infilled with intumescent sealant. 30 Mins FR. | IMG_0022.JPG | 0 | P2A
20-1-20 | West Block | 1 | 20/01/03/36 | 200 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Protective lagged pipework passes through excessive aperture in wall. Infill aperture surrounding pipe work using fire rated foam. Once dry remove surface excess and skim foam using intumescent mastic. 30 Mins FR. | IMG_0023.JPG | 0 | P2A
20-1-21 | West Block | 1 | 20/01/03/36 | 250 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable trays pass through wall inadequately protected using loosely packed Glass wool. Infill area behind cable trays with Glass wool and supplement the Infill using intumescent pillows. Overboard the area above the cable trays using 30 minute fire rated material sealed at the perimeter using intumescent mastic. | IMG_0024.JPG | 0 | P2A
20-1-22 | West Block | 1 | 20/01/03/36 | 10 x perimeter | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Inadequate fire protection between head of wall and floor plate above. The aperture at the head of the wall for the room should be sealed using intumescent mastic. 30 Mins FR. | IMG_0025.JPG | 0 | P2A
20-1-23 | West Block | 1 | 20/01/03/36 | 20 x perimeter of duct | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Ventilation ducting passes through wall without damper and through excessive unprotected aperture. Seal the peimeter of the ducting using intumescent sealant . Infill the damper using an intumescent grill. 30 Mins FR. | IMG_0026.JPG | 0 | P2A
20-1-24 | West Block | 1 | 20/01/03/36 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Unprotected plastic conduit passes through wall above door. Infill plastic conduit using intumescent sealant at point it passes through the wall. 30 Mins FR. | IMG_0027.JPG | 0 | P2A
20-1-25 | West Block | 1 | 20/01/03/36 | Numerous | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Multiple white plastic conduits and a black flexible conduit pass through wall inadequately sealed. Infill plastic conduit's at the point they pass through the wall using intumescent sealant. 30 Mins FR. | IMG_0028.JPG | 0 | P2A
20-1-26 | West Block | 1 | 20/01/03/32 | 20 x 40 and 20 x perimeter of ducting | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | No evidence of fire dampers. Fire rated protection provided for ductwork. Fire stopping surrounding penetration appears inadequate. Investigate the presence of dampers. Seal the perimeter of the duct work using intumescent sealant. Infill any conduit at the point it passes through the wall. 30 Mins FR. | IMG_0029.JPG | 0 | P2A
20-1-27 | West Block | 1 | 20/01/03/35 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Iron pipe passes through floorplate apparently unsealed. Infil pipework using intumescent sealant to the depth of 100mm. 60 Mins FR. | IMG_0030.JPG | 0 | P2A
20-1-28 | West Block | 1 | 20/01/03/09 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable passes through wall in plastic conduit apparently unsealed. Infill conduit and seal perimeter with intumescent sealant. 30 Mins FR. | IMG_0031.JPG | 0 | P2A
20-1-29 | West Block | 1 | 20/01/03/09 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable passes through wall in plastic conduit apparently unsealed. Infill conduit and seal perimeter with intumescent sealant. 30 Mins FR. | IMG_0032.JPG | 0 | P2A
20-1-30 | West Block | 1 | 20/01/03/46 | 20 x perimeter of cupboard | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Perimeter seal at the head of the wall is inadequate. Seal perimeter of cupboard construction using intumescent sealant. 30 Mins FR. | IMG_0033.JPG | 0 | P2A
20-1-31 | West Block | 1 | 20/01/03/46 | 150 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable tray passes through excessive aperture in wall inadequately stopped. Seal gap above cable and to the side of cable tray using ablative batt. Wrap cables and lower part of tray in elastomeric intumescent wrap. Seal perimeter of above work with intumescent sealant. 30 Mins FR. | IMG_0034.JPG | 0 | P2A
20-1-32 | West Block | 1 | 20/01/03/46 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Conduit and cable penetrates wall inadequately sealed. Infill the conduit and seal the perimeter with intumescent sealant. 30 Mins FR. | IMG_0035.JPG | 0 | P2A
20-1-33 | West Block | 1 | 20/01/03/46 | 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Plastic pipework passes through floor plate unprotected. Cut away the excess of the pink foam and fit an intumescent closing collar. Ensure the collar is fitted securely to the floor plate above. 60 Mins FR. | IMG_0036.JPG | 0 | P2A
20-1-34 | West Block | 1 | 20/01/03/46 | 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Plastic pipework passes through wall unprotected. Fit an intumescent closing collar. Ensure the collar is fitted securely to the wall. 30 Mins FR. | IMG_0037.JPG | 0 | P2A
20-1-35 | West Block | 1 | 20/01/01/08 | 150 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Missing compartmentation on wall to allow passage of services. Infill area with ablative batt sealed at the perimeter using intumescent sealant. 30 Mins FR. | IMG_0038.JPG | 0 | P2A
20-1-36 | West Block | 1 | 20/01/01/08 | 150 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Passage of black plastic ventilation ducting through wall unprotected. Fit intumescent closing collar to the duct on the dirty utility side of the wall. 30 Mins FR. | IMG_0039.JPG | 0 | P2A
20-1-37 | West Block | First Floor | 20-01-01-17 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0001 (Small).JPG | 1 | P2A
20-1-38 | West Block | First Floor | 20-01-01-21 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening and conduits with intumescent mastic. (3no) | IMG_0002 (Small).JPG | 2 | P2A
20-1-39 | West Block | First Floor | 20-01-01-21 | 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent batt and intumescent mastic. | IMG_0003 (Small).JPG | 3 | P2A
20-1-40 | West Block | First Floor | 20-01-01-21 | 10 D, 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening and cables with intumescent mastic. | IMG_0004 (Small).JPG | 4 | P2A
20-1-41 | West Block | First Floor | 20-01-01-21 | 10 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0005 (Small).JPG | 5 | P2A
20-1-42 | West Block | First Floor | 20-01-01-25 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0006 (Small).JPG | 6 | P2A
20-1-43 | West Block | First Floor | 20-01-01-25 | 20 D, 5 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables and pipe with intumescent mastic. (3no) | IMG_0007 (Small).JPG | 7 | P2A
20-1-44 | West Block | First Floor | 20-01-01-34 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0008 (Small).JPG | 8 | P2A
20-1-45 | West Block | First Floor | 20-01-01-31 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0009 (Small).JPG | 9 | P2A
20-1-46 | West Block | First Floor | 20-01-01-37 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0010 (Small).JPG | 10 | P2A
20-1-47 | West Block | First Floor | 20-01-01-33 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 120 minutes fire resistance in accordance with BS 476. | Infill around pipe with intumescent mastic. (3no) | IMG_0011 (Small).JPG | 11 | P2A
20-1-48 | West Block | First Floor | 20-01-01-44 | 1000 x 2000 | Confirm that fireboard provides 60 minutes resisting construction. |  | IMG_0012 (Small).JPG | 12 | P2A
20-1-49 | West Block | First Floor | 20-01-02-13 | 300 x 2000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0014 (Small).JPG | 14 | P2A
20-1-50 | West Block | First Floor | 20-01-02-01 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0015 (Small).JPG | 15 | P2A
20-1-51 | West Block | First Floor | 20-01-02-02 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0016 (Small).JPG | 16 | P2A
20-1-52 | West Block | First Floor | 20-01-02-03 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0017 (Small).JPG | 17 | P2A
07-1-1 | Donald Wilson NRC | First Floor | 07-01-105 | 30 x 40 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 30 minute fire resistance. | Remove non-fire rated foam and infill head space using an intumescent batt and intumescent mastic. | IMG_0001 (Small).JPG | 1 | P2A
07-1-2 | Donald Wilson NRC | First Floor | 07-01-105 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cut out the existing non-fire resistant foam. Infill the openings using an intumescent batt and intumescent mastic. | IMG_0002 (Small).JPG | 2 | P2A
07-1-3 | Donald Wilson NRC | First Floor | 07-01-103 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0003 (Small).JPG | 3 | P2A
07-1-4 | Donald Wilson NRC | First Floor | 07-01-102 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0004 (Small).JPG | 4 | P2A
07-1-5 | Donald Wilson NRC | First Floor | 07-01-104 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0005 (Small).JPG | 5 | P2A
55-1-1 | Chichester Treatment Centre | First Floor | 55-01-03-27 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill gap inside conduit with intumescent mastic. | IMG_0001.JPG | 1 | P2A
55-1-2 | Chichester Treatment Centre | First Floor | 55-01-03-24 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill gap inside conduit with intumescent mastic. | IMG_0002.JPG | 2 | P2A
55-1-3 | Chichester Treatment Centre | First Floor | 55-01-03-24 | 40 dia. 40 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the openings using an intumescent batt and intumescent mastic. (2no) | IMG_0003.JPG | 3 | P2A
55-1-4 | Chichester Treatment Centre | First Floor | 55-01-03-24 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0004.JPG | 4 | P2A
55-1-5 | Chichester Treatment Centre | First Floor | 55-01-03-11 | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0005.JPG | 5 | P2A
55-1-6 | Chichester Treatment Centre | First Floor | 55-01-03-24 | 1500 x 5000 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the soffit. Install 60 minute fire resisting fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0006.JPG | 6 | P2A
55-1-7 | Chichester Treatment Centre | First Floor | 55-01-03-24 | 50 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove foam and infill around cable trays using an intumescent batt and intumescent mastic. | IMG_0007.JPG | 7 | P2A
55-1-8 | Chichester Treatment Centre | First Floor | 55-01-04-01 | 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0008.JPG | 8 | P2A
55-1-9 | Chichester Treatment Centre | First Floor | 55-01-04-01 | 50 x 200 100 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent batt and intumescent mastic. | IMG_0009.JPG | 9 | P2A
55-1-10 | Chichester Treatment Centre | First Floor | 55-01-04-01 | 100 x 5000 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Confirm that head space is adeqautely firestopped. | IMG_0010.JPG | 10 | P2A
55-1-11 | Chichester Treatment Centre | First Floor | 55-01-04-01 | 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0011.JPG | 11 | P2A
55-1-12 | Chichester Treatment Centre | First Floor | 55-01-04-01 | 40 x 200 10 dia. 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable trays using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). Infill around cables using an intumescent mastic. (2No) | IMG_0012.JPG | 12 | P2A
55-1-13 | Chichester Treatment Centre | First Floor | 55-01-03-23 | 1500 x 200 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0013.JPG | 13 | P2A
55-1-14 | Chichester Treatment Centre | First Floor | 55-01-03-20 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0014.JPG | 14 | P2A
55-1-15 | Chichester Treatment Centre | First Floor | 55-01-03-20 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove insulation and infill the opening using an intumescent batt and intumescent mastic. | IMG_0015.JPG | 15 | P2A
55-1-16 | Chichester Treatment Centre | First Floor | 55-01-04-28 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0016.JPG | 16 | P2A
55-1-17 | Chichester Treatment Centre | First Floor | 55-01-04-28 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (6no) | IMG_0017.JPG | 17 | P2A
55-1-18 | Chichester Treatment Centre | First Floor | 55-01-04-28 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0018.JPG | 18 | P2A
55-1-19 | Chichester Treatment Centre | First Floor | 55-01-04-28 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. (2no) | IMG_0019.JPG | 19 | P2A
55-1-20 | Chichester Treatment Centre | First Floor | 55-01-04-19 | 200 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around ductwork with intumescent mastic. | IMG_0020.JPG | 20 | P2A
55-1-21 | Chichester Treatment Centre | First Floor | 55-01-04-17 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0021.JPG | 21 | P2A
55-1-22 | Chichester Treatment Centre | First Floor | 55-01-04-17 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0022.JPG | 22 | P2A
55-1-23 | Chichester Treatment Centre | First Floor | 55-01-04-11 | 50 dia. 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the openings using an intumescent mastic. (2no) | IMG_0023.JPG | 23 | P2A
55-1-24 | Chichester Treatment Centre | First Floor | 55-01-04-11 | 50 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable trays using an intumescent batt and intumescent mastic (3no). (If the route is to be used frequently consider using intumescent pillows). | IMG_0024.JPG | 24 | P2A
55-1-25 | Chichester Treatment Centre | First Floor | 55-01-04-10 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0025.JPG | 25 | P2A
55-1-26 | Chichester Treatment Centre | First Floor | 55-01-04-10 |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with pipe collars on both penetrating sides. (2no) | IMG_0026.JPG | 26 | P2A
55-1-27 | Chichester Treatment Centre | First Floor | 55-01-04-09 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. | The fire rating of the door couldn’t be determined. Ensure a door of specification FD30S is provided. | IMG_0027.JPG | 27 | P2A
55-1-28 | Chichester Treatment Centre | First Floor | 55-01-04-09 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0028.JPG | 28 | P2A
55-1-29 | Chichester Treatment Centre | First Floor | 55-01-04-09 | 10 dia. 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit and around cables with intumescent mastic. (2no) | IMG_0029.JPG | 29 | P2A
55-1-30 | Chichester Treatment Centre | First Floor | 55-01-04-09 | 2000 x 8000 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the soffit. Install 60 minute fire resisting fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0030.JPG | 30 | P2A
55-1-31 | Chichester Treatment Centre | First Floor | 55-01-04-09 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill inside and around conduit and cables with intumescent mastic. (2no) | IMG_0031.JPG | 31 | P2A
55-1-32 | Chichester Treatment Centre | First Floor | 55-01-04-09 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0032.JPG | 32 | P2A
55-1-33 | Chichester Treatment Centre | First Floor | 55-01-04-09 | 400 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable tray using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). | IMG_0033.JPG | 33 | P2A
55-1-34 | Chichester Treatment Centre | First Floor | 55-01-01-09 | 600 x 1000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | fire stopping to be adressed for pipes and cable tray | IMG_0034.JPG | 34 | P2A
55-1-35 | Chichester Treatment Centre | First Floor | 55-01-01-12 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (3no) | IMG_0035.JPG | 35 | P2A
55-1-36 | Chichester Treatment Centre | First Floor | 55-01-01-13 | 20 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0036.JPG | 36 | P2A
55-1-37 | Chichester Treatment Centre | First Floor | 55-01-01-13 | 10 x 60 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0037.JPG | 37 | P2A
55-1-38 | Chichester Treatment Centre | First Floor | 55-01-01-13 | 20 dia. 10 x 20 20 x 30 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables and conduits using an intumescent mastic. (4no) | IMG_0038.JPG | 38 | P2A
55-1-39 | Chichester Treatment Centre | First Floor | 55-01-01-13 | 30 dia. 30 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening and around cable with intumescent mastic. | IMG_0039.JPG | 39 | P2A
55-1-40 | Chichester Treatment Centre | First Floor | 55-01-01-13 | 150 dia. 100 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (2no) | IMG_0040.JPG | 40 | P2A
55-1-41 | Chichester Treatment Centre | First Floor | 55-01-01-13 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0041.JPG | 41 | P2A
55-1-42 | Chichester Treatment Centre | First Floor | 55-01-01-14 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0042.JPG | 42 | P2A
55-1-43 | Chichester Treatment Centre | First Floor | 55-01-01-14 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0043.JPG | 43 | P2A
55-1-44 | Chichester Treatment Centre | First Floor | 55-01-01-14 | 20 x 50 60 x 60 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe and ductwork with intumescent mastic. (2no) | IMG_0044.JPG | 44 | P2A
55-1-45 | Chichester Treatment Centre | First Floor | 55-01-01-15 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. | The fire rating of the door wasn’t determined. Ensure that the door meets the specifaction of a FD30S door. | IMG_0045.JPG | 45 | P2A
55-1-46 | Chichester Treatment Centre | First Floor | 55-01-01-16 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0046.JPG | 46 | P2A
55-1-47 | Chichester Treatment Centre | First Floor | 55-01-01-17 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0047.JPG | 47 | P2A
55-1-48 | Chichester Treatment Centre | First Floor | 55-01-01-19 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. | The fire rating of the door wasn’t determined. Ensure that the door meets the specifaction of a FD30S door. | IMG_0048.JPG | 48 | P2A
55-1-49 | Chichester Treatment Centre | First Floor | 55-01-01-21 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0049.JPG | 49 | P2A
55-1-50 | Chichester Treatment Centre | First Floor | 55-01-01-23 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0050.JPG | 50 | P2A
55-1-51 | Chichester Treatment Centre | First Floor | 55-01-01-25 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0051.JPG | 51 | P2A
55-1-52 | Chichester Treatment Centre | First Floor | 55-01-01-26 | 30 dai. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0052.JPG | 52 | P2A
55-1-53 | Chichester Treatment Centre | First Floor | 55-01-01-26 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0053.JPG | 53 | P2A
55-1-54 | Chichester Treatment Centre | First Floor | 55-01-01-27 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0054.JPG | 54 | P2A
55-1-55 | Chichester Treatment Centre | First Floor | 55-01-01-27 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0055.JPG | 55 | P2A
55-1-56 | Chichester Treatment Centre | First Floor | 55-01-01-27 | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0056.JPG | 56 | P2A
55-1-57 | Chichester Treatment Centre | First Floor | 55-01-01-27 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0057.JPG | 57 | P2A
20-1-55 | West Block | First Floor | 20/01/02/02 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the roof wasn’t determined. Provide 60 minute FR construction. | IMG_0104.JPG | 104 | P2A
20-1-56 | West Block | First Floor | 20/01/02/02 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 minute FR floor construction. | IMG_0105.JPG | 105 | P2A
20-1-57 | West Block | First Floor | 20/01/02/02 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0106.JPG | 106 | P2A
20-1-58 | West Block | First Floor | 20/01/02/02 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0107.JPG | 107 | P2A
20-1-59 | West Block | First Floor | 20/01/02/02 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0108.JPG | 108 | P2A
20-1-60 | West Block | First Floor | 20/01/02/02 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. | IMG_0109.JPG | 109 | P2A
20-1-61 | West Block | First Floor | 20/01/02/02 | 300 x 3000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Insert a structurally supported intumescent batt into the gap in floor. | IMG_0110.JPG | 110 | P2A
20-1-62 | West Block | First Floor | 20/01/02/03 | 400 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Provide hatch to close opening in ceiling. FR 60 | IMG_0111.JPG | 111 | P2A
20-1-63 | West Block | First Floor | 20/01/02/03 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable tray with intumescent mastic. | IMG_0112.JPG | 112 | P2A
20-1-88 | West Block | First Floor | 20-01-01-46 | 700 x 2500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0232 (Small).JPG | 107 | P2A
20-1-89 | West Block | First Floor | 20-01-01-46 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0233 (Small).JPG | 108 | P2A
20-1-90 | West Block | First Floor | 20-01-01-46 | 100 x 2000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0234 (Small).JPG | 109 | P2A
20-1-91 | West Block | First Floor | 20-01-01-46 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 min FR floor construction. | IMG_0235 (Small).JPG | 110 | P2A
20-1-92 | West Block | First Floor | 20-01-01-46 | 50 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent mastic. (3no) | IMG_0236 (Small).JPG | 111 | P2A
20-1-93 | West Block | First Floor | 20-01-01-46 | 30 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0237 (Small).JPG | 112 | P2A
20-1-94 | West Block | First Floor | 20-01-01-46 | 30 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening with intumescent mastic. FR 60 | IMG_0238 (Small).JPG | 113 | P2A
07-1-6 | Donald Wilson NRC | First Floor | 116 Plant Room | 400 D | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill openings using an intumescent batt and intumescent mastic. | IMG_0311 (Small).JPG | 62 | P2A
07-1-7 | Donald Wilson NRC | First Floor | 116 Plant Room | 50 x 100 across perimeter of room | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam in head space and replace with cavity barriers. Remove non-fire rated foam around cable and use an intumescent batt and intumescent mastic. (30no) | IMG_0312 (Small).JPG | 63 | P2A
01-G-01-1 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-01 | 1500 x 3000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0065 (Small).JPG | 65 | P2A
01-G-01-2 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-11 | 2000 x 2000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Ensure that the batt components are fixed together and penetration gaps are sealed off using suitable intumescent mastic. | IMG_0066 (Small).JPG | 66 | P2A
01-G-01-3 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-07 | 300 x 2000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0067 (Small).JPG | 67 | P2A
01-G-01-4 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-07 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0068 (Small).JPG | 68 | P2A
01-G-01-5 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-08 | 2000 x 7000 | Confirm head space detail is adequately firestopped at the soffit without any gaps through the installation to ensure 30 minute fire resistance. |  | IMG_0069 (Small).JPG | 69 | P2A
01-G-01-6 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-08 | 100 x 300 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard is not provided in the head space above the ductwork duct. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0070 (Small).JPG | 70 | P2A
01-G-01-7 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-08 | 2000 x 3000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Ensure that the batt components are fixed together and penetration gaps are sealed off using suitable intumescent mastic. | IMG_0071 (Small).JPG | 71 | P2A
01-G-01-8 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-32 | 20 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0072 (Small).JPG | 72 | P2A
01-G-01-9 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-36 | 100 x 1000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0073 (Small).JPG | 73 | P2A
01-G-01-10 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-36 | 500 x 8000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0074 (Small).JPG | 74 | P2A
01-G-01-11 | Main Hospital - Emergency Floor | Ground floor | 01-G-01-36 | 50 x 50 100 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent mastic. (2no) | IMG_0075 (Small).JPG | 75 | P2A
01-G-01-12 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-90 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0005 (Small).JPG | 5 | P2A
01-G-01-13 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-90 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0006 (Small).JPG | 6 | P2A
01-G-01-14 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-86 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0007 (Small).JPG | 7 | P2A
01-G-01-15 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-73 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0008 (Small).JPG | 8 | P2A
01-G-01-16 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-73 | 50 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0009 (Small).JPG | 9 | P2A
01-G-01-17 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-73 | 50 x 250 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable tray using an intumescent mastic. | IMG_0010 (Small).JPG | 10 | P2A
01-G-01-18 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-91 |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | IMG_0011 (Small).JPG | 11 | P2A
01-G-01-19 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-81 |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. | IMG_0012 (Small).JPG | 12 | P2A
01-G-01-20 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-79 |  | Confirm that head detail is sufficently firestopped with cavity barriers or intumescent expansion joint seal. |  | IMG_0013 (Small).JPG | 13 | P2A
01-G-01-21 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-78 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0014 (Small).JPG | 14 | P2A
01-G-01-22 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-78 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0015 (Small).JPG | 15 | P2A
01-G-01-23 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-65 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0016 (Small).JPG | 16 | P2A
01-G-01-24 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-65 | 10 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent batt and intumescent mastic. | IMG_0017 (Small).JPG | 17 | P2A
01-G-01-25 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-67 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0018 (Small).JPG | 18 | P2A
01-G-01-26 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-67 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0019 (Small).JPG | 19 | P2A
01-G-01-27 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-68 | 2500 x 2500 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Provide 60 min FR ceiling. With suitable board and fixings | IMG_0020 (Small).JPG | 20 | P2A
01-G-01-28 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-68 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0021 (Small).JPG | 21 | P2A
01-G-01-29 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-52 |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 30 minute fire resistance. | Remove overfilled non-fire rated foam. Infill around cable tray using an intumescent batt and intumescent mastic. (If the route is to be used frequently consider using intumescent pillows). | IMG_0022 (Small).JPG | 22 | P2A
01-G-01-30 | Main Hospital - Emergency Floor | Ground Floor | 01-G-01-52 | 50 D | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipe with a pipe collar. Remove non-fire rated foam. Infill around pipe using an intumescent mastic. | IMG_0023 (Small).JPG | 23 | P2A
01-01-04-1 | Main Hospital - Bosham Ward | First Floor | 01-01-04-44 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0067 (Small).JPG | 67 | P2A
01-01-04-2 | Main Hospital - Bosham Ward | First Floor | 01-01-04-43 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0068 (Small).JPG | 68 | P2A
01-01-04-3 | Main Hospital - Bosham Ward | First Floor | 01-01-04-39 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around black cables using an intumescent mastic. (2no) | IMG_0069 (Small).JPG | 69 | P2A
01-01-04-4 | Main Hospital - Bosham Ward | First Floor | 01-01-04-32 | 20 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0070 (Small).JPG | 70 | P2A
01-01-04-5 | Main Hospital - Bosham Ward | First Floor | 01-01-04-34 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0071 (Small).JPG | 71 | P2A
01-01-04-6 | Main Hospital - Selsey Ward | First Floor | 01-01-04-72 | 50 x 70, 100 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove protruding insulation and infill opening and around pipes using an intumescent batt and intumescent mastic. (3no) | IMG_0072 (Small).JPG | 72 | P2A
01-01-06-1 | Main Hospital - Intensive Care Unit | First Floor | 01-01-06-16 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. | The lock needs maintenance to close the gap present. | IMG_0073 (Small).JPG | 73 | P2A
01-01-06-2 | Main Hospital - Intensive Care Unit | First Floor | 01-01-06-16 |  | Confirm that head detail is sufficently firestopped with cavity barriers or intumescent expansion joint seal. |  | IMG_0074 (Small).JPG | 74 | P2A
01-01-06-3 | Main Hospital - Intensive Care Unit | First Floor | 01-01-06-16 | 200 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. | IMG_0075 (Small).JPG | 75 | P2A
01-01-06-4 | Main Hospital - Intensive Care Unit | First Floor | 01-01-06-16 | 300 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around ductwork using an intumescent batt and intumescent mastic. | IMG_0076 (Small).JPG | 76 | P2A
01-01-06-5 | Main Hospital - Intensive Care Unit | First Floor | 01-01-06-26 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0077 (Small).JPG | 77 | P2A
01-01-09-1 | Main Hospital - Middleton Ward | First floor | 01-01-09-01 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0001 (Small).JPG | 1 | P2A
01-01-09-2 | Main Hospital - Middleton Ward | First floor | 01-01-09-01 | 100 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0002 (Small).JPG | 2 | P2A
01-01-09-3 | Main Hospital - Middleton Ward | First floor | 01-01-09-01 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0003 (Small).JPG | 3 | P2A
01-01-09-4 | Main Hospital - Middleton Ward | First floor | 01-01-09-10 | 50 x 100 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill around conduits using an intumescent mastic. (2no) | IMG_0004 (Small).JPG | 4 | P2A
01-01-09-5 | Main Hospital - Middleton Ward | First floor | 01-01-09-10 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0005 (Small).JPG | 5 | P2A
01-01-09-6 | Main Hospital - Middleton Ward | First floor | 01-01-09-10 | 300 x 300 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around ductwork using an intumescent batt and intumescent mastic. | IMG_0006 (Small).JPG | 6 | P2A
01-01-09-7 | Main Hospital - Middleton Ward | First floor | 01-01-09-10 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0007 (Small).JPG | 7 | P2A
01-01-09-8 | Main Hospital - Middleton Ward | First floor | 01-01-09-55 | 10 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam and infill around conduit using an intumescent mastic. (2no) | IMG_0008 (Small).JPG | 8 | P2A
01-01-09-9 | Main Hospital - Middleton Ward | First floor | 01-01-09-55 | 20 x 100 20 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam and infill around conduits using an intumescent batt and intumescent mastic. | IMG_0009 (Small).JPG | 9 | P2A
01-01-09-10 | Main Hospital - Middleton Ward | First floor | 01-01-09-55 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent mastic. | IMG_0010 (Small).JPG | 10 | P2A
01-01-09-11 | Main Hospital - Middleton Ward | First floor | 01-01-09-32 |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Ensure the cavity barrier is structurally fixed to the suspended ceiling. | IMG_0011 (Small).JPG | 11 | P2A
01-01-09-12 | Main Hospital - Middleton Ward | First floor | 01-01-09-38 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent mastic. | IMG_0012 (Small).JPG | 12 | P2A
01-01-09-13 | Main Hospital - Middleton Ward | First floor | 01-01-09-35 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. (3no) | IMG_0013 (Small).JPG | 13 | P2A
01-01-09-14 | Main Hospital - Middleton Ward | First floor | 01-01-09-34 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0014 (Small).JPG | 14 | P2A
01-01-09-15 | Main Hospital - Wittering Ward | First floor | 01-01-09-03 |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Ensure the cavity barrier is structurally fixed to the suspended ceiling. | IMG_0015 (Small).JPG | 15 | P2A
01-01-07-1 | Main Hospital - Chichester Suite | First floor | 01-01-07-01 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits and opening using an intumescent mastic. (3no) | IMG_0016 (Small).JPG | 16 | P2A
01-01-07-2 | Main Hospital - Chichester Suite | First floor | 01-01-07-02 | 100 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0017 (Small).JPG | 17 | P2A
01-01-07-3 | Main Hospital - Chichester Suite | First floor | 01-01-07-02 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent mastic. | IMG_0018 (Small).JPG | 18 | P2A
01-01-07-4 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the openings using an intumescent mastic. (2no) | IMG_0019 (Small).JPG | 19 | P2A
01-01-07-5 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 100 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent batt and intumescent mastic. | IMG_0020 (Small).JPG | 20 | P2A
01-01-07-6 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 10 x 70 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0021 (Small).JPG | 21 | P2A
01-01-07-7 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0022 (Small).JPG | 22 | P2A
01-01-07-8 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0023 (Small).JPG | 23 | P2A
01-01-07-9 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0024 (Small).JPG | 24 | P2A
01-01-07-10 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0025 (Small).JPG | 25 | P2A
01-01-07-11 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0026 (Small).JPG | 26 | P2A
01-01-07-12 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0027 (Small).JPG | 27 | P2A
01-01-07-13 | Main Hospital - Chichester Suite | First floor | 01-01-07-11 | 70 x 800 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Install intumescent batt around the opening structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0028 (Small).JPG | 28 | P2A
01-01-07-14 | Main Hospital - Chichester Suite | First floor | 01-01-07-67 | 300 x 400 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0029 (Small).JPG | 29 | P2A
01-01-07-15 | Main Hospital - Chichester Suite | First floor | 01-01-07-67 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0030 (Small).JPG | 30 | P2A
01-01-07-16 | Main Hospital - Chichester Suite | First floor | 01-01-07-17 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0031 (Small).JPG | 31 | P2A
01-01-07-17 | Main Hospital - Chichester Suite | First floor | 01-01-07-51 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (3no) | IMG_0032 (Small).JPG | 32 | P2A
01-01-07-18 | Main Hospital - Chichester Suite | First floor | 01-01-07-38 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0033 (Small).JPG | 33 | P2A
01-01-09-16 | Main Hospital - Middleton Ward Lobby | First floor | 01-01-09-43 |  | Pipes were observed passing through the indicated compartmentation. Provide and fit new suitable fire pipe collar to the pipe where it passes through the compartmentation. | Provide uPVC pipes with pipe collars to FR 60. (2no) | IMG_0034 (Small).JPG | 34 | P2A
01-01-09-17 | Main Hospital - Middleton Ward Lobby | First floor | 01-01-09-43 | 600 x 600 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the soffit. Install 60 minute fire resisting fireboard structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0035 (Small).JPG | 35 | P2A
01-01-01-1 | Main Hospital - Birdham Ward | First floor | 01-01-01-01 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0036 (Small).JPG | 36 | P2A
01-01-01-2 | Main Hospital - Birdham Ward | First floor | 01-01-01-11 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0037 (Small).JPG | 37 | P2A
01-01-01-3 | Main Hospital - Birdham Ward | First floor | 01-01-01-11 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent batt and intumescent mastic. | IMG_0038 (Small).JPG | 38 | P2A
01-01-01-4 | Main Hospital - Birdham Ward | First floor | 01-01-01-11 | 10 D 50 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated foam and infill the opening using an intumescent mastic. | IMG_0039 (Small).JPG | 39 | P2A
01-01-01-5 | Main Hospital - Fishbourne Ward | First floor | 01-01-01-12 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. (2no) | IMG_0040 (Small).JPG | 40 | P2A
01-01-01-6 | Main Hospital - Fishbourne Ward | First floor | 01-01-01-12 | 10 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable trays using an intumescent mastic. (2no) | IMG_0041 (Small).JPG | 41 | P2A
01-01-01-7 | Main Hospital - Birdham Ward | First floor | 01-01-01-11 |  | The indicated fire door is not fully self closing into the frame. Ease and adjust door self closer to enable door to close in the event of fire. |  | IMG_0042 (Small).JPG | 42 | P2A
01-01-01-8 | Main Hospital - Birdham Ward | First floor | 01-01-01-63 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. (2no) | IMG_0043 (Small).JPG | 43 | P2A
01-01-01-9 | Main Hospital - Birdham Ward | First floor | 01-01-01-63 | 100 x 500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable trays and conduit using an intumescent batt and intumescent mastic. Remove non rated foam and infill the opening using an intumescent mastic. | IMG_0044 (Small).JPG | 44 | P2A
01-01-01-10 | Main Hospital - Birdham Ward | First floor | 01-01-01-63 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0045 (Small).JPG | 45 | P2A
01-01-01-11 | Main Hospital - Birdham Ward | First floor | 01-01-01-33 |  | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Ensure the cavity barrier is structurally fixed to the suspended ceiling. | IMG_0046 (Small).JPG | 46 | P2A
01-01-01-12 | Main Hospital - Birdham Ward | First floor | 01-01-01-40 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent batt and intumescent mastic. (2no) | IMG_0047 (Small).JPG | 47 | P2A
01-01-01-13 | Main Hospital - Birdham Ward | First floor | 01-01-01-40 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. (3no) | IMG_0048 (Small).JPG | 48 | P2A
01-01-01-14 | Main Hospital - Birdham Ward | First floor | 01-01-01-40 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent batt and intumescent mastic. | IMG_0049 (Small).JPG | 49 | P2A
01-01-01-15 | Main Hospital - Birdham Ward | First floor | 01-01-01-40 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0050 (Small).JPG | 50 | P2A
01-01-01-16 | Main Hospital - Birdham Ward | First floor | 01-01-01-33 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0051 (Small).JPG | 51 | P2A
01-01-01-17 | Main Hospital - Birdham Ward | First floor | 01-01-01-36 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0052 (Small).JPG | 52 | P2A
01-01-01-18 | Main Hospital - Birdham Ward | First floor | 01-01-01-35 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0053 (Small).JPG | 53 | P2A
01-01-01-19 | Main Hospital - Birdham Ward | First floor | 01-01-01-35 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0054 (Small).JPG | 54 | P2A
01-01-01-20 | Main Hospital - Fishbourne Ward | First floor | 01-01-01-03 |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Ensure the cavity barrier is structurally fixed to the suspended ceiling. | IMG_0055 (Small).JPG | 55 | P2A
01-01-01-21 | Main Hospital - Birdham Ward | First floor | 01-01-01-23 | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0056 (Small).JPG | 56 | P2A
01-01-01-22 | Main Hospital - Birdham Ward | First floor | 01-01-01-23 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0057 (Small).JPG | 57 | P2A
HS8-1 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0001 (Small).JPG | 1 | P2A
HS8-2 | Hospital Street 8 | First Floor |  |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0002 (Small).JPG | 2 | P2A
HS8-3 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables and conduit using an intumescent mastic. (2no) | IMG_0003 (Small).JPG | 3 | P2A
HS8-4 | Hospital Street 8 | First Floor |  | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0004 (Small).JPG | 4 | P2A
HS8-5 | Hospital Street 8 | First Floor |  | 20 D, 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0005 (Small).JPG | 5 | P2A
HS8-6 | Hospital Street 8 | First Floor |  |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0006 (Small).JPG | 6 | P2A
HS8-7 | Hospital Street 8 | First Floor |  | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0007 (Small).JPG | 7 | P2A
HS8-8 | Hospital Street 8 | First Floor |  | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent mastic. (2no) | IMG_0008 (Small).JPG | 8 | P2A
HS8-9 | Hospital Street 8 | First Floor |  | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0009 (Small).JPG | 9 | P2A
HS8-10 | Hospital Street 8 | First Floor |  | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0010 (Small).JPG | 10 | P2A
HS8-11 | Hospital Street 8 | First Floor |  | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0011 (Small).JPG | 11 | P2A
HS8-12 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill inside conduits using an intumescent mastic. (2no) | IMG_0012 (Small).JPG | 12 | P2A
HS8-13 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0013 (Small).JPG | 13 | P2A
HS8-14 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0014 (Small).JPG | 14 | P2A
HS8-15 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0015 (Small).JPG | 15 | P2A
HS8-16 | Hospital Street 8 | First Floor |  | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0016 (Small).JPG | 16 | P2A
HS8-17 | Hospital Street 8 | First Floor |  | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0017 (Small).JPG | 17 | P2A
HS8-18 | Hospital Street 8 | First Floor |  | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0018 (Small).JPG | 18 | P2A
HS8-19 | Hospital Street 8 | First Floor |  | 20 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around cables using an intumescent mastic. | IMG_0019 (Small).JPG | 19 | P2A
HS8-20 | Hospital Street 8 | First Floor |  | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0020 (Small).JPG | 20 | P2A

## Worthing P2s
Drawing Reference | Building | Level | Room | Hole size (mm) | Remedial Actions | Specific details | Priority
S1-1-1 | East Wing | First Floor | 1/S/1a | 300 D | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S1-1-2 | East Wing | First Floor | 1/S/1a | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. | P2
S2-1-1 | East Wing | First Floor | 1/S/1 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening and opening around cable using an intumescent mastic. (2no) | P2
S2-1-2 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Cut out the existing non-fire resistant foam at high level around the cable. Infill the opening using an instumescent batt and intumescent mastic. Infill around and inside the pipe with an intumescent mastic. | P2
S2-1-3 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S2-1-4 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Cut out the existing non-fire resistant foam at high level and around the cable. Infill the opening using an instumescent batt and intumescent mastic. Infill around and inside the pipe with an intumescent mastic. | P2
S2-1-5 | East Wing | First Floor | 1/S/2 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S2-1-6 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around and inside conduit using an intumescent mastic. | P2
S2-1-7 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S2-1-8 | East Wing | First Floor | 1/S/2 | 500 x 1500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S2-1-9 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around cables using an instumescent mastic. | P2
S2-1-10 | East Wing | First Floor | 1/S/2 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around pipes using an instumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S2-1-11 | East Wing | First Floor | 1/S/2 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the wall using an intumescent batt and intumescent mastic. Infill opening around cables using an intumescent mastic. | P2
S2-1-12 | East Wing | First Floor | 1/S/2 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S2-1-13 | East Wing | First Floor | 1/S/2 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | P2
S4-1-1 | East Wing | First Floor | 1/S/4 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | P2
S4-1-2 | East Wing | First Floor | 1/S/4 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill inside conduit and around cable using an intumescent mastic. (2no) | P2
S4-1-3 | East Wing | First Floor | 1/S/4 | 100 x 150 | Opening was observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using a new sutiably supported intumescent batt and intumescent mastic. | P2
S4-1-4 | East Wing | First Floor | 1/S/4 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening above cable tray using an intumescent batt and intumescent mastic. | P2
S4-1-5 | East Wing | First Floor | 1/S/4 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing self closing device and ensure positive self closure into the frame. |  | P2
S4-1-6 | East Wing | First Floor | 1/S/4 | 10 D, 20 D, 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening and inside conduit using an intumescent batt and intumescent mastic. (3no) | P2
S4-1-7 | East Wing | First Floor | 1/S/4 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S4-1-8 | East Wing | First Floor | 1/S/4 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the wall using an intumescent batt and intumescent mastic. Infill openings around pipes using an intumescent mastic. | P2
S4-1-9 | East Wing | First Floor | 1/S/4 | 100 x 1500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S4-1-10 | East Wing | First Floor | 1/S/4 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | P2
S4-1-11 | East Wing | First Floor | 1/S/4 | 10 D, 20 D, 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe usinbg an intumescent batt and intumescent mastic Infill around pipe and cables using an intumescent mastic. (4no) | P2
S4-1-12 | East Wing | First Floor | 1/S/4 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the wall using an intumescent batt and intumescent mastic. Infill opening around pipes using an intumescent mastic. | P2
S5-1-1 | East Wing | First Floor | 1/S/5 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent batt and intumescent mastic. | P2
S5-1-2 | East Wing | First Floor | 1/S/5 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
S6-1-1 | East Wing | First Floor | 1/S/6 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the wall using an intumescent batt and intumescent mastic. Infill opening around pipe using an intumescent mastic. | P2
S7-1-1 | East Wing | First Floor | 1/S/7 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S7-1-2 | East Wing | First Floor | 1/S/7 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S6-1-2 | East Wing | First Floor | 1/S/6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. (2no) | P2
S6-1-3 | East Wing | First Floor | 1/S/6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S6-1-4 | East Wing | First Floor | 1/S/6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill around conduit using an intumescent mastic. | P2
S6-1-5 | East Wing | First Floor | 1/S/6 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around pipe using an intumescent mastic. | P2
S6-1-6 | East Wing | First Floor | 1/S/6 | 40 D, 150 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent batt and intumescent mastic. (2no) | P2
S6-1-7 | East Wing | First Floor | 1/S/6 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around pipe using an intumescent mastic. | P2
S6-1-8 | East Wing | First Floor | 1/S/6 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around pipes using an intumescent mastic. (3no) | P2
S6-1-9 | East Wing | First Floor | 1/S/6 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S6-1-10 | East Wing | First Floor | 1/S/6 | 150 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S6-1-11 | East Wing | First Floor | 1/S/6 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent mastic. (3no) | P2
S6-1-12 | East Wing | First Floor | 1/S/6 | 100 x 500 | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around cables using an instumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S6-1-13 | East Wing | First Floor | 1/S/6 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing self closing device and ensure positive self closure into the frame. |  | P2
S6-1-14 | East Wing | First Floor | 1/S/6 | 150 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S6-1-15 | East Wing | First Floor | 1/S/6 | 10 D, 10 x 70 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable and cables tray using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S6-1-16 | East Wing | First Floor | 1/S/6 | 50 D | Openings were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill openings using an intumescent mastic. (2no) | P2
S6-1-17 | East Wing | First Floor | 1/S/6 |  | Provide and fit new magnetic hold open device connected to the existing fire alarm system. Ensure that the door is held open on the hold open device and when the fire alarm operates the door fully self closes into the frame. | The magnetic hold device does not release upon activating the release button. | P2
S6-1-18 | East Wing | First Floor | 1/S/6 | 150 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove existing non-fire resisitng foam and Infill along the head of the wall using an intumescent mastic. Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S6-1-19 | East Wing | First Floor | 1/S/6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S6-1-20 | East Wing | First Floor | 1/S/6 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S6-1-21 | East Wing | First Floor | 1/S/6 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
C1-1-1 | East Wing | First Floor | 1/E/66 | 100 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the cable tray using an intumescent batt and intumescent mastic. | P2
C1-1-2 | East Wing | First Floor | 1/E/66 | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent batt and intumescent mastic. | P2
C1-1-3 | East Wing | First Floor | 1/E/66 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cable trays using an intumescent batt and intumescent mastic. | P2
C1-1-4 | East Wing | First Floor | 1/E/66 | 30 D, 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the openings using an intumescent mastic. (2no) | P2
C1-1-5 | East Wing | First Floor | 1/E/66 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
C1-1-6 | East Wing | First Floor | 1/E/66 | 100 x 350 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
C1-1-7 | East Wing | First Floor | 1/E/66 | 30 x 60 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Close conduit lid and Infill opening around cable tray and conduit using an intumescent mastic. (2no) | P2
C1-1-8 | East Wing | First Floor | 1/E/66 | 20 x 20, 40 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent batt and intumescent mastic. (2no) | P2
C1-1-9 | East Wing | First Floor | 1/E/66 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
C1-1-10 | East Wing | First Floor | 1/E/66 | 30 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (8no) | P2
C1-1-11 | East Wing | First Floor | 1/E/66 | 30 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
C1-1-12 | East Wing | First Floor | 1/E/66 | 70 D, 150 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill openings using an intumescent batt and intumescent mastic. (2no) | P2
C1-1-13 | East Wing | First Floor | 1/E/66 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
C1-1-14 | East Wing | First Floor | 1/E/66 | 150 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around cables using an intumescent batt and intumescent mastic. | P2
C1-1-15 | East Wing | First Floor | 1/E/66 | Small | Damage was observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
C1-1-16 | East Wing | First Floor | 1/E/66 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
C1-1-17 | East Wing | First Floor | 1/E/66 | 300 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove insulation and infill the opening using an intumescent batt and intumescent mastic. | P2
C1-1-18 | East Wing | First Floor | 1/E/66 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. | P2
S11-1-1 | East Wing | First Floor | 1/E/66 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
46-01-01-1 | Beacon/Barrow | First Floor | 1/J/02 | Small | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable trays using an intumescent mastic. (2no) | P2
46-01-01-2 | Beacon/Barrow | First Floor | 1/J/02 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
46-01-01-3 | Beacon/Barrow | First Floor | 1/J/03 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent mastic (3no). Provide uPVC pipe with a pipe collar. | P2
06-01-07-1 | Bramber/Gynae Day Unit | First Floor | 1/E/67 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
S9-1-1 | East Wing | First Floor | 1/S/9 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S9-1-2 | East Wing | First Floor | 1/S/9 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openingaround pipe using an intumescent mastic. | P2
S9-1-3 | East Wing | First Floor | 1/S/9 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S9-1-4 | East Wing | First Floor | 1/S/9 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. (2no) | P2
S1-2-1 | East Wing | Second Floor | 2/S/1 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S2-2-1 | East Wing | Second Floor | 2/S/1 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | P2
S2-2-2 | East Wing | Second Floor | 2F West | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S2-2-3 | East Wing | Second Floor | 2A West | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
S2-2-4 | East Wing | Second Floor | 2/A/01 |  | The intumescent / intumescent backed cold smoke seals to the indicated fire door are defective. Replace the existing seals with new intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing intumescent smoke seal and dispose. (b) Remove existing fire door from its frame. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S2-2-5 | East Wing | Second Floor | 2/A/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around and inside plastic conduit using an intumescent mastic. (2no) | P2
S2-2-6 | East Wing | Second Floor | 2/A/02 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
S2-2-7 | East Wing | Second Floor | 2/F/01 | 100 x 150 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated insulation and infill opening cable tray using an intumescent batt and intumescent mastic. | P2
S2-2-8 | East Wing | Second Floor | 2/F/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around and inside plastic conduit using an intumescent mastic. | P2
S2-2-9 | East Wing | Second Floor | 2F East | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
S2-2-10 | East Wing | Second Floor | 2S Electric Riser | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S2-2-11 | East Wing | Second Floor | 2S Electric Riser | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
S2-2-12 | East Wing | Second Floor | 2S Electric Riser | 100 x 1500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the cable tray using an intumescent batt and intumescent mastic. | P2
S2-2-13 | East Wing | Second Floor | 2S Electric Riser | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening in floor using an intumescent batt and intumescent mastic. | P2
S2-2-14 | East Wing | Second Floor | 2S Electric Riser | 40 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
S2-2-15 | East Wing | Second Floor | 2S Electric Riser | 40 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill opening around conduit using an intumescent batt and intumescent mastic. | P2
S2-2-16 | East Wing | Second Floor | 2/S/2 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S4-2-1 | East Wing | Second Floor | 2B West |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S4-2-2 | East Wing | Second Floor | 2B West |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S4-2-3 | East Wing | Second Floor | 2B West | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around and inside plastic conduit using an intumescent mastic. | P2
S4-2-4 | East Wing | Second Floor | 2/E/01 | 70 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
S4-2-5 | East Wing | Second Floor | 2B East | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam at high level and infill opening using an intumescent batt and intumescent mastic. Infill opening around cables using an intumescent mastic. | P2
S4-2-6 | East Wing | Second Floor | Electric Riser | 100 x 1500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the cable tray using an intumescent batt and intumescent mastic. | P2
S4-2-7 | East Wing | Second Floor | Electric Riser | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove insulation and infill the opening using an intumescent batt and intumescent mastic. | P2
S4-2-8 | East Wing | Second Floor | 2E East | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S4-2-9 | East Wing | Second Floor | 2/S/4 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent batt and intumescent mastic. | P2
S5-2-1 | East Wing | Second Floor | 2/S/5A | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S6-2-1 | East Wing | Second Floor | 2/S/7 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
S6-2-2 | East Wing | Second Floor | 2/S/7 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S7-2-1 | East Wing | Second Floor | 2/S/7 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S7-2-2 | East Wing | Second Floor | 2/S/7 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S7-2-3 | East Wing | Second Floor | 2/S/6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam at high level and infill opening using an intumescent batt and intumescent mastic. Infill around cable using an intumescent mastic. | P2
S7-2-4 | East Wing | Second Floor | 2/S/6 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam at high level and infill opening using an intumescent batt and intumescent mastic. Infill around cable using an intumescent mastic. | P2
S6-2-3 | East Wing | Second Floor | Mechanic Riser | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. (2no) | P2
C1-2-1 | East Wing | Second Floor | 2/E/62a | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
C1-2-2 | East Wing | Second Floor | 2/E/62 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
C1-2-3 | East Wing | Second Floor | 2/E/62 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
C1-2-4 | East Wing | Second Floor | 2/E/62 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cables using an intumescent mastic. (2no) | P2
C1-2-5 | East Wing | Second Floor | 2/E/62 | 40 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. Remove non-fire rated foam and infill opening using an intumescent batt and intumescent mastic. | P2
C1-2-6 | East Wing | Second Floor | 2/E/62 | 10 D, 20 D, 40 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside and around conduits using an intumescent mastic (2no). Infill the opening using an intumescent batt and intumescent mastic. | P2
S6-2-4 | East Wing | Second Floor | 2/S/6 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S6-2-5 | East Wing | Second Floor | 2/S/6 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | P2
S6-2-6 | East Wing | Second Floor | 2/D South | 300 x 500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around the conduit using an intumescent batt and intumescent mastic. | P2
S6-2-7 | East Wing | Second Floor | Mechanic Riser | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S6-2-8 | East Wing | Second Floor | Mechanic Riser | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S6-2-9 | East Wing | Second Floor | Duct |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S6-2-10 | East Wing | Second Floor | Duct | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S6-2-11 | East Wing | Second Floor | Duct | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S6-2-12 | East Wing | Second Floor | 2/S/8 |  | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. |  | P2
S6-2-13 | East Wing | Second Floor | 2/D/07 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S6-2-14 | East Wing | Second Floor | 2/S/8 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
S6-2-15 | East Wing | Second Floor | 2/S/8 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S6-2-16 | East Wing | Second Floor | 2/S/8 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam at high level and infill opening using an intumescent batt and intumescent mastic. Infill around and inside conduit using an intumescent mastic. | P2
S6-2-17 | East Wing | Second Floor | 2/S/8 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S9-2-1 | East Wing | Second Floor | 2/S/9 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S9-2-2 | East Wing | Second Floor | 2/S/9 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
S9-2-3 | East Wing | Second Floor | 2/S/9 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
S9-2-4 | East Wing | Second Floor | 2/S/9 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S9-2-5 | East Wing | Second Floor | 2/S/9 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes with an intumescent batt and intumescent mastic. Infill inside conduit using an intumescent mastic. | P2
S9-2-6 | East Wing | Second Floor | 2/C/01 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
S9-2-7 | East Wing | Second Floor | 2C North |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
S9-2-8 | East Wing | Second Floor | 2C North | 20 x across room perimeter | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill around cables and head of board using an intumescent batt and intumescent mastic. | P2
S9-2-9 | East Wing | Second Floor | 2/B/51 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
S9-2-10 | East Wing | Second Floor | 2/B/51 | 10 D, 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables and pipe using an intumescent mastic (2no). | P2
S9-2-11 | East Wing | Second Floor | 2/C/10 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. | The indicated door was found to have an excessive gap. Ease and adjust the existing fire door to reduce excessive gap between door leaves to a maximum of 3mm to ensure correct functionality. | P2
S9-2-12 | East Wing | Second Floor | 2/S/9 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables and opening using an intumescent mastic (2no). | P2
S9-2-13 | East Wing | Second Floor | 2/S/9 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
S10-2-1 | East Wing | Second Floor | Stair 3 |  | The indicated doorset is not fully self closing into the frame. Ease and adjust the existing self closing device and ensure positive self closure into the frame. |  | P2
S10-2-2 | East Wing | Second Floor | Stair 3 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-01-1 | Bluefin Ward | First Floor | 1/A/02 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-2 | Bluefin Ward | First Floor | 1/A/01 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-01-3 | Bluefin Ward | First Floor | 1/A/01 | 500 x 500 | The construction at high level was not present.Install a new intumescent batt and suitable support for the batt along the opening. Where cables or conduits pass through the new batt, ensure they are suitable back coated with intumescent mastic or similar to reinstate the integrity of the compartmentation. | Install intumescent batt structurally secured to existing construction elements. | P2
06-01-01-4 | Bluefin Ward | First Floor | 1/A/01 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-5 | Bluefin Ward | First Floor | 1/A/01 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening above cable tray using an intumescent batt and intumescent mastic. | P2
06-01-01-6 | Bluefin Ward | First Floor | 1/A/06 | 20 x 50 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic. (2no) | P2
06-01-01-7 | Bluefin Ward | First Floor | 1/A/72 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening using an intumescent batt and intumescent mastic. | P2
06-01-01-8 | Bluefin Ward | First Floor | 1/A/72 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. (2no) | P2
06-01-01-9 | Bluefin Ward | First Floor | 1/A/06 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-10 | Bluefin Ward | First Floor | 1/A/06 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent masticc. | P2
06-01-01-11 | Bluefin Ward | First Floor | 1/A/10 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic | P2
06-01-01-12 | Bluefin Ward | First Floor | 1/A/07 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic | P2
06-01-01-13 | Bluefin Ward | First Floor | 1/A/19 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-01-14 | Bluefin Ward | First Floor | 1/A/19 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-01-15 | Bluefin Ward | First Floor | 1/A/19 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside and openings around conduits using an intumescent mastic. (4no) | P2
06-01-01-16 | Bluefin Ward | First Floor | 1/A/19 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around cables using an intumescent mastic. | P2
06-01-01-17 | Bluefin Ward | First Floor | 1/A/19 | 10 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-18 | Bluefin Ward | First Floor | 1/A/19 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-19 | Bluefin Ward | First Floor | 1/A/19 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduits using an intumescent mastic. (3no) | P2
06-01-01-20 | Bluefin Ward | First Floor | 1/A/20 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove insulation and infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-01-21 | Bluefin Ward | First Floor | 1/A/20 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduits using an intumescent mastic. | P2
06-01-01-22 | Bluefin Ward | First Floor | 1/A/20a | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-01-23 | Bluefin Ward | First Floor | 1/A/20a | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent mastic. | P2
06-01-01-24 | Bluefin Ward | First Floor | 1/A/20a | 20 x 70 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-01-25 | Bluefin Ward | First Floor | 1/A/20 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-26 | Bluefin Ward | First Floor | 1/A/20 | 10 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduits and cable tray using an intumescent batt and intumescent mastic. (3no) | P2
06-01-01-27 | Bluefin Ward | First Floor | 1/A/20 | 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-01-01-28 | Bluefin Ward | First Floor | 1/A/20 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-29 | Bluefin Ward | First Floor | 1/A/20 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-30 | Bluefin Ward | First Floor | 1/A/20 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-31 | Bluefin Ward | First Floor | 1/A/20 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-32 | Bluefin Ward | First Floor | 1/A/69 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-33 | Bluefin Ward | First Floor | 1/A/48 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-01-34 | Bluefin Ward | First Floor | 1/A/48 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-35 | Bluefin Ward | First Floor | 1/A/48 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-36 | Bluefin Ward | First Floor | 1/A/34 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-37 | Bluefin Ward | First Floor | 1/A/34 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-38 | Bluefin Ward | First Floor | 1/A/34 |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around conduit using an intumescent mastic. | P2
06-01-01-39 | Bluefin Ward | First Floor | 1/A/34 |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cables using an intumescent mastic. | P2
06-01-01-40 | Bluefin Ward | First Floor | 1/A/34 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-01-41 | Bluefin Ward | First Floor | 1/A/32 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-01-42 | Bluefin Ward | First Floor | 1/A/35 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduits using an intumescent mastic. (2no) | P2
06-01-01-43 | Bluefin Ward | First Floor | 1/A/35 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-44 | Bluefin Ward | First Floor | 1/A/43 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-01-45 | Bluefin Ward | First Floor | 1/A/40 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-01-46 | Bluefin Ward | First Floor | 1/A/41B |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Remove non-fire rated foam and infill opening around cables using an intumescent mastic. | P2
06-01-07-2 | Bramber/Gynae Day Unit | First Floor | 1/E/64 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-3 | Bramber/Gynae Day Unit | First Floor | 1/E/07 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P2
06-01-07-4 | Bramber/Gynae Day Unit | First Floor | 1/E/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill insideand around conduit using an intumescent mastic. | P2
06-01-07-5 | Bramber/Gynae Day Unit | First Floor | 1/E/01 | 40 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening using an intumescent mastic. (2no) | P2
06-01-07-6 | Bramber/Gynae Day Unit | First Floor | 1/E/01 |  | The indicated fire door is not provided with intumescent backed cold smoke seals to the head of the door. Supply and install into the existing fire door, intumescent backed cold smoke seals to head of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-7 | Bramber/Gynae Day Unit | First Floor | 1/E/57 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-07-8 | Bramber/Gynae Day Unit | First Floor | 1/E/09 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-9 | Bramber/Gynae Day Unit | First Floor | 1/E/55 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-07-10 | Bramber/Gynae Day Unit | First Floor | 1/E/55 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-11 | Bramber/Gynae Day Unit | First Floor | 1/E/54a | 10 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-07-12 | Bramber/Gynae Day Unit | First Floor | 1/E/49 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-07-13 | Bramber/Gynae Day Unit | First Floor | 1/E/49 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-07-14 | Bramber/Gynae Day Unit | First Floor | 1/E/42 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-15 | Bramber/Gynae Day Unit | First Floor | 1/E/42 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. (2no) | P2
06-01-07-16 | Bramber/Gynae Day Unit | First Floor | 1/E/36 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-07-17 | Bramber/Gynae Day Unit | First Floor | 1/E/34 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-07-18 | Bramber/Gynae Day Unit | First Floor | 1/E/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-07-19 | Bramber/Gynae Day Unit | First Floor | 1/E/01 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-07-20 | Bramber/Gynae Day Unit | First Floor | 1/E/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-07-21 | Bramber/Gynae Day Unit | First Floor | 1/E/01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-07-22 | Bramber/Gynae Day Unit | First Floor | 1/E/01 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-23 | Bramber/Gynae Day Unit | First Floor | 1/E/13 |  | The existingfire door is being held open. If it is desired to keep the door open to allow easier movement of beds, then consider installing a magnetic hold on the door linked to the local fire alarm. |  | P2
06-01-07-24 | Bramber/Gynae Day Unit | First Floor | 1/E/18 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
06-01-07-25 | Bramber/Gynae Day Unit | First Floor | 1/E/18 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-26 | Bramber/Gynae Day Unit | First Floor | 1/E/26 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-07-27 | Bramber/Gynae Day Unit | First Floor | 1/E/74 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-07-28 | Bramber/Gynae Day Unit | First Floor | 1/E/74B | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-07-29 | Bramber/Gynae Day Unit | First Floor | 1/E/74B |  | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Remove non-fire rated insulation and infill the opening using an intumescent batt and intumescent mastic, secured structurally to existing construction elements. | P2
06-01-07-30 | Bramber/Gynae Day Unit | First Floor | 1/E/74B | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-07-31 | Bramber/Gynae Day Unit | First Floor | 1/E/74B | Small | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent mastic. | P2
06-01-07-32 | Bramber/Gynae Day Unit | First Floor | 1/E/74B | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
06-01-07-33 | Bramber/Gynae Day Unit | First Floor | 1/E/74B | 40 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening using an intumescent batt and intumescent mastic. | P2
06-01-07-34 | Bramber/Gynae Day Unit | First Floor | 1/E/74B |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-G-01-1 | Emergency Floor | Ground Floor | G-B-12 | 10 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-G-01-2 | Emergency Floor | Ground Floor | G-B-19 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-3 | Emergency Floor | Ground Floor | G-B-19 | Small | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-G-01-4 | Emergency Floor | Ground Floor | G-B-19 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around and inside conduits using an intumescent mastic. (2no) | P2
06-G-01-5 | Emergency Floor | Ground Floor | G-A-48 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-6 | Emergency Floor | Ground Floor | G-A-48 | 20 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent mastic. | P2
06-G-01-7 | Emergency Floor | Ground Floor | G-A-48 | 50 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-G-01-8 | Emergency Floor | Ground Floor | G-A-48 | 70 x 70 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside cable tray using an intumescent batt and intumescent mastic. Ensure the cables are sutiable backed coated with intumescent mastic | P2
06-G-01-9 | Emergency Floor | Ground Floor | G-A-48 | 20 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-10 | Emergency Floor | Ground Floor | G-A-45 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduit using an intumescent mastic. | P2
06-G-01-11 | Emergency Floor | Ground Floor | G-A-45 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduit using an intumescent mastic. | P2
06-G-01-12 | Emergency Floor | Ground Floor | G-A-45 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-G-01-13 | Emergency Floor | Ground Floor | G-A-45 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-G-01-14 | Emergency Floor | Ground Floor | G-A-46 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (3no) | P2
06-G-01-15 | Emergency Floor | Ground Floor | G-A-46 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-16 | Emergency Floor | Ground Floor | G-A-48 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-G-01-17 | Emergency Floor | Ground Floor | G-A-52 | 50 x 1000 | The construction at high level was not present. Install a new instumescent batt and sutiable support for the batt along the opening. Where cables or pipes pass through the new batt, ensure that they are suitable back coated with instumescent mastic. Infill opening using a suitable intumescent masctic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt between the two adjacent walls, structurally secured to existing construction elements. | P2
06-G-01-18 | Emergency Floor | Ground Floor | G-A-53 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-G-01-19 | Emergency Floor | Ground Floor | G-A-42 | 500 x 500 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the pipes using an intumescent batt and intumescent mastic. | P2
06-G-01-20 | Emergency Floor | Ground Floor | G-A-42 | 100 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
06-G-01-21 | Emergency Floor | Ground Floor | G-A-42 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
06-G-01-22 | Emergency Floor | Ground Floor | G-A-42 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
06-G-01-23 | Emergency Floor | Ground Floor | G-A-42 | 150 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-G-01-24 | Emergency Floor | Ground Floor | G-A-41 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
06-G-01-25 | Emergency Floor | Ground Floor | G-A-41 | 30 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Remove non-fire rated foam and infill opening above cable tray using an intumescent mastic. | P2
06-G-01-26 | Emergency Floor | Ground Floor | G-A-41 | 40 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-27 | Emergency Floor | Ground Floor | G-A-41 | 40 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around and inside cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-28 | Emergency Floor | Ground Floor | G-A-40 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside conduits using an intumescent mastic. (4no) | P2
06-G-01-29 | Emergency Floor | Ground Floor | G-A-41 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside conduit using an intumescent mastic. | P2
06-G-01-30 | Emergency Floor | Ground Floor | G-A-42 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-31 | Emergency Floor | Ground Floor | G-A-06 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduits using an intumescent mastic. (2no) | P2
06-G-01-32 | Emergency Floor | Ground Floor | G-A-06 | 200 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the pipe using a new intumescent batt and intumescent mastic. | P2
06-G-01-33 | Emergency Floor | Ground Floor | G-A-06 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduits using an intumescent mastic. (2no) | P2
06-G-01-34 | Emergency Floor | Ground Floor | G-A-06 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-G-01-35 | Emergency Floor | Ground Floor | G-A-12 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent mastic. | P2
06-G-01-36 | Emergency Floor | Ground Floor | G-A-16 | 20 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside and around conduits using an intumescent mastic. | P2
06-G-01-37 | Emergency Floor | Ground Floor | G-A-36 | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening using an intumescent mastic. | P2
06-G-01-38 | Emergency Floor | Ground Floor | G-A-28 | 100 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-G-01-39 | Emergency Floor | Ground Floor | G-A-29 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening inside and around cable tray using an intumescent mastic. | P2
06-G-01-40 | Emergency Floor | Ground Floor | G-A-07 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside the conduit using an intumescent mastic. | P2
06-G-01-41 | Emergency Floor | Ground Floor | G-A-07 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening using an intumescent mastic. | P2
06-G-01-42 | Emergency Floor | Ground Floor | G-A-07 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduit using an intumescent mastic. | P2
06-G-01-43 | Emergency Floor | Ground Floor | G-A-06 | 30 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent batt and intumescent mastic. | P2
06-G-01-44 | Emergency Floor | Ground Floor | G-A-55 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-G-01-45 | Emergency Floor | Ground Floor | G-A-55 | 50 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-G-01-46 | Emergency Floor | Ground Floor | G-A-55 | 50 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-G-01-47 | Emergency Floor | Ground Floor | G-A-56 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-G-01-48 | Emergency Floor | Ground Floor | G-A-05 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent mastic. (3no) | P2
06-G-01-49 | Emergency Floor | Ground Floor | G-A-64 | 1000 x 4000 | The construction at high level was not present. Install a new instumescent batt and sutiable support for the batt along the opening. Where cables or pipes pass through the new batt, ensure that they are suitable back coated with instumescent mastic. Infill opening using a suitable intumescent masctic or similar to provide a minimum 30 minute fire resistance. | Install an intumescent batt structurally secured to existing construction elements. | P2
06-01-02-1 | Botolphs | First Floor | 1-B-02 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-02-2 | Botolphs | First Floor | 1-B-04 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-02-3 | Botolphs | First Floor | 1-B-04 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-02-4 | Botolphs | First Floor | 1-B-04 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (2no) | P2
06-01-02-5 | Botolphs | First Floor | 1-B-06 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-02-6 | Botolphs | First Floor | 1-B-06 | 40 x 70 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-02-7 | Botolphs | First Floor | 1-B-06 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipe using an intumescent mastic. | P2
06-01-02-8 | Botolphs | First Floor | 1-B-07 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-02-9 | Botolphs | First Floor | 1-B-07 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-02-10 | Botolphs | First Floor | 1-B-07b | 30 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-02-11 | Botolphs | First Floor | 1-B-07b | 40 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-02-12 | Botolphs | First Floor | 1-B-07b | 1500 x 1500 | The construction at high level was not present. Install a new intumescent batt and sutiable support for the batt along the opening. Provide a minimum 30 minute fire resistance. | Infill the opening using a new intumescent batt and intumescent mastic structurally secured to existing construction elements. | P2
06-01-02-13 | Botolphs | First Floor | 1-B-08 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduit using an intumescent mastic. | P2
06-01-02-14 | Botolphs | First Floor | 1-B-08 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-02-15 | Botolphs | First Floor | 1-B-14 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-02-16 | Botolphs | First Floor | 1-B-14 | 70 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around conduit using an intumescent batt and intumescent mastic. | P2
06-01-02-17 | Botolphs | First Floor | 1-B-14 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-02-18 | Botolphs | First Floor | 1-B-22 | 100 x 500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside the cable tray using an intumescent batt and intumescent mastic. | P2
06-01-02-19 | Botolphs | First Floor | 1-B-22 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (3no) | P2
06-01-02-20 | Botolphs | First Floor | 1-B-22 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-02-21 | Botolphs | First Floor | 1-B-24 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-02-22 | Botolphs | First Floor | 1-B-24 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-02-23 | Botolphs | First Floor | 1-B-33 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduits using an intumescent mastic. (2no) | P2
06-01-02-24 | Botolphs | First Floor | 1-B-33 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-02-25 | Botolphs | First Floor | 1-B-08 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-02-26 | Botolphs | First Floor | 1-B-32 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (2no) | P2
06-01-02-27 | Botolphs | First Floor | 1-B-31a | 10 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-02-28 | Botolphs | First Floor | 1-B-20 | 50 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-02-29 | Botolphs | First Floor | 1-B-20 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around conduits using an intumescent mastic. (4no) | P2
06-01-02-30 | Botolphs | First Floor | 1-B-20 | 30 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent batt and intumescent mastic. | P2
06-01-02-31 | Botolphs | First Floor | 1-B-20 | 30 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent batt and intumescent mastic. | P2
06-01-02-32 | Botolphs | First Floor | 1-B-20 | 50 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. | P2
06-01-02-33 | Botolphs | First Floor | 1-B-20 | 20 x 20, 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. Infill around pipe using an intumescent batt and intumescent mastic. (2no) | P2
06-01-02-34 | Botolphs | First Floor | 1-B-20 | 100 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
06-01-02-35 | Botolphs | First Floor | 1-B-18 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-02-36 | Botolphs | First Floor | 1-B-21 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. (2no) | P2
06-01-02-37 | Botolphs | First Floor | 1-B-21 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent mastic. (2no) | P2
06-01-06-1 | Burlington | First Floor | 1-D-001 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around cables using an intumescent mastic. | P2
06-01-06-2 | Burlington | First Floor | 1-D-C01 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-06-3 | Burlington | First Floor | 1-D-030 | 50 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside cable tray using an intumescent batt and intumescent mastic. | P2
06-01-06-4 | Burlington | First Floor | 1-D-030 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Remove the damaged batt Infill the opening around and inside ductwork using an intumescent batt and intumescent mastic. | P2
06-01-06-5 | Burlington | First Floor | 1-D-033 | 20 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-06-6 | Burlington | First Floor | 1-D-033 | 20 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-06-7 | Burlington | First Floor | 1-D-033 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-06-8 | Burlington | First Floor | 1-D-036 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-06-9 | Burlington | First Floor | 1-D-039 | 50 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around and inside cable tray using an intumescent batt and intumescent mastic. | P2
06-01-06-10 | Burlington | First Floor | 1-D-C04 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around cables using an intumescent mastic. (4no) | P2
06-01-06-11 | Burlington | First Floor | 1-D-C04 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-06-12 | Becket | First Floor | 1-D-032 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-06-13 | Becket | First Floor | 1-D-032 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-06-14 | Becket | First Floor | 1-D-032 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around conduit using an intumescent mastic. | P2
06-01-06-15 | Becket | First Floor | 1-D-018a | 200 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around ductwork using an intumescent batt and intumescent mastic. | P2
06-01-06-16 | Becket | First Floor | 1-D-018a | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-06-17 | Becket | First Floor | 1-D-024 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
06-01-06-18 | Becket | First Floor | 1-D-015 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
06-01-06-19 | Becket | First Floor | 1-D-015 | 200 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around ductwork using an intumescent batt and intumescent mastic. | P2
06-01-06-20 | Becket | First Floor | 1-D-015 | 150 x 150 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around ductwork using an intumescent batt and intumescent mastic. | P2
46-01-01-4 | Beacon/Barrow | First Floor | 1-J-49 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill above cable tray using an intumescent batt and intumescent mastic. | P2
46-01-01-5 | Beacon/Barrow | First Floor | 1-J-49 | 10 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around pipes using an intumescent mastic. (2no) | P2
46-01-01-6 | Beacon/Barrow | First Floor | 1-J-48 | 10 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable using an intumescent mastic. | P2
46-01-01-7 | Beacon/Barrow | First Floor | 1-L-33 | 20 x 50 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
46-01-01-8 | Beacon/Barrow | First Floor | 1-L-33 | 300 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around the pipes using an intumescent batt and intumescent mastic. | P2
46-01-01-9 | Beacon/Barrow | First Floor | 1-L-33 | 20 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside and around conduit using an intumescent mastic. | P2
46-01-01-10 | Beacon/Barrow | First Floor | 1-L-33 | 10 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
46-01-01-11 | Beacon/Barrow | First Floor | 1-J-45 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill openings around pipe using an intumescent batt and intumescent mastic. | P2
46-01-01-12 | Beacon/Barrow | First Floor | 1-J-45 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
46-01-01-13 | Beacon/Barrow | First Floor | 1-J-45 | 100 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
46-01-01-14 | Beacon/Barrow | First Floor | 1-J-45 | 200 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
46-01-01-15 | Beacon/Barrow | First Floor | 1-J-34 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent mastic. | P2
46-01-01-16 | Beacon/Barrow | First Floor | 1-J-34 | 40 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
46-01-01-17 | Beacon/Barrow | First Floor | 1-J-34 | 40 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
46-01-01-18 | Beacon/Barrow | First Floor | 1-J-30 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
46-01-01-19 | Beacon/Barrow | First Floor | 1-J-30 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. (2no) | P2
46-01-01-20 | Beacon/Barrow | First Floor | 1-J-30 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
46-01-01-21 | Beacon/Barrow | First Floor | 1-J-27 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening above cable tray using an intumescent batt and intumescent mastic. | P2
46-01-01-22 | Beacon/Barrow | First Floor | 1-J-27 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill openings around cables tray using an intumescent mastic. (2no) | P2
46-01-01-23 | Beacon/Barrow | First Floor |  | 50 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around pipes using an intumescent batt and intumescent mastic. | P2
46-01-01-24 | Beacon/Barrow | First Floor |  | 50 x 500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
46-01-01-25 | Beacon/Barrow | First Floor |  | 50 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
46-01-01-26 | Beacon/Barrow | First Floor |  | 50 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cable tray using an intumescent mastic. | P2
46-01-01-27 | Beacon/Barrow | First Floor | 1-L-16 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
46-01-01-28 | Beacon/Barrow | First Floor | 1-L-16 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
46-01-01-29 | Beacon/Barrow | First Floor | 1-L-16 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. | P2
46-01-01-30 | Beacon/Barrow | First Floor |  | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill opening around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | P2
06-01-08-1 | Delivery Suite & Beeding | First Floor | 1/F/02 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-2 | Delivery Suite & Beeding | First Floor | 1/F/02 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-3 | Delivery Suite & Beeding | First Floor | 1/F/03 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-4 | Delivery Suite & Beeding | First Floor | 1/F/03 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-5 | Delivery Suite & Beeding | First Floor | 1/F/08 |  | The indicated door was found to have an opening where an old lock had been removed. Carry out repair to door to restore the fire integrity of door. Splice in new section of timber, glued and screwed to the door. |  | P2
06-01-08-6 | Delivery Suite & Beeding | First Floor | 1/F/76 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-7 | Delivery Suite & Beeding | First Floor | 1/F/76 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P2
06-01-08-8 | Delivery Suite & Beeding | First Floor | 1/F/76 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-9 | Delivery Suite & Beeding | First Floor | 1/F/75 | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
06-01-08-10 | Delivery Suite & Beeding | First Floor | 1/F/75 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Metal ventilation pipe work passes through compartment wall without damper. Install an intumescent damper to pipework. | P2
06-01-08-11 | Delivery Suite & Beeding | First Floor | 1/F/75 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-12 | Delivery Suite & Beeding | First Floor | 1/F/73 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-13 | Delivery Suite & Beeding | First Floor | 1/F/09 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-14 | Delivery Suite & Beeding | First Floor | 1/F/09 | 30 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent mastic. (3no) | P2
06-01-08-15 | Delivery Suite & Beeding | First Floor | 1/F/13 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-16 | Delivery Suite & Beeding | First Floor | 1/F/15 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-17 | Delivery Suite & Beeding | First Floor | 1/F/16 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-18 | Delivery Suite & Beeding | First Floor | 1/F/01 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
06-01-08-19 | Delivery Suite & Beeding | First Floor | 1/F/17 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-20 | Delivery Suite & Beeding | First Floor | 1/F/01 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
06-01-08-21 | Delivery Suite & Beeding | First Floor | 1/F/100 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Cut-out non-fire rated foam and infill opening using an intumescent batt and intumescent mastic Infill opening around cable using an intumescent mastic. | P2
06-01-08-22 | Delivery Suite & Beeding | First Floor | 1/F/100 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-23 | Delivery Suite & Beeding | First Floor | 1/F/57 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-24 | Delivery Suite & Beeding | First Floor | 1/F/56 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-25 | Delivery Suite & Beeding | First Floor | 1/F/60 | 50 x 100 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable tray using an intumescent batt and intumescent mastic. | P2
06-01-08-26 | Delivery Suite & Beeding | First Floor | 1/F/24 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-27 | Delivery Suite & Beeding | First Floor | 1/F/24 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
06-01-08-28 | Delivery Suite & Beeding | First Floor | 1/F/24 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
06-01-08-29 | Delivery Suite & Beeding | First Floor | 1/F/26 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-30 | Delivery Suite & Beeding | First Floor | 1/F/26 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P2
06-01-08-31 | Delivery Suite & Beeding | First Floor | 1/F/33 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
06-01-08-32 | Delivery Suite & Beeding | First Floor | 1/F/33 | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
06-01-08-33 | Delivery Suite & Beeding | First Floor | 1/F/42 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-1 | Broadwater | First Floor | 1.42 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-2 | Broadwater | First Floor | 1.42 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-01-3 | Broadwater | First Floor | 1.42 | 200 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. Where cables pass through the new batt, ensure the openings are infilled using a sutiable intumescent mastic or similar. | P2
02-01-01-4 | Broadwater | First Floor | 1.42 | 40 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P2
02-01-01-5 | Broadwater | First Floor | 1.45B |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-6 | Broadwater | First Floor | 1.46 | Small | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-01-7 | Broadwater | First Floor | 1.46 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-8 | Broadwater | First Floor | 1.48 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-9 | Broadwater | First Floor | 1.48 |  | The indicated fire door is provided with a non-fire rated air grille. Remove the existing air grille and provide and fit new sealmaster fire door ventilator VH60/FS (or equivalent) providing intumescent fire and smoke control for up to one hour interfaced into and activated by the fire detection system. New sealmaster fire door ventilator VH60/FS to be suitably measured for existing opening. Pack out around opening new fire door ventilator using suitable fire resistant material and intumescent mastic. |  | P2
02-01-01-10 | Broadwater | First Floor | 1.49 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-11 | Broadwater | First Floor | 1.49 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-01-12 | Broadwater | First Floor | 1.51 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (2no) | P2
02-01-01-13 | Broadwater | First Floor | 1.51 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-01-14 | Broadwater | First Floor | 1.C8B | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-01-15 | Broadwater | First Floor | 1.C8B | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around cables using an intumescent mastic. | P2
02-01-01-16 | Broadwater | First Floor | 1.C8B | 20 D | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening around cables using an intumescent mastic. | P2
02-01-01-17 | Broadwater | First Floor | 1.66 | 50 x 50 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around pipe using an intumescent batt and intumescent mastic. | P2
02-01-01-18 | Broadwater | First Floor | 1.66 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-04-1 | Brooklands | First Floor | 1.67b |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-04-2 | Brooklands | First Floor | 1.67b |  | The construction at high level was not present. Install a new fire rated board (30minute FR) suitably fixed to the existing structure. Where cables or conduits pass through the new fire board, ensure that they are suitably infilled using an instumescent mastic. Infill openings using a sutiable instumescent mastic or similar to provide a minimum 30 minutes fire resistance. |  | P2
02-01-04-3 | Brooklands | First Floor | 1.67b |  | The construction at high level was not present. Install a new fire rated board (30minute FR) suitably fixed to the existing structure. Where cables or conduits pass through the new fire board, ensure that they are suitably infilled using an instumescent mastic. Infill openings using a sutiable instumescent mastic or similar to provide a minimum 30 minutes fire resistance. |  | P2
02-01-04-4 | Brooklands | First Floor | 1.67b | 50 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening around pipes using an intumescent batt and intumescent mastic. | P2
02-01-04-5 | Brooklands | First Floor | 1.68C |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | P2
02-01-04-6 | Brooklands | First Floor | 1.69a | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduits using an intumescent mastic. (2no) | P2
02-01-04-7 | Brooklands | First Floor | 1.69a | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-04-8 | Brooklands | First Floor | 1.69a | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
02-01-04-9 | Brooklands | First Floor | 1.69a | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-04-10 | Brooklands | First Floor | 1.69a | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-04-11 | Brooklands | First Floor | 1.69b | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
02-01-04-12 | Brooklands | First Floor | 1.69b | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-04-13 | Brooklands | First Floor | 1.69b | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
02-01-04-14 | Brooklands | First Floor | 1.69c | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (2no) | P2
02-01-04-15 | Brooklands | First Floor | 1.69c | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-04-16 | Brooklands | First Floor | 1.70b | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
02-01-04-17 | Brooklands | First Floor | 1.70b | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-04-18 | Brooklands | First Floor | 1.70b | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-04-19 | Brooklands | First Floor | 1.70b | 50 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
02-01-04-20 | Brooklands | First Floor | Duct 21 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill openings around cables using an intumescent mastic. (4no) | P2
02-01-04-21 | Brooklands | First Floor | Duct 21 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-04-22 | Brooklands | First Floor | 1.70C | 40 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-03-1 | Buckingham | First Floor | Electrics | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill around and inside conduits using an intumescent mastic. (2no) | P2
02-01-03-2 | Buckingham | First Floor | 1.C7B | 10 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-03-3 | Buckingham | First Floor | 1.72 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. | Ensure intumescent cold seals/strips are replaced either on the door or door frame. | P2
02-01-03-4 | Buckingham | First Floor | 1.72 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around cables using an intumescent mastic. | P2
02-01-03-5 | Buckingham | First Floor | 1.73 | 300 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic, structurally supported to existing construction elements. | P2
02-01-03-6 | Buckingham | First Floor | 1.90 | 20 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | P2
02-01-03-7 | Buckingham | First Floor | 1.76 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. |  | P2
02-01-03-8 | Buckingham | First Floor | 1.76 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill around and inside conduit using an intumescent mastic. | P2
02-01-03-9 | Buckingham | First Floor | 1.79 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. | Ensure intumescent cold seals/strips are replaced either on the door or door frame. | P2
02-01-03-10 | Buckingham | First Floor | 1.91 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. |  | P2
02-01-03-11 | Buckingham | First Floor | 1.92 |  | The inspection found that the glazing present at the indicated location was not provided with suitable indication of being fire resistant in nature. Confirm if the glazing is fire resistant in nature, and if the glass is not confirmed as being fire resistant then remove the existing glazing and supply and install new 30 minute fire resisting glazing (in accordance with BS 476). Ensure that glazing is suitably provided with intumescent gaskets and fixed beading at suitable centres. |  | P2
02-01-03-12 | Buckingham | First Floor | 1.92 | 10 x 1000 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent batt and intumescent mastic. | P2
02-01-03-13 | Buckingham | First Floor | 1.80 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
02-01-03-14 | Buckingham | First Floor | 1.80 | 20 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around cable using an intumescent mastic. | P2
02-01-03-15 | Buckingham | First Floor | 1.94 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P2
02-01-03-16 | Buckingham | First Floor | 1.94 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around conduit using an intumescent mastic. | P2
02-01-03-17 | Buckingham | First Floor | 1.94 | 30 D | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476 | Infill opening around pipes using an intumescent mastic. (3no) | P2
02-01-03-18 | Buckingham | First Floor | 1.94 | 50 x 50 | Penetrations were observed at the indicated location. Ensure that the openings and penetrations are suitably fire stopped with suitable fire resistant materials. Make good the penetration and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476 | Infill opening around pipe using an intumescent batt and intumescent mastic. | P2
19-3-1 | Horton Court Flats 7 to 12 | Second Floor | Attic | 10d 30d | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill holes around cables with an intumescent mastic (2No) | P2
19-4-1 | Horton Court Flats 13 to 18 | Second Floor | Attic | 10d | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill in and around the conduit with an intumescent mastic. | P2
19-4-2 | Horton Court Flats 13 to 18 | Second Floor | Attic | 10d | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill in and around the conduit with an intumescent mastic. | P2
19-2-1 | Horton Court Flats 1 to 6 | Second Floor | Attic | 10d | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill around the cables with an intumescent mastic. (2No) | P2