## App A - Schedule of Work
Appendix A
MCA - SCHEDULE OF WORKS
Site Address: |  | HM Coastguard National Maritime Operations Centre, Unit 12 Kites Croft Business Park.
Fareham, Hants. PO14 4LW
Project Type: |  | Consolidation of Generator Fuel Supplies
Tenderers for the above contract should complete the tables below, indicating what they would charge for each required element. Prices must: • Be stated in Pounds Sterling; • Include all other charges and overheads associated with the element being priced.
|  | General Works, Site Conditions and Prelims: | Tender: £ | Tenderer Comments
Notes
** | Existing fuel systems are to be reviewed to ensure adequate knowledge is available to undertake the redesign appropriate to the desired outcome. |  | 0
** | Works are to be planned and undertaken to maintain the operation of at least one generator to ensure emergency electrical backup is available within 15 minutes of a external power loss. |  | 0
** | All works are to comply with all current legislative regulations and best practice guidance.
1 | Health, Safety & Environment
1.01 | Allow for the provision of all pre-construction safety file documentation including risk assessments, method statements, COSHH assessments, safety programs, lifting plans etc. & F10 submissions on behalf of the client (if appropriate). |  | 0
1.02 | Allow for all new staff and operatives to undertake a site safety induction prior to starting work on the site. This is envisaged to last approximatly 20 minutes and can be conducted with a group of operatives if required. |  | 0
1.03 | Allow for all safety related equipment including such items as barriers, signage, confined space entry equipment, working at height access equipment and lifting equipment etc. to enable works to be carried out with minimal risk to operatives and building users. our ai is for a zero accident working environment and we encourage all staff and contractors to work toward this goal. |  | 0
1.04 | Allow for your own companies Safe Systems of Work to be utilised and provide the necessary Authorised Persons to issue work permits and safety documentation as required. |  | 0
1.05 | Allow for all approriate waste transportation licences and ensure all arrisings are removed from site and disposed of in an environmentally approved manner. Any spills are to be controlled and cleared immediately they occur, back up remediation plans / resources should be available in the event of a major spill or release of product. |  | 0
2 | Design Works
2.01 | Allow for all investigations of the existing equipment and layouts to enable modifications where necessary for the new system to function correctly on completion of the project. |  | 0
2.02 | Allow for all design works and calculations for all modifications and to ensure the sizing of the new single fuel tank can support the operation of the building under existing load conditions (approx. 400A on all three phases) + 15% for 7 days continuous 24hr running. |  | 0
2.03 | Allow for all electrical design work and calculations for additional supplies to support the new fuel tank system |  | 0
3 | Statement of Requirement
3.01 | Allow to flush any debris from the existing little used pipelines and transfer the existing fuel oil from tank 2 into tank 1. Temporarily modify the return pipework to allow both generators to run from Tank 1. |  | 0
3.02 | Allow to carefully disconnect all electrical supplies and control / monitoring cables from tank 2 ready for reuse where necessary. Empty tank 2, carry out tank clean and provide a gas free certificate. |  | 0
3.03 | Allow for all craneage operations and transport costs to remove tank 2 from site and dispose of in an environmentally approved manner. |  | 0
3.04 | Allow to supply and install a new fully bunded oil fuel tank, suitably sized to comply with section 2.02 above. This tank is to include a fixed fuel polishing system sized sufficiently to agitate the entire tank and prevent dead spots. It shall also be fitted with: Easily accessible fill point providing safe access for operatives engaged in filling operations. Local overfill alarm and remote monitoring of fuel level status via the existing Trend 963 BMS graphics display. Low level alarm indication via the existing BMS Bund flood alarm indication via the existing BMS. Tank / product heaters if considered necessary. The bund access should be constructed to make use of the existing access gantry or an allowance to remove / dispose of the existing gantry and provide a new safe access route shall be included. All relevant pipework, strainers, valves and pumps are to be sized to ensure safe and correct operation of both generator sets at full capacity in the event of load bank testing and simultaneous external power loss. |  | 0
3.05 | Allow for the new tank to be transported and craned into position where tank 2 had previously been located. |  | 0
3.06 | Allow to modify or replace the existing pipework feed and returns to both generators from the new tank position. Pipework arrangement and sizing to simultaneous operation of both sets during load bank testing etc. Flush out and provide gas free certificates for any redundant pipework left underground and semi-permanently cap off to prevent inadvertent use . Install additional supports where pipework is now left exposed and erect signage to warn potential users this equipment is no longer in use. |  | 0
3.07 | Allow to reconnect the existing electrical supplies and alarm cabling, install new cabling where required and fully test and commission the installation. Provide the services of a competent trend BMS engineer to modify the existing Trend 963 programming to remove redundant alarms / graphics and confirm all new alarms and interfaces are set up and working correctly. |  | 0
3.08 | Fill the new tank with new red diesel fuel oil to the recommended full capacity |  | 0
3.09 | Drain down tank 1 and remove / dispose of the product, provide any inherent monitory value back to the client to off set the cost of the overall project. |  | 0
3.1 | Allow to clean and degas tank 1 and remove from site for disposal including all transportation and craneage costs |  | 0
3.11 | Allow to modify the existing access gantry to install additional handrails etc where tank 1 has been removed. Clean, degrease and fully prep the existing rusty metalwork of the complete gantry and apply suitable primer / undercoat / topcoats using proprietary products suitable for the application, external conditions and expected long life use. Colour to be determined after award of contract. |  | 0
3.12 | Allow to fully clean / degrease and prep the accessible external surfaces of both generator housings and exhaust silencers. Apply suitable primer / undercoat / topcoats using proprietary products suitable for the application, external conditions and expected long life use. Colour to be determined after award of contract. |  | 0
3.13 | Jet clean all 6 in number concrete bases in the area using a pressure washer to remove any staining or existing debris build-up |  | 0
4 | Completion
4.01 | Allow for the provision of 2 x electronic copies on CD Rom and one printed hard copy of all commsionning certification, test sheets, manufacturers information, user operation and engineers service and maintenance guides, suppliers contact information, disposal information, ammended BMS strategy and logic modifications etc. together with full layout and schematic drawings of the complete install in DWG. & PDF. formats. This information is to be presented in a post-construction health and safety file format. |  | 0
4.03 | On completion the Contractor to undertake deep clean of working areas and leave the premises clean and tidy, free from dirt, dust and any builders waste and plant. |  | 0
5 | Preliminaries & Overheads
5.01 | Prelims |  | 0
5.02 | Overheads & Profit |  | 0
| TENDER TOTAL |  | 0
| VAT |  | 0
| TOTAL INCLUSIVE OF VAT |  | 0
The nominated Procurement Manager is:
Kathy Monk
Finance & Contracts
Bay 3/19 – Spring Place
105 Commercial Road
Southampton
SO15 1EG
Tel:- 020 381 72328
Email: - Contracts@mcga.gov.uk
| Signed: | Name (Block Capitals):
in the capacity of:
duly authorised to sign tenders for and on behalf of (in BLOCK CAPITALS):
Postal Address:
| Telephone No: | Email:
Date:

## App B - Exisiting Fuel Status
Appendix B
National Maritime Operations Centre
Existing Generator Fuel Status
Background Information
Following guidance from UK National Grid ‘Black Start’ initiative, the MCA has been looking at the requirements to mitigate against a prolonged national power outage and the use of standby power generation until the National Grid could be fully restored.
Indications are that should a major catastrophic event occur, intermittent or prolonged interruptions could be experienced for up to 3 or 4 days after the initial blackout.
The NMOC has 2 fixed LV standby generators to provide N+2 resilience in combination with the Distribution Network Operators (DNO) HV incoming electricity supply.
The operation of these standby generators is that should the HV electricity supply fail, both generators will automatically receive a start signal. Generator 1 will act as the primary source of supply and take the load. Once confirmed that Gen 1 is operational, generator 2 will cool down and switch back to standby. Should generator 1 fail to start or fail during operation, generator 2 will take the load.
Current Fuel Status.
Dual above ground fuel tanks, each with the capacity to hold 24,00 litres, were originally configured to provide a flexible approach to maintaining fuel distribution to each generator. The size of the tanks were designed on an anticipated full load of 1150A per phase, this far exceeds the 400A 3 phase load that the building now presents.
The fuel tanks are currently configured so that tank 1 feeds Generator 1 and tank 2 feeds generator 2 with Tank 1 currently holding 5000 ltrs and tank 2 holding 3000 ltrs.
The fuel is been stored since installation in 2008 and although monthly running checks have not identified any issues of poor starting or combustion, it has been recommended that the fuel should be disposed of and replenished with new fuel oil for the following reasons:
The tanks have been consistently kept with low levels of fuel introducing the increased potential for condensation build up and water contamination, together with the potential for rusting of the tanks internal surfaces is prevalent.
The service valve configuration means that stagnant / contaminated fuel has laid within the unused secondary supply pipes since installation. We have concerns that opening these secondary valves will release debris and although the fuel filters are in line to protect the injectors, works to flush these pipes is recommended before reconfiguring the fuel flow.
Generator Running Capability
Current Building Load and %age of Generator capability
The Generators are rated at 1000kVA (800kW). These Perkins 4000 series diesel engines (4008TAG2A) have a stated fuel consumption of:
Standby Max Power @ 107% | 286 Litres / Hr
Prime Power Rating | 226 Litres / Hr
Continuous Baseload Rating | 175 Litres / Hr
75% Baseload Rating | 163 Litres /Hr
50% Baseload Rating | 109 Litres / Hr
25% Baseload Rating | 59 Litres / Hr
The current loading of the building is approx. 400A per phase (277kW) so we can estimate this to be approx. 35% of the generator’s full capacity.
Interpolation of the stated baseload fuel consumption figures give an approximate consumption at 35% loading of 84 Litres / Hr.
Back calculations to identify the quantity required to achieve a continuous 7 x 24hr day generated supply on 50% Baseload Rating (to allow for future expansion of building use) is to be calculated and allowed for.

## App C - Site Photos
Appendix C
Site Photos
Tank 1 Bund Layout
Tank 1 Information Plate
Tank 2 Bund Layout
Tank 2 Information Plate
Remote fill and drain points located external to the site and connected to the existing fuel tanks via underground pipework.
Drain Valve at remote filling point enclosure
One of the two fill point valves at the remote filling enclosure
Tank 2
Tank 1