## Instructions
Instructions
Please look through the tabs labelled AHU (Air Handling Unit)Requirements and AHU Drawing to see the specifications for the real room exercise.
You will be required to provide one sum for the maintenance of the AHU unit, on the basis of it being a yearly maintenance check. Please note that the following will need to be included in the price. We kindly ask you to complete the price tab, by entering the price for the maintenance check as well as any variations that may not be included for the below list of requirements.
1. Clean exterior of AHU
2. Inspect doors, handles, latches and hinges for proper operation
3. Inspect door gaskets for damage and proper seal
4. Inspect panels for damage
5. Inspect air hoods and air louvers for damage and debris
6. Inspect bird screens for damage, dirt and debris
7. Clean fan segments and fan assembly
8. Check housing, wheel, shaft, frame, inlet vanes and bearing for damage, wear, loose parts, dirt and debris
9. Check fan base, vibration isolators and thrust restraints for damage, wear, loose parts, dirt and debris
10. Check flex connector for damage and wear
11. Check the cleanliness of the filters and replace or clean as required
12. Check filter frames (filter tracks) for residual contaminates and clean as necessary
13. Verify filter gauge and/or switch to function properly
14. Check drive kit for damage, loose parts, wear, dirt, alignment and clean as necessary
15. Check belt tension
16. Lubricate fan bearings
17. Check condition of extended lubrication lines when present
18. Clean variable inlet vanes
19. Check adjustable fan motor base and mounting hardware for loose parts, as well as damage
20. Check fan motor for leaky bearing seals, as well as damage
21. Clean dampers
22. Check for dirt, dust and debris in air vents on fan motor housing
23. Clean dehumidification coils
24. Clean condensation drain pan, trap, drain line and adjusted wetted surfaces
25. Check, clean and calibrate controls
26. Documentation and certification
Pricing
Price will be required to be entered in the tab labelled price. Figure inserted into the price list must be single figure and not a range of figure. If a range is entered either clarification will be requested or the highest value in the range quoted will be used for the purpose of scoring. If clarification is requested and is not provided within the timescales given then the highest value in the range quoted will be used for the purpose of scoring.
We kindly ask you to base your price on the specification of the AHU in the tabs labelled AHU. The price should be given as a figure and not a range. Please note that the AHU is in an accessible plantroom location, which will require no special access equipment e.g. ladders etc. and service work can be carried out during normal working hours, in this case 8:00 am to 5:00pm. The price should be given as a lump sum. Any additional services offered in regards to maintenance should be listed in the tab Additional Service
All prices submitted must be in Sterling and excluding VAT.
Scores will be calculated using the following formula : (Lowest Total Price Received / Total Price to be Scored) x 50% Weighting = Total Score .
All marks and weightings will be calculated to two decimal places.

## AHU Requirements
Requirements of the AHU Unit
Requirements
Supply Air :-
Filter Location No.1
Size: 063
Filter length: pleated filter
Filter class: G4
Filter type: synthetic, cleanable
Drain tray: without
Material: galvanized sheet steel
Inspection side: left
Number of filters 6x592x592, 2x287x592
Pressure drop, start 54 Pa
Pressure drop, dimensioning 89 Pa
Pressure drop, end 124 Pa
Face area 2.5 m²
Face velocity 2.5 m/s
Filter Location No. 2
Size: 063
Filter length: Long bag (vertical pockets only)
Filter class: F7
Filter type: glass fibre, standard
Filter frame : plastic
Inspection side: inlet in end wall
Location: negative pressure
Prefilter: without
Drain tray: without
Material: galvanized sheet steel
Inspection side: left
Number of filters 6x592x592, 2x287x592
Pressure drop, start 69 Pa
Pressure drop, dimensioning 119 Pa
Pressure drop, end 169 Pa
Face area 2.5 m²
Face velocity 2.4 m/s
Exhaust Air :-
Filter Location No. 3
Size: 063
Filter length: pleated filter
Filter class: G4
Filter type: synthetic, cleanable
Drain tray: without
Material: galvanized sheet steel
Inspection side: right
Number of filters 6x592x592, 2x287x592
Pressure drop, start 51 Pa
Pressure drop, dimensioning 86 Pa
Pressure drop, end 121 Pa
Face area 2.5 m²
Face velocity 2.3 m/s

## Price
Maintenance Price
Variants from Requirements | Comments

## Additional Services Offered
Additional Services Offered
Additional Service | Price | Comments