## SRH WEST WING
Drawing Reference | Building | Level | Room | Hole size (mm) | Remedial Actions | Specific details | Photo Ref. | Priority
20-1-1 | West Block | 1 | 20/01/03/43 | 2 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Two pipes pass into floor above unprotected. Fill with intumescent mastic sealant. 60 mins FR. | IMG_0003.JPG | P2A
20-1-2 | West Block | 1 | 20/01/03/43 | Unknown. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Large diameter black metal pipe passes into floor plate above surrounding area over boarded with timber. Remove timber plate to investigate and if required replace timber with mortar seal surrounding pipe to the depth of the floor plate. 60 mins FR | IMG_0004.JPG | P2A
20-1-3 | West Block | 1 | 20/01/03/43 | Unknown. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Protected lagged pipe passes into floor plate above surrounding area over boarded with timber. Remove timber plate to investigate and if required replace timber with mortar seal surrounding pipe to the depth of the floor plate. 60 mins FR. | IMG_0005.JPG | P2A
20-1-4 | West Block | 1 | 20/01/03/42 | 2 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Two plastic conduits pass through wall unprotected. Protective lagged pipework passes through wall through excessive diameter Aperture unsealed. Infill the plastic conduit with intumescent mastic. Overboard the area surrounding pipework using 30 minute fire rated material and seal the perimeter and the joint at the pipework using intumescent mastic. 30 mins FR. | IMG_0007.JPG | P2A
20-1-5 | West Block | 1 | 20/01/03/42 | 10 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Metal ventilation pipe work passes through excessive aperture in wall unprotected and without damper. Install and intumescent damper into the pipework and infill the area surrounding the pipework using intumescent sealant. 30 Mins FR. | IMG_0008.JPG | P2A
20-1-6 | West Block | 1 | 20/01/03/41 | 10 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Orange data cable passes through unsealed aperture. Infill aperture using intumescent mastic. 30 Mins FR. | IMG_0009.JPG | P2A
20-1-7 | West Block | 1 | 20/01/03/41 | 20mm x room perimeter | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Example of inadequate seal between wall and floor plate above. This exists at the perimeter of this room. Infill gap between head of wall and floor plate above using intumescent movement seal. 30 mins FR. | IMG_0010.JPG | P2A
20-1-8 | West Block | 1 | 20/01/03/41 | 100 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Fire alarm cable passing through 2 plastic conduits through excessive aperture. Infill conduits at the point they pass through the wall using intumescent sealant. Infill surrounding area using fire rated foam. Remove the surface excess and coat with a 3 mm layer of intumescent sealant. 30 Mins FR. | IMG_0011.JPG | P2A
20-1-9 | West Block | 1 | 20/01/03/41 | 100 x 100 x 5 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Five protective lagged pipes pass through excessive aperture in the wall. Infill aperture surrounding pipework using fire rated foam. Once dry remove surface Excess of foam and coat using a 3 mm layer of intumescent sealant. 30 Mins FR. | IMG_0012.JPG | P2A
20-1-10 | West Block | 1 | 20/01/03/41 | 300 x 15 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable trays carrying data cables and fire alarm cables pass through excessive aperture in the wall inadequately sealed using Rockwool. Remove previous attempts at Fire stopping and replace with ablative batt, cut to size and sealed at the perimeter / around services using intumescent sealant. It is recommended that a gap is left above the largest cable tray and infilled with an intumescent pillow so that this may be easily maintained for future use. 30 Mins FR. | IMG_0013.JPG | P2A
20-1-11 | West Block | 1 | 20/01/03/32 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Purple data cable passes through unprotected plastic conduit. Infill plastic conduit using intumescent mastic. 30 Mins FR. | IMG_0014.JPG | P2A
20-1-12 | West Block | 1 | 20/01/03/32 | 960 x 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Inspection hatches in place but no other evidence of fire dampers. Fire rated protection provided for ductwork. Investigate the presence of dampers. 30 Mins FR. | IMG_0015.JPG | P2A
20-1-13 | West Block | 1 | 20/01/03/27 | 40 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | White plastic Pipework passes through wall and adequately protected. Fit an intumescent corner collar to the pipe. 30 Mins FR. | IMG_0016.JPG | P2A
20-1-14 | West Block | 1 | 20/01/03/34 | 40 x perimeter of room | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Inadequate fire protection between head of wall and floor flat above. Overboard this immediate area and seal around the boarding using intumescent sealant. The remaining aperture at the head of the wall for the room should be sealed using an intumescent movement seal. 30 Mins FR. | IMG_0017.JPG | P2A
20-1-15 | West Block | 1 | 20/01/03/34 | 200 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Protective lagged pipework passes through excessive aperture in wall. Infill aperture surrounding pipework using fire rated foam. Once dry remove the surface excess and coat using a three mm layer of intumescent sealant. This should be undertaken for the entry and exit of this pipe. 30 Mins FR. | IMG_0018.JPG | P2A
20-1-16 | West Block | 1 | 20/01/03/34 | 30 x 20 x 3 penetrations | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Three plastic conduits pass through wall inadequately sealed. Infill plastic conduit's at that point they pass through the wall using intumescent sealant. The apertures surrounding the plastic conduits should be infilled using intumescent sealant. 30 Mins FR. | IMG_0019.JPG | P2A
20-1-17 | West Block | 1 | 20/01/03/34 | 120 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Open cable trays pass through unprotected aperture in wall. Infill area surrounding cable trays using intumescent pillows. Seal aperture surrounding encosed tray with intumescent mastic sealant. 30 Mins FR. | IMG_0020.JPG | P2A
20-1-18 | West Block | 1 | 20/01/03/34 | 120 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Open cable trays pass through unprotected aperture in wall. Infill area surrounding cable trays using intumescent pillows. Seal aperture surrounding encosed tray with intumescent mastic sealant. 30 Mins FR. | IMG_0021.JPG | P2A
20-1-19 | West Block | 1 | 20/01/03/34 | Numerous | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Multiple plastic conduits and a fire alarm cable pass through wall inadequately sealed. Infill plastic conduit's at that point they pass through the wall using intumescent sealant. The apertures surrounding the plastic conduits should be expanded to a 20mm radius surrounding the pipe and infilled using intumescent sealant rated to crush the pipe. The aperture surrounding the fire alarm cable should be infilled with intumescent sealant. 30 Mins FR. | IMG_0022.JPG | P2A
20-1-20 | West Block | 1 | 20/01/03/36 | 200 x 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Protective lagged pipework passes through excessive aperture in wall. Infill aperture surrounding pipe work using fire rated foam. Once dry remove surface excess and skim foam using intumescent mastic. 30 Mins FR. | IMG_0023.JPG | P2A
20-1-21 | West Block | 1 | 20/01/03/36 | 250 x 300 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable trays pass through wall inadequately protected using loosely packed Glass wool. Infill area behind cable trays with Glass wool and supplement the Infill using intumescent pillows. Overboard the area above the cable trays using 30 minute fire rated material sealed at the perimeter using intumescent mastic. | IMG_0024.JPG | P2A
20-1-22 | West Block | 1 | 20/01/03/36 | 10 x perimeter | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Inadequate fire protection between head of wall and floor plate above. The aperture at the head of the wall for the room should be sealed using intumescent mastic. 30 Mins FR. | IMG_0025.JPG | P2A
20-1-23 | West Block | 1 | 20/01/03/36 | 20 x perimeter of duct | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Ventilation ducting passes through wall without damper and through excessive unprotected aperture. Seal the peimeter of the ducting using intumescent sealant . Infill the damper using an intumescent grill. 30 Mins FR. | IMG_0026.JPG | P2A
20-1-24 | West Block | 1 | 20/01/03/36 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Unprotected plastic conduit passes through wall above door. Infill plastic conduit using intumescent sealant at point it passes through the wall. 30 Mins FR. | IMG_0027.JPG | P2A
20-1-25 | West Block | 1 | 20/01/03/36 | Numerous | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Multiple white plastic conduits and a black flexible conduit pass through wall inadequately sealed. Infill plastic conduit's at the point they pass through the wall using intumescent sealant. 30 Mins FR. | IMG_0028.JPG | P2A
20-1-26 | West Block | 1 | 20/01/03/32 | 20 x 40 and 20 x perimeter of ducting | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | No evidence of fire dampers. Fire rated protection provided for ductwork. Fire stopping surrounding penetration appears inadequate. Investigate the presence of dampers. Seal the perimeter of the duct work using intumescent sealant. Infill any conduit at the point it passes through the wall. 30 Mins FR. | IMG_0029.JPG | P2A
20-1-27 | West Block | 1 | 20/01/03/35 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Iron pipe passes through floorplate apparently unsealed. Infil pipework using intumescent sealant to the depth of 100mm. 60 Mins FR. | IMG_0030.JPG | P2A
20-1-28 | West Block | 1 | 20/01/03/09 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable passes through wall in plastic conduit apparently unsealed. Infill conduit and seal perimeter with intumescent sealant. 30 Mins FR. | IMG_0031.JPG | P2A
20-1-29 | West Block | 1 | 20/01/03/09 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable passes through wall in plastic conduit apparently unsealed. Infill conduit and seal perimeter with intumescent sealant. 30 Mins FR. | IMG_0032.JPG | P2A
20-1-30 | West Block | 1 | 20/01/03/46 | 20 x perimeter of cupboard | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Perimeter seal at the head of the wall is inadequate. Seal perimeter of cupboard construction using intumescent sealant. 30 Mins FR. | IMG_0033.JPG | P2A
20-1-31 | West Block | 1 | 20/01/03/46 | 150 x 200 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Cable tray passes through excessive aperture in wall inadequately stopped. Seal gap above cable and to the side of cable tray using ablative batt. Wrap cables and lower part of tray in elastomeric intumescent wrap. Seal perimeter of above work with intumescent sealant. 30 Mins FR. | IMG_0034.JPG | P2A
20-1-32 | West Block | 1 | 20/01/03/46 | 20 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Conduit and cable penetrates wall inadequately sealed. Infill the conduit and seal the perimeter with intumescent sealant. 30 Mins FR. | IMG_0035.JPG | P2A
20-1-33 | West Block | 1 | 20/01/03/46 | 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Plastic pipework passes through floor plate unprotected. Cut away the excess of the pink foam and fit an intumescent closing collar. Ensure the collar is fitted securely to the floor plate above. 60 Mins FR. | IMG_0036.JPG | P2A
20-1-34 | West Block | 1 | 20/01/03/46 | 100 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Plastic pipework passes through wall unprotected. Fit an intumescent closing collar. Ensure the collar is fitted securely to the wall. 30 Mins FR. | IMG_0037.JPG | P2A
20-1-35 | West Block | 1 | 20/01/01/08 | 150 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Missing compartmentation on wall to allow passage of services. Infill area with ablative batt sealed at the perimeter using intumescent sealant. 30 Mins FR. | IMG_0038.JPG | P2A
20-1-36 | West Block | 1 | 20/01/01/08 | 150 x 150 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Passage of black plastic ventilation ducting through wall unprotected. Fit intumescent closing collar to the duct on the dirty utility side of the wall. 30 Mins FR. | IMG_0039.JPG | P2A
20-1-37 | West Block | First Floor | 20-01-01-17 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0001 (Small).JPG | P2A
20-1-38 | West Block | First Floor | 20-01-01-21 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening and conduits with intumescent mastic. (3no) | IMG_0002 (Small).JPG | P2A
20-1-39 | West Block | First Floor | 20-01-01-21 | 40 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent batt and intumescent mastic. | IMG_0003 (Small).JPG | P2A
20-1-40 | West Block | First Floor | 20-01-01-21 | 10 D, 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening and cables with intumescent mastic. | IMG_0004 (Small).JPG | P2A
20-1-41 | West Block | First Floor | 20-01-01-21 | 10 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0005 (Small).JPG | P2A
20-1-42 | West Block | First Floor | 20-01-01-25 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0006 (Small).JPG | P2A
20-1-43 | West Block | First Floor | 20-01-01-25 | 20 D, 5 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables and pipe with intumescent mastic. (3no) | IMG_0007 (Small).JPG | P2A
20-1-44 | West Block | First Floor | 20-01-01-34 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0008 (Small).JPG | P2A
20-1-45 | West Block | First Floor | 20-01-01-31 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0009 (Small).JPG | P2A
20-1-46 | West Block | First Floor | 20-01-01-37 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0010 (Small).JPG | P2A
20-1-47 | West Block | First Floor | 20-01-01-33 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 120 minutes fire resistance in accordance with BS 476. | Infill around pipe with intumescent mastic. (3no) | IMG_0011 (Small).JPG | P2A
20-1-48 | West Block | First Floor | 20-01-01-44 | 1000 x 2000 | Confirm that fireboard provides 60 minutes resisting construction. |  | IMG_0012 (Small).JPG | P2A
20-1-49 | West Block | First Floor | 20-01-02-13 | 300 x 2000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0014 (Small).JPG | P2A
20-1-50 | West Block | First Floor | 20-01-02-01 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0015 (Small).JPG | P2A
20-1-51 | West Block | First Floor | 20-01-02-02 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0016 (Small).JPG | P2A
20-1-52 | West Block | First Floor | 20-01-02-03 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0017 (Small).JPG | P2A
20-2-1 | West Block | Second Floor | 20-02-02-03 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 120 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0019 (Small).JPG | P1
20-2-2 | West Block | Second Floor | 20-02-02-03 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0020 (Small).JPG | P1
20-2-3 | West Block | Second Floor | 20-02-02-03 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0021 (Small).JPG | P1
20-2-4 | West Block | Second Floor | 20-02-02-01 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0022 (Small).JPG | P1
20-2-5 | West Block | Second Floor | 20-02-01-04 | 400 x 4000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0023 (Small).JPG | P1
20-2-6 | West Block | Second Floor | 20-02-01-05 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0024 (Small).JPG | P1
20-2-7 | West Block | Second Floor | 20-02-01-05 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0025 (Small).JPG | P1
20-2-8 | West Block | Second Floor | 20-02-01-05 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0026 (Small).JPG | P1
20-2-9 | West Block | Second Floor | 20-02-01-05 | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around ductwork using an intumescent batt and intumescent mastic. | IMG_0027 (Small).JPG | P1
20-2-10 | West Block | Second Floor | 20-02-01-05 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0028 (Small).JPG | P1
20-2-11 | West Block | Second Floor | 20-02-01-22 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0029 (Small).JPG | P1
20-2-12 | West Block | Second Floor | 20-02-01-20 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0030 (Small).JPG | P1
20-2-13 | West Block | Second Floor | 20-02-01-20 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduits with intumescent mastic. (3no) | IMG_0031 (Small).JPG | P1
20-2-14 | West Block | Second Floor | 20-02-01-28 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0032 (Small).JPG | P1
20-2-15 | West Block | Second Floor | 20-02-01-24 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0033 (Small).JPG | P1
20-2-16 | West Block | Second Floor | 20-02-01-31 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0034 (Small).JPG | P1
20-2-17 | West Block | Second Floor | 20-02-01-37 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0035 (Small).JPG | P1
20-2-18 | West Block | Second Floor | 20-02-01-39 | 30 D, 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0036 (Small).JPG | P1
20-2-19 | West Block | Second Floor | 20-02-01-39 |  | The inspection found that ducting penetrates the existing fire compartmentation and does not appear, from a visual inspection, to be provided with a damper or enclosed in fire resistant construction. | Provide ductwork with an accessible fire damper. | IMG_0037 (Small).JPG | P1
20-2-20 | West Block | Second Floor | 20-02-01-42 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0038 (Small).JPG | P1
20-2-21 | West Block | Second Floor | 20-02-01-42 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0039 (Small).JPG | P1
20-2-22 | West Block | Second Floor | 20-02-01-47 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0040 (Small).JPG | P1
20-2-23 | West Block | Second Floor | 20-02-01-47 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0041 (Small).JPG | P1
20-2-24 | West Block | Second Floor | 20-02-01-31 | 10 x 20 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 120 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0042 (Small).JPG | P1
20-2-25 | West Block | Second Floor | 20-02-01-52 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0043 (Small).JPG | P1
20-2-26 | West Block | Second Floor | 20-02-03-37 | 300 x 500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. | IMG_0044 (Small).JPG | P1
20-2-27 | West Block | Second Floor | 20-02-03-31 | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0045 (Small).JPG | P1
20-2-28 | West Block | Second Floor | 20-02-03-31 | 60 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0046 (Small).JPG | P1
20-2-29 | West Block | Second Floor | 20-02-03-31 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0047 (Small).JPG | P1
20-2-30 | West Block | Second Floor | 20-02-03-22 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduits using an intumescent mastic. (2no) | IMG_0048 (Small).JPG | P1
20-2-31 | West Block | Second Floor | 20-02-03-22 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0049 (Small).JPG | P1
20-2-32 | West Block | Second Floor | 20-02-03-21 | 10 D, 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. (2no) | IMG_0050 (Small).JPG | P1
20-2-33 | West Block | Second Floor | 20-02-03-17 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. | IMG_0051 (Small).JPG | P1
20-2-34 | West Block | Second Floor | 20-02-03-14 | 2000 x 6000 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0052 (Small).JPG | P1
20-2-35 | West Block | Second Floor | 20-02-03-14 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. Seal off gaps between batt components with intumescent mastic. | IMG_0053 (Small).JPG | P1
20-2-36 | West Block | Second Floor | 20-02-03-14 | 40 x 40 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0054 (Small).JPG | P1
20-2-37 | West Block | Second Floor | 20-02-03-13 | 10 x 250 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent batt and intumescent mastic. | IMG_0055 (Small).JPG | P1
20-2-38 | West Block | Second Floor | 20-02-03-06 | 10 x 10 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 120 minutes fire resistance in accordance with BS 476. | Infill around penetration in wall corner using an intumescent mastic. | IMG_0056 (Small).JPG | P1
20-2-39 | West Block | Second Floor | 20-02-03-01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 120 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0057 (Small).JPG | P1
20-3-1 | West Block | Third Floor | 20-03-03-06 | 30 D, 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (2no) | IMG_0058 (Small).JPG | P1
20-3-2 | West Block | Third Floor | 20-03-03-07 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0059 (Small).JPG | P1
20-3-3 | West Block | Third Floor | 20-03-03-07 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around opening and cable with intumescent mastic. (2no) | IMG_0060 (Small).JPG | P1
20-3-4 | West Block | Third Floor | 20-03-03-07 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0061 (Small).JPG | P1
20-3-5 | West Block | Third Floor | 20-03-03-12 | 40 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0062 (Small).JPG | P1
20-3-6 | West Block | Third Floor | 20-03-03-46 | 200 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. Provide uPVC pipe with a pipe collar. | IMG_0063 (Small).JPG | P1
20-3-7 | West Block | Third Floor | 20-03-03-46 | 200 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0064 (Small).JPG | P1
20-3-8 | West Block | Third Floor | 20-03-03-46 | 10 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0065 (Small).JPG | P1
20-3-9 | West Block | Third Floor | 20-03-03-47 | 30 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (4no) | IMG_0066 (Small).JPG | P1
20-3-10 | West Block | Third Floor | 20-03-03-47 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0067 (Small).JPG | P1
20-3-11 | West Block | Third Floor | 20-03-03-48 | 20 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (4no) | IMG_0068 (Small).JPG | P1
20-3-12 | West Block | Third Floor | 20-03-01-43 | 10 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill above conduit using an intumescent mastic. | IMG_0069 (Small).JPG | P1
20-3-13 | West Block | Third Floor | 20-03-01-43 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0070 (Small).JPG | P1
20-3-14 | West Block | Third Floor | 20-03-01-38 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. | (2no) | IMG_0071 (Small).JPG | P1
20-3-15 | West Block | Third Floor | 20-03-01-29 | 30 x 30 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around and inside conduit penetration with suitable intumescent mastic. | IMG_0072 (Small).JPG | P1
20-3-16 | West Block | Third Floor | 20-03-01-29 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduits with intumescent mastic. (2no) | IMG_0073 (Small).JPG | P1
20-3-17 | West Block | Third Floor | 20-03-01-28 | 50 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0074 (Small).JPG | P1
20-3-18 | West Block | Third Floor | 20-03-01-22 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0075 (Small).JPG | P1
20-3-19 | West Block | Third Floor | 20-03-01-18 | 70 x 2500 | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0076 (Small).JPG | P1
20-3-20 | West Block | Third Floor | 20-03-01-20 | 70 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent mastic. | IMG_0077 (Small).JPG | P1
20-3-21 | West Block | Third Floor | 20-03-01-01 |  | The construction at high level was not present. Provide a minimum 30 minute fire resistance. | The linen cupboard is not enclosed in fire resisting construction. Enclose cupboard in 30 min FR construction. | IMG_0078 (Small).JPG | P1
20-3-22 | West Block | Third Floor | 20-03-01-01 |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0079 (Small).JPG | P1
20-3-23 | West Block | Third Floor | 20-03-01-01 | 100 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill around cable tray using an intumescent batt and intumescent mastic. | IMG_0080 (Small).JPG | P1
20-3-24 | West Block | Third Floor | 20-03-01-02 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 30 minutes fire resistance in accordance with BS 476. | Infill inside conduit with intumescent mastic. | IMG_0081 (Small).JPG | P1
20-3-25 | West Block | Third Floor | 20-03-02-01 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable with suitable intumescent mastic. | IMG_0082 (Small).JPG | P1
20-3-26 | West Block | Third Floor | 20-03-03-01 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. Ensure that the cables are suitably back coated with intumescent mastic. | IMG_0083 (Small).JPG | P1
20-3-27 | West Block | Third Floor | 20-03-02-02 | 100 x 2500 | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Plasterboard does not extend to the soffit. Install intumescent batt structurally secured to existing construction elements. Seal the head of the wall with an intumescent expansion joint seal. | IMG_0084 (Small).JPG | P1
20-3-28 | West Block | Third Floor | 20-03-02-02 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0085 (Small).JPG | P1
20-3-29 | West Block | Third Floor | 20-03-02-02 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable using an intumescent mastic. | IMG_0086 (Small).JPG | P1
20-3-30 | West Block | Third Floor | 20-03-03-21 | 20 x 40 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0087 (Small).JPG | P1
20-3-31 | West Block | Third Floor | 20-03-03-21 | 10 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0088 (Small).JPG | P1
20-1-55 | West Block | First Floor | 20/01/02/02 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the roof wasn’t determined. Provide 60 minute FR construction. | IMG_0104.JPG | P2A
20-1-56 | West Block | First Floor | 20/01/02/02 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 minute FR floor construction. | IMG_0105.JPG | P2A
20-1-57 | West Block | First Floor | 20/01/02/02 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0106.JPG | P2A
20-1-58 | West Block | First Floor | 20/01/02/02 | 30 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0107.JPG | P2A
20-1-59 | West Block | First Floor | 20/01/02/02 | 20 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0108.JPG | P2A
20-1-60 | West Block | First Floor | 20/01/02/02 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipe using an intumescent batt and intumescent mastic. | IMG_0109.JPG | P2A
20-1-61 | West Block | First Floor | 20/01/02/02 | 300 x 3000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Insert a structurally supported intumescent batt into the gap in floor. | IMG_0110.JPG | P2A
20-1-62 | West Block | First Floor | 20/01/02/03 | 400 x 400 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Provide hatch to close opening in ceiling. FR 60 | IMG_0111.JPG | P2A
20-1-63 | West Block | First Floor | 20/01/02/03 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable tray with intumescent mastic. | IMG_0112.JPG | P2A
20-2-40 | West Block | Second Floor | 20-02-03-04 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | Insert a structurally supported intumescent batt into the gap in floor. | IMG_0113.JPG | P1
20-2-41 | West Block | Second Floor | 20-02-03-04 |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | The fire rating of the floor wasn’t determined. Provide 60 minute FR floor construction. | IMG_0114.JPG | P1
20-2-42 | West Block | Second Floor | 20-02-03-04 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 minute FR floor construction. | IMG_0115.JPG | P1
20-2-43 | West Block | Second Floor | 20-02-03-04 | 100 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. | IMG_0116.JPG | P1
20-2-44 | West Block | Second Floor | 20-02-03-04 | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0117.JPG | P1
20-2-45 | West Block | Second Floor | 20-02-03-04 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent mastic. | IMG_0118.JPG | P1
20-2-46 | West Block | Second Floor | 20-02-03-04 | 60 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0119.JPG | P1
20-2-47 | West Block | Second Floor | 20-02-01-50 | 60 x 60 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. | IMG_0120.JPG | P1
20-2-48 | West Block | Second Floor | 20-02-01-50 | 60 x 2500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Insert a structurally supported intumescent batt into the gap in floor. | IMG_0121.JPG | P1
20-2-49 | West Block | Second Floor | 20-02-01-50 |  | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable tray using an intumescent batt and intumescent mastic. | IMG_0122.JPG | P1
20-2-50 | West Block | Second Floor | 20-02-01-50 | 50 x 1000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cable trays using an intumescent batt and intumescent mastic. | IMG_0124.JPG | P1
20-2-51 | West Block | Second Floor | 20-02-01-50 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. | IMG_0125.JPG | P1
20-1-88 | West Block | First Floor | 20-01-01-46 | 700 x 2500 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0232 (Small).JPG | P2A
20-1-89 | West Block | First Floor | 20-01-01-46 | 100 x 200 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0233 (Small).JPG | P2A
20-1-90 | West Block | First Floor | 20-01-01-46 | 100 x 2000 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0234 (Small).JPG | P2A
20-1-91 | West Block | First Floor | 20-01-01-46 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 min FR floor construction. | IMG_0235 (Small).JPG | P2A
20-1-92 | West Block | First Floor | 20-01-01-46 | 50 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the openings using an intumescent mastic. (3no) | IMG_0236 (Small).JPG | P2A
20-1-93 | West Block | First Floor | 20-01-01-46 | 30 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill the opening using an intumescent mastic. | IMG_0237 (Small).JPG | P2A
20-1-94 | West Block | First Floor | 20-01-01-46 | 30 x 30 | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening with intumescent mastic. FR 60 | IMG_0238 (Small).JPG | P2A
20-3-95 | West Block | Third Floor | 20-03-01-48 |  | The indicated fire door is not provided with intumescent backed cold smoke seals. Supply and install into the existing fire door, intumescent backed cold smoke seals to head and edges of door. To the existing fire door undertake the appropriate preparatory works. (a) Remove existing fire door from its frame, rout out top and vertical edges of door to cut a smooth groove of 10mm x 4mm. Provide and install new intumescent backed cold smoke seals (suitably glued and tacked into the door). Re-hang existing fire door ensuring it closes fully into its frame. |  | IMG_0239 (Small).JPG | P1
20-3-96 | West Block | Third Floor | 20-03-01-48 |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 min FR floor construction. | IMG_0240 (Small).JPG | P1
20-3-97 | West Block | Third Floor | 20-03-01-48 | 100 x 400 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill above ductwork using an intumescent batt and intumescent mastic. | IMG_0241 (Small).JPG | P1
20-3-98 | West Block | Third Floor | 20-03-01-48 | 50 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening with intumescent mastic. FR 60 | IMG_0242 (Small).JPG | P1
20-3-99 | West Block | Third Floor | 20-03-01-48 | 50 x 100 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around conduit using an intumescent batt and intumescent mastic. | IMG_0243 (Small).JPG | P1
20-3-100 | West Block | Third Floor | 20-03-01-48 |  | Foam was observed at high level. The type and fire resistance of the foam was questionable. Therefore, remove the existing foam and infill the opening using a new intumescent batt and/or intumescent mastic. Infill openings to provide a minimum 60 minute fire resistance. | Apply a 3 mm layer surface finish using intumescent mastic. | IMG_0244 (Small).JPG | P1
20-3-101 | West Block | Third Floor | 20-03-01-48 | 50 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent mastic. (4no) | IMG_0245 (Small).JPG | P1
20-3-102 | West Block | Third Floor | 20-03-01-48 | 50 x 50 | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent mastic. | IMG_0246 (Small).JPG | P1
20-4-103 | West Block | Fourth Floor |  |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 60 minute fire resistant door set complete with frame, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. | The fire rating of the door wasn’t determined. Ensure that the door meets the specifaction of a FD60S door. | IMG_0247 (Small).JPG | P1
20-4-104 | West Block | Fourth Floor |  | 10 dia. | Openings/penetrations were observed in the compartmentation at the indicated location. Undertake fire stopping works as outlined to reinstate the integrity of the compartmentation. | Infill opening with intumescent mastic. FR 60 | IMG_0248 (Small).JPG | P1
20-4-105 | West Block | Fourth Floor |  |  | The construction at high level was not present. Provide a minimum 60 minute fire resistance. | The fire rating of the floor wasn’t determined. Provide 60 min FR floor construction. | IMG_0249 (Small).JPG | P1
20-4-4 | West Block | Fourth Floor | 20-04-Plant Room | 10 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill the opening using an intumescent batt and intumescent mastic. | IMG_0324 (Small).JPG | P1
20-4-5 | West Block | Fourth Floor | 20-04-Plant Room | 60 dia. | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around cables using an intumescent batt and intumescent mastic. | IMG_0325 (Small).JPG | P1
20-4-6 | West Block | Fourth Floor | 20-04-Plant Room | 100 D | Penetration(s) were observed at the indicated location. Ensure that the opening(s) and penetration(s) are suitably fire stopped with suitable fire resistant materials. Make good the penetration(s) and ensure they are adequately fire stopped using an intumescent sealing system which affords a minimum of 60 minutes fire resistance in accordance with BS 476. | Infill around pipes using an intumescent batt and intumescent mastic. (2no) | IMG_0326 (Small).JPG | P1
20-4-7 | West Block | Fourth Floor | 20-04-Plant Room |  | The existing door is not fire resistant in nature. Remove existing door and frame and dispose. Supply and install 30 minute fire resistant door set complete with frame, glazed 30 minute vision panels, overhead self closing door closer and intumescent strips and seals. Hang the fire door on the frame using three steel hinges. Provide and fit suitable door furniture and fire door signage. Door to be decorated to match surrounding doors. |  | IMG_0327 (Small).JPG | P1