## Sheet1
The Pirbright Institute
BACS Alarms and Human Factors
MOD 2 Enabling works |  | Unit | Rate | Total
ref | General Items |  |  |  | Drawings | 30687- AR - SK -1001 A1 Existing Ground Floor Layout
1 | Allow for supervision of the works |  |  |  |  | 30687- AR - DR-1001 A1 Client Definition Ground Floor MOD2 WIP
2 | Allow for skips, protection and regular cleaning
3 | Allow for the preparation of RAMS and the Management of Health and Safety
4 | Construct temporary hoarding as sketch to close off the work area
5 | The door to the permit room should be removed and walled up early in the contract to ensure separation of the work area
6 | The contractor should allow for desk moves and taking some furniture to store on site
7 | Once this work is complete the staff will move into the far end of the office and contractor will construct a temporary hoarding as shown to enclose his work area
Builders Work
1 | Extend the existing concrete base for the split unit to serve the Permit Office approximately 700mm by 1000mm with suitable reinforcement
2 | Seal up the hole in the external wall where the split HVAC unit has been removed and decorate to match existing
Carpenter and Joiner
Permit Office
1 | Remove the existing door and set aside for reuse
2 | Infill the door opening in Vinyl coated plasterboard on both sides fixed to steel studding infilled with sound deadening quilt
3 | Remove the sliding permit board from the wall and set aside. Form new door opening as indicated on drawings and reinstall the door previously removed
4 | Remove existing window approximately 1194 wide by 1091 high and reglaze with two panes one pane to slide open
5 | Relocate the large 55 inch screen in the open office are and relocate in the permit office. Remove the existing plaster board, introduce a plywood panel in the partition wall to take the screen and make good plasterboard to match existing
6 | Meeting Room
7 | Form new wall to meeting room in 50mm metal stud approx. 3560mm wide with 1500mm return Clad both sides in 12.5 mm plasterboard coated in Muraspec Teviot Vinyl paper and white PVC joint strips to match existing with Rockwool sound deadening quilt layer between
8 | Form new door opening and supply and fit new door FD30 timber veneer door set 926mm wide complete with 160mm by 1440mm vision panel to match other internal doors as closely as possible
Control room Wall
9 | Construct wall to control room 8560mm long by 2489mm high in 75mm metal stud clad one side only in 12mm plywood and 12.5mm vinyl coated plasterboard
10 | From new door opening and install new SR2 security door from Titan Doors as quote supplied or similar approved with vision panel and electro lock
11 | Relocate the sliding work permit screens onto the new partition wall and introduce plywood as necessary to support the screen runners
Decorator
12 | Decorate any new or disturbed surfaces that require decoration
Electrical
MOD2
1 | The objective is to isolate all services in the proposed new control room at the West end of MOD 2 and strip out lighting and containment so that the walls can be reclad by others
2 | Isolate the small power and data ring main leaving the remining office area operational. Remove containment and set aside for re-use
3 | Remove and dispose of the strip lights in the proposed control room area
4 | Isolate the strip lights at the west end and remove the line of lights which conflict with the new wall. Refit to the ceiling approx. 600mm from the line of the new wall
Permit Office
4 | Amend the small power and data on both sides of the office wall to allow for the new door to the permit office. Run power and data up and over the door to leave all existing sockets and data outlets live
5 | Provide additional power and data for the new desk in the corner of permit office
6 | Move the light switch to suit the new door location
Main office area
1 | Run the set aside dado trunking with power and data along the new partition walls - install double sockets and twin RJ45 outlets at 1.8m centre
2 | Run twin 13amp socket outlets and twin RJ45 points to the line of six relocated desks. Set aside Dado trunking to be fixed to both sides of a privacy screen provided by the Employer with doble socket and twin RJ45 to each desk
3 | Run new power supply for the split HVAC unit serving the permit office
Meeting Room
4 | Disconnect and move two sections of white plastic trunking which conflict with the new head plate of the meeting room wall. Replace and reconnect on completion of the meeting room wall
Mechanical
1 | Isolate the heating main at either side of the office area so as to isolate the radiators in the proposed control room area leaving all other radiators working. Remove the redundant radiators and the redundant pipework. Recommission the system
2 | De Gas and relocate the split unit which conflicts with the new wall. Move approx. 1.4m leaving the condenser unit where it is. Recommission the system
3 | Install a new 3.5kw split unit in the permit office commission and provide O&M manuals
Total Cost to complete the works
isolate power and data
this area to be electrically isolated
new trunking
power and data
new door and amended power and data on both sides of the wall
isolate heating main and remove rads. in control room area marked thus
relocate split AC unit
new split unit in this office
additional power and data in this corner where door removed
temporary hoarding
Mechanical Work
Electrical Work
remove existing door
form new door
new stud wall and door
proposed control room area