## OTA Range
RFQ FY19-28 Cleanroom Response template
Ref # | Requirement | Description | Shall (Minimum requirement) | Should (Desirable Feature) | Response - Please provide details your product features which confirm your compliance with this requirement | Note
1 | Acceptance Cleanroom | 5.5 x 12.4m Cleanroom, ISO 8 | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
2 | Production and Assembly Cleanroom | 13.5 x 15.5m Cleanroom, ISO 7 | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
3 | Enviromental Test and Verification Cleanroom | 11 x 7.3m Cleanroom, ISO 7 | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
4 | CubeSat Production and Assembly Cleanroom | 6 x 14.2m Cleanroom, ISO 7 | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
5 | Gowning Area 1 | 4.6 x 8.2m Cleanroom area, ISO 8 | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
6 | Gowning Area 2 | 3 x 6.4m Cleanroom area, ISO 8 | X |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
7 | Technical Support Area Cleanroom | 5.5 x 3m Cleanroom, ISO 7 | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
8 | Clean airlock | 4.6 x 1.4m Airlock, ISO 8 | X
9 | Climate Control System | Capable of maintaining 40% - 60% RH at all times | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
10 | Power (SP) | Multiple single phase double sockets on dado rails / trunking in all areas, rated to 240V | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
11 | Power (3PH) | Multiple 480V-3PH-60HZ (capable of 450A per phase) drops in the production and assembly cleanroom - provision for sockets | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
12 | Compressed Air | Multiple drops in all cleanrooms, system capable of maintaining 200 PSI | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
13 | Lighting | LED high lumen lighting to all areas, with emergency lighting as backup | X |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
14 | Doors | Doors labelled (L), to be high speed roll doors or equivalent to 4m high | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
15 | Internal Heights | 4m ceilings | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
16 | Data Points | Ethernet access points in all dado trunking, Cat 6 cabling, in all areas | x |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
17 | Flooring | ESD compliant flooring in all areas | X |  | [Please insert your answer. No more than 200 word per answer} | pass/fail
Ref # | Desirable features Requirement | Description | Shall (Minimum requirement) | Should (Desirable Feature) | Response - Please provide details your product features which confirm your compliance with this requirement | Max score | Mark Awarded
18 | Oxygen monitoring | Provision for monitoring atmosphere in Environmental test and verification cleanroom for low oxygen levels |  | x | [Please insert your answer. No more than 200 word per answer} | 10 | 0
19 | Reconfigurable construction | Ability to reconfig the layout of the cleanrooms, e.g. to expand or create smaller work areas |  | x | [Please insert your answer. No more than 200 word per answer} | 10 | 0
20 | ISO Rating | Ability to upgrade or down grade the ISO cleanliness rating |  | x | [Please insert your answer. No more than 200 word per answer} | 10 | 0
21 | Ease of access to HEPA filteration system | Preferred ease of access to to replace HEPA filters by own facility staff |  | x | [Please insert your answer. No more than 200 word per answer} | 10 | 0
Max score available for desirable features: | [5 empty] | 40 | 0