Ref:  PC/N.W1700021	Date:  November 2017

SPECIFICATION FOR THE REMOVAL OF THE EXISTING TWO

HYDRAULIC PASSENGER LIFTS AND FULL REPLACEMENT

WITH 2 NO. MRL DESIGN PASSENGER LIFTS

SUITABLE FOR INTENSIVE USE

LOCATED AT

MERSEYSIDE MARITIME MUSEUM

ON BEHALF OF

NATIONAL MUSEUMS  LIVERPOOL

IN CONJUNCTION WITH

TUV SUD DUNBAR BOARDMAN

Prepared by: P. Crosbie……………………. Date: 18th October 2017 ……………………………….

Checked by: S.W. Aitken.…………………. Date: 20th October 2017……………………………….

This document and its contents are the property of the Purchaser/Employer and TUV-SUD Dunbar Boardman. They may not be copied or reproduced in any way, in part or whole, without prior written approval of both parties. Violations will result in legal action.

INDEX

Section 1	Pages	3 - 6	Instructions to Tenderer

Section 2	Pages	7 - 32	Preliminaries and Conditions of Contract

Section 3 	Pages	33 – 57	CDM 2015 Regulations

Section 4	Pages	58 - 64	Schedule of Builders Work

Section 5	Pages	65 - 68	Schedule of Electrical Work

Section 6	Pages	69 - 75	Schedule of Equipment

Section 7	Pages 	76 - 127	Technical Specification

Section 8	Pages	128 - 135	Commissioning and Acceptance

Section 9	Pages	136 - 140	Maintenance

Section 10	Pages 	141 - 159	Tender Particulars

INSTRUCTIONS TO TENDERERS

SECTION 1

# 1.	INSTRUCTIONS TO TENDERER

1.1	Acknowledgement:  On receipt of these documents the Lift Contractor should confirm in writing that he has received the documents and whether or not he will be submitting a Tender in accordance with these instructions by the due date, and confirm that the documents received are complete.

The Lift Contractor shall return the fully completed tender documents via email to;

tenders@liverpoolmuseums.org.uk

subject title 'Merseyside Maritime Museum Passenger Lifts Replacement'

By Thursday 7th December 2017                            by    12 Noon

Tenders received after this date or time will be deemed invalid.

Completion of Documents: All of the pages in Section 10 of this Specification are to be fully completed by the Lift Contractor and submitted with the Tender together with any supporting information requested in this Specification.  Failure to provide this documentation will invalidate the Tender.

Implementations: No guarantee can be made that the project will proceed as planned, or at all, or that it will not be postponed or cancelled. The Purchaser does not bind himself to accept either the lowest or any Tender. No claim by a Lift Contractor for any expense, loss of profit or other such consideration incurred in the preparation of a Tender will be accepted.

Public Contracts Regulations 2015: Where this Tender is one to which the Public Contracts Regulations 2015, and/or the Public Contracts (Scotland) Regulations 2015, applies the award of any Contract shall be determined upon the basis of the most economically advantageous tender, which may, where appropriate, include factors such as key staff qualification and experience and life-cycle costing.

Alterations: Any alteration to the text of these documents will not be accepted. Any unauthorised alterations or qualifications will be disregarded and may result in disqualification of the Tender.  Any conditions which may be printed on the Lift Contractor’s letter paper and which may accompany the Tender will not be accepted and, any such conditions are deemed to be waived by the Lift Contractor unless specifically noted in the Lift Contractor’s accompanying letter and agreed in writing by the Engineer.

Qualifications:  The requirements of the Project are indicated within this Specification. Where the Lift Contractor’s Tender for carrying out the work is based on any deviation from the requirements of this Specification in respect of any materials, method of installation, performance, builders work or the like, which is due solely to the Lift Contractor’s own standard design requirements, such deviations shall be clearly set out in a covering letter or schedule to be submitted with this Tender.  In the absence of such a covering letter or schedule it will be deemed that the price quoted by the Lift Contractor includes for the whole of the work to be carried out as specified herein and no later requests for deviation will be considered.

Corrections:  Lift Contractors are requested to take all due care in the completion of the tender documents. Should errors occur the person signing the Form of Tender shall initial the correction. Under no circumstances should correction fluid be used.

Bona Fide Tender: The Lift Contractor undertakes that he has not communicated, and will not communicate, to any person under any agreement or arrangement to do so, the amount of this Tender, and that the amount of this Tender has not been adjusted under any agreement or arrangement with any persons so to do.

Lifts Regulations 2016 & EU Lifts Directive 2014/33/EU

The Lift Contractor shall ensure that the design, manufacture, construction and installation of the lifts is undertaken in full compliance with the requirements of the Lifts Regulations 2016 and EU Lifts Directive 2014/33/EU.

Wherever necessary the Lift Contractor shall include for seeking and obtaining the approval of a Notified Body in relation to any variation against the requirements of the applicable Harmonised Standards BS EN81-20: 2014 and BS EN81-50: 2014 together with all other applicable and/or associated Harmonised Standards.

The Lift Contractor shall include within his Tender for all costs associated with seeking and obtaining all Notified Body approvals.

Risk Assessment (CDM): The Project will fall within the scope of the Construction (Design & Management) Regulations 2015. The Lift Contractor shall provide with his offer his risk assessments, COSHH data, Safety Policy and hierarchy of responsibilities, along with his accident record under RIDDOR covering the previous 3 year period.

TUV-SUD LTD DUNBAR & BOARDMAN

LIFT AND ESCALATOR CONSULTANTS

CONFIRMATION OF RECEIPT OF TENDER DOCUMENTS OR AMENDMENTS

CONTRACT:	Full Replacement of 2 No. Passenger Lifts at Merseyside Maritime Museum

CONTRACTOR:

ACKNOWLEDGEMENT:

We confirm that we have today received your tender documents, which we have checked and agree these are complete, and that we will submit a bona fide tender by the due date.

Signed 		………………………..

Contractor		………………………..

Date			………………………..

RETURN TO:	Paul.Crosbie@tuv-sud.co.uk

REF: 				N.W1700021

PRELIMINARIES AND CONDITIONS OF CONTRACT

SECTION 2

FORM OF AGREEMENT

This Deed is made on the………………………………. Day of ……………………...…...

between:

- ……………… (No. ………) whose registered office is at………………………….

………………………………………………………………………….………………..

(the ‘Purchaser’) of the one part; and

- ……………… (No. ………) whose registered office is at...................................... ........................................…………......................................................

(the ‘Contractor’) of the other part.

Recitals:

(A)	The Purchaser wishes to have certain Works executed by the Contractor, briefly described as:

Full replacement of 2 no. hydraulic passenger lifts with 2 no. machine roomless design passenger lifts in accordance with the TUV-SUD Dunbar Boardman specification reference N.W1700021

(the ‘Works’) at Merseyside Maritime Museum, Albert Dock Liverpool L34AQ (the ‘Site’)

(B)	The Purchaser has agreed to engage the Contractor for the design, manufacture, delivery to Site, installation, testing and completion of the Works, including the associated building works and the remedying of defects in the Works in accordance with the Contract, as amended by the Schedule of Amendments, under the direction of the Engineer, in the sum of

……………………………………………………………………..…... (amount in figures)

(……………………………………………………………………………………………………………………………………………………………………….....) (amount in words)

(the ‘Contract Price’).

(C) The Purchaser has appointed Tuv-Sud Ltd Dunbar Boardman (No. SC215164) of 93 Scottish Enterprise Technology Park, East Kilbride, Glasgow G75 0QF as the Engineer (the ‘Engineer’) for the purposes of the Works and as Principal Designer for the purposes of the Construction (Design and Management) Regulations 2015.

This Contract is the entire agreement between the parties in relation to the subject matter herein and supersedes any previous agreement between the parties with regard to the Works.

It is agreed as follows:

1.	In this Agreement words and expressions shall have the same meanings as are respectively assigned to them in the General Conditions, as amended by the Schedule of Amendments.

2.	The following documents shall be deemed to form and be read and construed as part of the Contract:

(a) this Agreement;

(b) the Schedule of Amendments as annexed to this Form of Agreement with the following appendices:

(c) the MF/1 General Conditions of Contract (rev 6 2014 Edition) as amended by the Schedule of Amendments;

(d) the MF/1 Special Condition 2: adjudication;

(e) the Specification and the drawings and documents (if any) annexed to, or referred to in, the Contract;

(f) the Letter of Acceptance; and

(h) the Tender.

3.	In consideration of the payments to be made by the Purchaser to the Contractor in accordance with the Contract, the Contractor agrees to design, manufacture, deliver to Site, install, test and complete the Works and to remedy defects in the Works in conformity in all respects with the provisions of the Contract.

4.	The Purchaser shall pay the Contractor, in consideration of the execution and completion of the Works and the remedying of defects in the Works, the Contract Price or such other sum as may become payable under the provisions of the Contract together with the Value Added Tax properly chargeable on such sums, at the times and in the manner prescribed by the Contract.

5.	If any question, dispute or difference shall arise between the Purchaser and the Contractor in relation to the Contract or in any way related to the Works, which cannot be settled amicably, it shall be determined in accordance with clause 52 (Disputes) of the General Conditions.

The parties have entered into this Deed in the manner required by their respective constitutions and the laws of their respective countries.

In witness whereof the parties have executed and delivered this agreement as a deed on the date above written.

Executed as a deed for and on behalf of	………………... (Full name of Purchaser)

In the presence of         ..........................................(Signature)						…………………………………(Title)

Executed as a deed by	………………... (Full name of Purchaser) acting by two directors or by a director and its secretary

………………………………………… (Signature)

Director

………………………………………… (Signature)

Director/Secretary

  - CONDITIONS OF CONTRACT

The Conditions of Contract are to be read throughout, subject to the amendments and special conditions set out in the Preliminaries.

The Form of Contract shall be the MF1 (rev 6) 2014 Edition published for the Joint IMechE/IET Committee on Model Forms of General Conditions of Contract by The Institution of Engineering and Technology, London, United Kingdom.  This should be read in conjunction with the conditions contained herein.

The submission of a Tender by the Lift Contractor shall be deemed to signify acceptance of the incorporation of the Terms and Conditions of the MF1 Form of Contract stated, which shall be read subject to the Conditions contained herein.

The costs of complying with all standard amendments to the MF1 Contract, promulgated by the date of Tender (as defined in the Conditions) shall be included in the Tender sum.

Any additional cost considered necessary to meet all the requirements of the following amendments to the Conditions of Contract shall be included in the Tender.

2.1	Schedule of Amendments to the MF/1 Rev 6 General Conditions

The following amendments apply and the MF/1 General Conditions shall be construed accordingly. In the case of any inconsistency between the printed MF/1 General Conditions and the following amendments, the following amendments prevail.

| Clause |  |
| --- | --- |
| 1.1.gg | In clause 1.1.gg, line 41, delete “and the sub-contractor’s legal successors in title”,. |
| 1.1.y | Delete clause 1.1.y. Replace with “’Purchaser’ means National Museums Liverpool whose registered office is at 127 Dale Street, Liverpool L2 2JH and the legal successors in title to the Purchaser”. |
| 1.1.g | Delete clause 1.1.g. Replace with “”Contractor” means ************ (No. ****) whose registered office is at **********************************”. |
| 1.1.c | In clause 1.1.c, after “Special Conditions”, insert “as amended by this Schedule of Amendments”. |
| 1.1.d | Delete clause 1.1.d. Replace with “”Contract” means the Form of Agreement, the Conditions and the Specification (together with all schedules, drawings and correspondence annexed to the Contract and/or the Specification or incorporated in these by reference).”. |
| 1.1.ii | Delete clause 1.1.ii. Replace with “This Contract is the entire agreement between the parties in relation to the subject matter herein and supersedes any previous agreement between the parties with regard to the Works” References to the term ‘Tender’ in the Contract shall be interpreted as referring to the Contract. Any ambiguity in the interpretation of the term ‘Tender’ in the Contract shall be resolved by the Purchaser at its sole discretion”. |
| 1.1.r | Delete clause 1.1.r. Replace with “This Contract is the entire agreement between the parties in relation to the subject matter herein and supersedes any previous agreement between the parties with regard to the Works” References to the term ‘Letter of Acceptance’ in the Contract shall be interpreted as referring to the Contract. Any ambiguity in the interpretation of the term ‘Letter of Acceptance’ in the Contract shall be resolved by the Purchaser at its sole discretion”. |
| 2.6 | In clause 2.6, line 26, before “If the Contractor” insert “Subject always to clause 2.4”. In clause 2.6, line 26, delete “14”. Insert “7”. In clause 2.6, line 31, delete “21”. Insert “14”. In clause 2.6, line 36, delete “21”. Insert “7”. In clause 2.6, line 37, delete “21”. Insert “7”. |
| 5.1 | Delete clause 5.1. Replace with “The Contractor shall be deemed to have inspected the Site and its environs and to have informed himself of all conditions and circumstances affecting the execution of the Works and of all risks and contingencies which may affect the Contractor’s performance of its obligations”. |
| 5.2 | Delete 5.2. Replace with “The Purchaser provides no warranty in relation to the accuracy or sufficiency of any information as to the Site or its environs. No lack of knowledge on the part of the Contractor in relation to such matters shall entitle the Contractor to any adjustment of the Contract Price” |
| 5.3 | In clause 5.3, line 35, delete “The”. Insert “Save as provided in clauses 5.1 and 5.2, the”. |
| 5.7 | Delete clause 5.7. |
| 6.1 | Delete clause 6.1. |
| 6.2 | Delete clause 6.2. |
| 7.1 | Delete clause 7.1 |
| 11.2 | In clause 11.2, line 6, delete “The Purchaser”. Insert “The Contractor”. |
| 11.3 | Delete clause 11.3 |
| 11.4 | Delete clause 11.4 |
| 11.5 | Delete clause 11.5 |
| 12.1 | Delete clause 12.1. |
| 13.1 | In clause 13.1, line 2, before “due” insert “all”. In clause 13.1, line 2, after “due” insert “skill”. In clause 13.1, line 2, after “diligence” insert “and in accordance with the Specification”. |
| 13.3 | In clause 13.3, line 2, after “Specification” insert “and the Plant shall be fit for the purpose for which it is intended in every respect, and shall be suitable to provide the minimum service life, as these requirements are defined in the Specification”. In clause 13.3, line 20, after “responsibility” add “by reason of the inadequacy of such design and stating reasonable and sufficient grounds for the disclaimer”. |
| 14.1 | In clause 14.1, line 24, delete “Within the time stated in the Contract or, if no time is stated, within 30 days after the Letter of Acceptance (or, if there is no Letter of Acceptance the date of the Agreement),” and replace with “Before commencing any work in respect of the Works or the Plant”. |
| 14.5 | Delete lines 9, 10 and 11. |
| 15.1(b) | Delete “such reasonable time as the Engineer may require” and replace with “14-days or such other period as agreed in writing with the Engineer”. |
| 15.2 | Delete “without delay” and replace with “within 14-days or such other period as agreed in writing with the Engineer”. |
| 15.7 | Delete clause 15.7. Replace with “The Contractor grants to the Purchaser a perpetual, irrevocable, royalty free, exclusive licence to use all drawings and information and tools and devices, supplied by the Contractor concerning the Plant for the purposes of completing, maintaining, adjusting, repairing, replacing or changing the Works or for other operational matters”. |
| 16.2 | In clause 16.2, line 45, delete “The”. Insert “Subject to the provisions of clause 5.2 and 13.3, the”. |
| 20.1 | Add to clause 20.1 “The Contractor shall comply with its statutory duties under the Construction (Design & Management) Regulations 2015.”. |
| 21.2 | Delete clause 21.2. |
| 21.3 | In clause 21.3, delete the second sentence. In clause 21.3, line 30, delete “Purchaser” and replace with “Contractor”. In clause 21.3, line 31, delete “Contractor” and replace with “Purchaser”. In clause 21.3, delete the second paragraph. |
| 22.1 | In clause 22.1, line 47, delete all wording after “the Contractor shall bear the cost of rectifying the error” to the end of line 50. |
| 23.5 | In clause 23.5, line 38, after “Price.” insert “The Contractor will repeat such re-testing or inspection until the Engineer is satisfied the Plant is not defective and/or is in accordance with the Contract. If in the Engineer’s reasonable opinion any defect in the Plant cannot be remedied or the Plant cannot be made to accord with the Contract the Engineer may finally reject the Plant and the Contractor will remove the Plant at his own cost and repay all monies received from the Purchaser in respect of it and indemnify the Purchaser in respect of any loss, damage, cost, expense, liability of claim suffered by the Purchaser as a result of such rejection” |
| 28.5 | In clause 28.5, line 26, delete all wording after “repeat them” and replace with “. If upon a repetition of such tests the Works or any Section fails to pass test, the Engineer may direct that the Contractor take whatever steps may be necessary to enable the Works or Section to pass test and repeat the tests, or the Engineer or the Purchaser may reject the Works or Section and direct that clause 49 (Contractors Default) apply (save that such rejection and application of clause 49 shall not include any Works or Section that has been taken over pursuant to clause 29.”. |
| 31.1 | Delete clause 31.1. |
| 31.2 | Delete clause 31.2. |
| 33.1 | In clause 33.1 delete sub clause (b) and replace with “any negligence or breach of the Contract on the part of the Purchaser or Engineer or by reason of any circumstances constituting force majeure beyond the reasonable control of the Contractor;”. In clause 33.1 delete sub clauses (c) and (d). At the end of clause 33.1 add “Notwithstanding any provisions of this Agreement the Time for Completion of the Works will not be extended for any event save for those provided in this clause and clause 46.”. |
| 34.1 | In clause 34.1, line 22, delete “save as regards his obligations under clauses 35 (Performance tests) and 36 (Defects liability),”. |
| 34.2 | In clause 34.2, line 46, delete all wording after “such failure” until the end of clause 34.2. |
| 36.9 | Delete clause 36.9. |
| 36.10 | In Clause 36.10, in line 39, delete “three” and replace with “twelve”. In Clause 36.10, in line 41, delete “Contractor's” and replace with “Purchaser's”. In Clause 36.10, in line 42, delete all wording after “option”. |
| 41.2 | In clause 41.2 delete line 9, sub clause (a). |
| 43.7 | In clause 43.7, line 52, after “to the claim.” Insert “The Contractor shall conduct all such negotiations and/or litigation expeditiously”. |
| 44.3 | Delete clause 44.3 and replace with “Notwithstanding anything stated elsewhere in the Contract, the Contractor’s liability to the Purchaser under or in connection with the Contract (other than in respect of clause 44.4) for any one act, omission, default or breach of contract shall not exceed the sum stated in the Appendix.”. |
| 44.4 | Delete clause 44.4 and replace with “Notwithstanding anything to the contrary in the Contract, no limitation of liability shall apply in respect of any liability for physical damage to property and/or personal injury (including death) resulting from a negligent act or omission by either party.”. |
| 45.1(d) | In clause 45.1(d), line 17, after “Use” insert “beyond that which would be reasonably expected”. |
| 46.1 | Delete clause 46.1, sub clause (f), line 33, and replace with “national strike or strikes which substantially affect the Contractor’s ability to carry out the Works.”. |
| 46.3 | In clause 46.3, line 5, delete “120” and substitute with “30”. |
| 46.4 | In clause 46.4 delete sub clauses (c) and (e). |
| 47.5a | Add new clause 47.5a “The Contractor shall insure and shall maintain insurance against his liability under the Contract for design of the Plant (Professional Indemnity Insurance). The terms of any such insurance policy also include the provision to indemnify the Purchaser.”. |
| 49.1 | In clause 49.1, line 30, delete “21” and substitute with “14”. |
| 50.1 | In clause 50.1, at the start of line 17 insert “If the Contractor becomes insolvent within the meaning of section 113 of the Housing Grants, Construction and Regeneration Act 1996, or”. |
| 51.1(a) | In clause 51.(a), line 33, delete “7” and substitute with “14”. |
| 51.1(c) | In clause 51.1 sub clause (c) at the start of line 35 insert “becoming insolvent within the meaning of section 113 of the Housing Grants, Construction and Regeneration Act 1996, or”. |
| 51.1(d) | Delete clause 51.1 sub clause (d). |
| 51.1(g) | Insert new Clause 51.1(g) Public Contracts Regulations 2015 & Public Contracts (Scotland) Regulations 2015 Where this Contract is one to which Regulation 73(1) of the Public Contracts Regulations 2015, and/or the Public Contracts (Scotland) Regulations 2015, applies the Purchaser shall be entitled by notice to the Contractor to terminate the Contractor’s employment under this Contract where the grounds set out in Regulation 73(1)(a) or 73(1)(c) of the Regulations apply. |
| 54 | Insert new Clause 54 Anti-Bribery Requirements The Contractor shall comply with all applicable anti-bribery and anti-corruption legislation including, without limitation, the Bribery Act 2010 and any applicable European Union Directives. |
| 54.1 | Throughout the term of this Agreement the Contractor shall maintain and enforce its own policies and procedures, including adequate procedures under the Bribery Act 2010, to ensure compliance with all applicable anti-bribery and anti-corruption legislation and European Union Directives. Adequate procedures shall be determined in accordance with section 7(2) of the Bribery Act 2010 (and any guidance issued under section 9 of the Act). |
| 54.2 | The Contractor shall use all reasonable endeavours to ensure that all persons associated with the Contractor (as defined by section 8 of the Bribery Act 2010) including any subcontractors and suppliers comply with clause 54 and 54.1. |

Appendix to the Conditions of Contract MF1 Rev 6

| APPENDIX |  |  |  |
| --- | --- | --- | --- |
| Numbers refer to the General Conditions’ sub-clause numbers unless otherwise stated. |  |  |  |
| 1.1m | Engineer |  |  |
|  | The Engineer is Paul Crosbie of Tuv Sud Ltd Dunbar Boardman |  |  |
| 1.1.s | Nominator |  |  |
|  | The Nominator is The President of the Institution of Engineering and Technology |  |  |
| 1.1.v | Performance Tests |  |  |
|  | Performance Tests are not required. |  |  |
| 1.1.b | Schedules |  |  |
|  | The following Schedules form part of the Contract: |  |  |
|  | Schedule of Amendments to the MF/1 Rev 6 Contract General Conditions |  |  |
|  | Schedule of Prices |  |  |
| 1.1.c | Sections |  |  |
|  | The Works are not Divided into Sections. |  |  |
| 1.1.ee | Special Conditions |  |  |
|  | The following Special Conditions form part of the Contract: |  |  |
|  | Special Condition 2: Adjudication |  |  |
| 1.1.ll | Time for Completion |  |  |
|  | The Time for Completion of the Works means ........... (days) |  |  |
|  | (a) The date specified for commencement of the Works is ............. |  |  |
|  | (c) The following matters are conditions precedent to commencement of the Works: |  |  |
|  | Contractor to provide an adequately developed Construction Phase Plan in compliance with the requirements of Regulation 12 of the Construction (Design & Management) Regulations 2015; Provisions to be in place to meet with the requirements of Part 4 and Part 5 of the Construction (Design & Management) Regulations 2015. |  |  |
| 2.1 | Engineer’s Duties |  |  |
|  | No specific limitations |  |  |
| 4.1 | Precedence of Documents |  |  |
|  | The order of precedence of the documents forming the Contract is as follows: |  |  |
|  | - The Agreement |  |  |
|  | - National Museums Liverpool Official Purchase Order |  |  |
|  | - The Appendix |  |  |
|  | - The Special Conditions |  |  |
|  | - The General Conditions as amended by the Schedule of Amendments |  |  |
|  | - The Specification |  |  |
|  | - The drawings annexed to, or referred to in, the Contract |  |  |
|  | - The Schedules |  |  |
|  | - The Tender |  |  |
| 5.5 | Prime Cost Items |  |  |
|  | Percentage to be added: 10% |  |  |
| 6.2 | Labour, Materials & Transport |  |  |
|  | Sub-clause 6.2 of the General Conditions shall not apply |  |  |
| 8.1 | Provision of Bond or Guarantee |  |  |
|  | Form of Bond |  |  |
|  | Retention Bond |  |  |
|  | Bond Amount % of Contract Price |  |  |
|  | Period of Validity – 12 months following taking over |  |  |
|  | Currency of Bond UK Pounds Sterling |  |  |
|  | Arrangements for Release On Demand |  |  |
|  | Governing Law: is the Law of England & Wales |  |  |
| 10 | Notices |  |  |
|  | Purchaser’s contact details are: |  |  |
|  | Address: National Museums Liverpool 127 Dale Street, Liverpool L2 2JH |  |  |
|  | Facsimile No: 0151-478-4740 |  |  |
|  | E-mail address: mike.collins@liverpoolmuseums.org.uk |  |  |
|  | Engineer’s Contact details are: |  |  |
|  | Address: TUV-SUD Dunbar Boardman, Suite D, Chadwick House, Birchwood Park, Warrington WA3 6AE |  |  |
|  | Facsimile No: 01925-823330 |  |  |
|  | E-mail address: Paul.Crosbie@tuv-sud.co.uk |  |  |
|  | Contractor’s contact details are: |  |  |
|  | Address: [The Successful Lift Contractor] |  |  |
|  | Facsimile No: |  |  |
|  | E-mail address: |  |  |
| 11.5 | Purchaser’s Lifting Equipment |  |  |
|  | The following lifting equipment belonging to the Purchaser may be used by the Contractor in connection with the Works: |  |  |
|  | Existing lifting beams may be used by the Contractor. The Contractor shall be responsible for testing, certifying and operating any Lifting Beams that are provided by the Purchaser and shall be responsible for supplying, testing certifying, operating and maintaining all other lifting equipment and scaffolding required in connection with the Works. |  |  |
| 11.6 | Utilities and Power |  |  |
|  | Utilities available for use by the Contractor on Site are as follows: |  |  |
|  | Utilities available for use by the Contractor on Site include all power outlets as generally available within the lift machine room and lift shaft. The Contractor is to make his own arrangements for any special equipment. Access to welfare facilities in a designated area will be provide to the Contractor on the basis that the Contractor shall be responsible for maintaining these in acceptable condition to the satisfaction of the Purchaser and/or the Engineer. |  |  |
| 11.7 | Power, etc, for tests on site |  |  |
|  | The following items will not be provided by the Purchaser: |  |  |
|  | The Contractor will be allowed free use of electrical power for commissioning and testing of the lift and this is the full extent of the Purchaser’s responsibility. The Contractor shall be responsible for providing all necessary equipment, including meters, instruments, tools, test-loads, etc as may be required to carry out the tests in accordance with the Engineer’s requirements. |  |  |
|  | Use of the following items will be charged to the Contractor: |  |  |
|  | Not applicable |  |  |
| 14.2 | Form of Programme |  |  |
|  | The Programme shall be in the following form: |  |  |
|  | The programme shall be provided and maintained such that all items of work contained within sections 10.5 and 10.6 of the Specification, including the date of possession/completion, shall be itemised and presented in the form of a bar chart. |  |  |
| 18.2 | Site services |  |  |
|  | The rates for Site services apparatus provided by the Purchaser are: |  |  |
|  | To be charged at an agreed fixed price or rate as applicable if and when required. |  |  |
| 28.1 | Notice of tests |  |  |
|  | The Contractor shall Test the completed Works, and satisfy himself of the compliance of these with the Specification, prior to offering these to the Engineer for witness testing. |  |  |
| 34.1 | Delay in completion |  |  |
|  | Percentage of the Contract Value to be paid or deducted for each week of delay to the completion of the whole of the Works 2% |  |  |
|  | Maximum percentage of Contract Value which payments or deductions shall not exceed 10%. |  |  |
| 34.2 | Prolonged delay |  |  |
|  | Maximum loss recoverable by the Purchaser: No sum stated. |  |  |
| 36.1 | Defects after taking-over |  |  |
|  | The Defects Liability Period shall be 24 months after taking over. |  |  |
| 36.3 | Notice of Defects |  |  |
|  | The Defects Liability Period in respect of any repair or replacement shall not extend beyond 36 months from the date of taking-over under clause 29 (Taking-over). |  |  |
| 39.1 | Payment by instalments |  |  |
|  | The Contractor is entitled to the following milestone payments on achieving the corresponding milestone deliverables: |  |  |
|  | Milestone deliverable |  | Milestone Payment |
|  | Accepted drawings |  | 10% |
|  | Consolidated delivery of the Lift equipment to Site |  | 50% |
|  | Installation works |  | 40% (By monthly valuation) |
|  | The Contractor is entitled to monthly payments in respect of: |  |  |
|  | - The value of the work executed on Site, and |  |  |
|  | - The value of Plant delivered to the Site, |  |  |
| 39.2 | Time for application |  |  |
|  | - Time for applications for interim certificates of payment |  |  |
|  | Applications for interim payments shall be made on or after the date that the relevant milestone deliverable has been achieved. |  |  |
|  | If the whole or any part of the Works have been suspended pursuant to sub-clause 25.1 (Suspension of work, delivery or installation), application for interim payment certificates shall be made on or after the 28th day of each month in relation to the Works affected by the suspension until the suspension is lifted, the suspended Works are omitted or the Contract is terminated. |  |  |
|  | Applications for interim payment certificates shall be made on or after the 28th day of each month. |  |  |
| 39.2 | Form of application |  |  |
|  | (a) Documentation to accompany applications for a certificate of payment |  |  |
|  | (i) Evidence required of the value of work done on the Site: |  |  |
|  | Contractor’s updated programme and verification of work completed by way of inspection of the Works by the Engineer. |  |  |
|  | (ii) Evidence required for Plant delivered to the Site: |  |  |
|  | Contractor’s updated materials delivery schedule and verification of the materials on Site by way of inspection of these by the Engineer. |  |  |
|  | Milestone Deliverable | Evidence required to demonstrate milestone deliverable has been achieved |  |
|  | Accepted drawings | Written acceptance of the drawings by the Engineer |  |
|  | Delivery of the Lift Equipment to Site | Contractor’s materials delivery schedule verified & confirmed in writing by the Engineer |  |
|  | Installation works | Monthly valuation by the Engineer & confirmed in writing |  |
| 39.5 | Final date for payment |  |  |
|  | The Final Date is 30 days after the due date. |  |  |
| 40.4 | Delayed payment |  |  |
|  | The rate of interest on overdue payment shall be 2% above the Bank of England Base Rate in force from time to time during the period of delay. |  |  |
| 40.6 | Advance payment |  |  |
|  | Advance payment does not apply. |  |  |
| 40.7 | Currencies of payment |  |  |
|  | The Contract Price (including any adjustments) shall be paid in the following currencies: |  |  |
|  | UK Pounds Sterling |  |  |
| 40.8 | Taxes |  |  |
|  | The Purchaser is responsible for the following taxes: |  |  |
|  | Value Added Tax |  |  |
| 41.2 | Allowance for profit on claims |  |  |
|  | Percentage to be added 0% (Nil) |  |  |
| 44.3 | Limitation of Contractor’s Liability |  |  |
|  | Limit of liability: Contract Value plus 10% |  |  |
| 47.4 | Third party insurance |  |  |
|  | The Contractor shall effect third party insurance for a minimum amount of £10,000,000.00 Ten Million Pounds for any one claim or series of claims arising from the same incident. The Contractor shall effect employer’s liability insurance for a minimum amount of £10,000,000.00 (Ten Million Pounds) for any one claim or series of claims arising from the same incident. |  |  |
| 52.1 | Arbitration |  |  |
|  | - The arbitration rules are those of the Chartered Institute of Arbitrators. |  |  |
|  | - The seat of the arbitration is England. |  |  |
| 52.4 | Adjudication |  |  |
|  | (c) The adjudication rules are those set out in the Scheme for Construction Contracts made in accordance with the provisions of section 114 of the Housing Grants, Construction and Regeneration Act 1996. |  |  |
| 53.1 | Applicable law |  |  |
|  | The substantive law of the Contract is the law of England & Wales. |  |  |

2.2 	Preliminaries

Description of the Works and Purpose of the Plant

The intent of the Specification is that the Plant and/or the Works shall be designed, manufactured, supplied, installed and constructed such as to be fit for the purpose of providing Passenger Lift service in compliance with BS EN81-20 and BS EN81-50 requirements; the Lifts Regulations 2016; EU Lifts Directive 2014/33/EU; Fire Recall Service to BS EN81-73 requirements;

The Plant shall have a minimum service life of not less than 25-years commencing from Taking Over by the Purchaser.

Definition of Terms

Purchaser			National Museums Liverpool

Main Contractor	Appointed Lift Contractor

Contract Administrator	TUV-SUD Dunbar Boardman

Engineer			TUV-SUD Dunbar Boardman

Lift Consultant			TUV-SUD Dunbar Boardman

Contractor			Appointed Lift Contractor

Principal Designer		TUV-SUD Dunbar Boardman

Principal Contractor		Appointed Lift Contractor

Programme

The Lift Contractor is required to confirm in writing the Production Schedule and Schedule of Site works, in Section 10 of the Specification and the dates for possession and completion as set out in the Conditions of Contract.

The Lift Contractor shall be responsible for the complete programming of all sub-contractors and service boards (water, gas, electricity, etc) before and during the work on site. The Lift Contractor shall also be responsible for organising meetings, as and when necessary, with the various sub-contractors and service boards.

The Lift Contractor shall provide, within 4 weeks of appointment, a detailed bar chart programme for both off-site and on-site works showing the items detailed in the Production Schedule and Schedule of Site Works contained in Section 10 of this Specification.  This shall be updated throughout the Works, as a progress report, at the frequency required by the Engineer.

Site Conditions

The site is situated at Albert Dock, Liverpool L3 4AQ. Access to the site will be via the staff entrance.

Site Storage

Provision of one 20’ x 8’ container is to be included within the contractors’ costs. The location of this will be agreed at the pre-start meeting.

Car Parking

Parking for one vehicle will be provided within the vicinity of the building.

Site Management Costs

The Lift Contractor shall provide for all on-site and off-site management costs including the cost for the Foreman in Charge.

The CDM 2015 Regulation requires that a Principal Contractor take responsibility for managing the Site Works.

For the avoidance of doubt, the Lift Contractor shall undertake the role and duties of Principal Contractor, and is expected to fulfil those duties applying the requirements of CDM 2015 which, based on the scope and complexity of the work, may require a full-time managerial presence on site.  In this respect the Lift Contractor must ensure that one of his senior employees acts as an on-site Supervisor/Manager, particularly when wholly Sub-contract labour is employed.

The Lift Contractor shall include for site management costs in relation to the requirements of the CDM 2015 Regulation together with the provisions of this Specification.

Labour on-cost

The Lift Contractor shall provide for all on-costs in respect of all workmen in relation to disbursements arising from the employment of labour.

Hours of Work

The hours of work will be as shown on the Schedule of Site Works incorporated into the Contract.  No additional working hours will be allowed except by agreement of the Engineer.

Daywork

The Lift Contractor shall obtain the Engineer’s approval prior to the commencement of any work which is to be executed on a daywork basis, or which the Lift Contractor considers should be paid for on a daywork basis. The Lift Contractor shall submit proper daywork sheets signed by the General Foreman specifying the time daily spent upon the daywork and the workmen’s names and the materials employed. The daywork sheets shall be delivered to the Engineer or his Authorised Representative not later than the end of the week following that in which the daywork has been executed.

Acceptance of daywork sheets will imply agreement only of the record of the hours worked and materials used and shall not thereby be considered to authorise payment for the work on a daywork basis. Payments for daywork shall be made in accordance with the relevant provision of the Contract.

The Engineer shall be entitled to amend the amount of time and/or materials shown in such daywork sheets if, in his opinion, such amount exceeds that which should reasonably have been expended in producing the result, the Engineer having regard to the circumstances and to the Lift Contractor’s obligations under the Conditions of Contract to proceed with the work in a regular and diligent manner.

Sub Contractors

The Lift Contractor is required to enter into Contracts with all Sub-contractors paid through him such as to bind the Sub-contractors to the same obligations and benefits in respect of the Sub-contract as those for which the Contractor is liable in respect of this Contract.

Working Rule Agreement: Declaration of Intent

The Lift Contractor or any Sub-contractor, whether nominated by the Purchaser or not, shall not employ in or upon the Works or any part thereof, any labour-only sub-contractor, other than in accordance with the National Working Rule settled by the National Joint Council for the Building Industry.

For the purpose of this Clause, a ‘labour-only sub-contractor’ shall mean any Sub-contractor undertaking to execute any part of the Works on terms that the materials and/or equipment and plant needed or used by such Sub-contractor shall be supplied or paid for directly by the Purchaser or Lift Contractor.

The Lift Contractor shall, if so required, produce evidence to the satisfaction of the Purchaser that any particular Sub-contractor for the time being or formerly employed on the Works is or was not a labour-only Sub-contractor employed, other than in accordance with the said National Working Rules at the time of such employment and, if in any specific case the Purchaser shall not be so satisfied, then the Purchaser shall be entitled to determine the Lift Contractor's employment, notwithstanding that the Lift Contractor may have ceased to employ such Sub-contractor on the Works.

If the Purchaser should determine the Lift Contractor’s employment under this Contract as aforesaid, then the Purchaser shall be entitled forthwith to enter upon the site of the Works and take possession thereof of all plant, tackle and materials thereon and complete the Works or have them completed by some other contractor and, all loss and extra expense which the Purchaser may suffer, incur or be put to, shall be borne by the Lift Contractor and may be deducted from any moneys due to him or may be recovered by legal process.

Incentive & Bonus Payments

The Lift Contractor is to note particularly, that should any change in the rates of wages and other emoluments and expenses payable to work people by a decision of the National Joint Council for the Building Industry or other body have in any way the effect of increasing the incentive and/or bonus payments, then such increase will not be allowed as an addition to this Contract.

Sample & Other Testing

The Lift Contractor shall provide samples, as the Engineer may require, of any or all materials and workmanship to be used on the Works.

The Lift Contractor shall bear the cost of providing samples and any testing of such samples of material which the Engineer may direct the Lift Contractor to arrange to be undertaken.

Any material or equipment which fails to meet the tests applied shall be replaced, “free of charge”, by the Lift Contractor, using a suitable alternative material or equipment which has first been approved by the Engineer.

Tolerances in Construction

The Lift Contractor is responsible for the co-ordination of tolerances (whether manufacturing or workmanship, including nominated sub-contractors and nominated suppliers) between different materials or components of the building.

Claims attributed to varying tolerances between materials and components will not be considered.

Drawings & Dimensions

Wherever dimensions are marked on drawings or described such dimensions are to be considered as correct. In the case of discrepancy between drawings and any existing site measurement this shall be referred to the Engineer whose decision will be final.

Trade Names

Where in the Specification a particular firm or product is specified, the Lift Contractor must use such firm or product.  Where in the Specification a choice of more than one firm or product is permitted for any particular item, then the Lift Contractor shall use the particular firm or product upon which he has based his Tender.

If the Specification permits an equivalent to a named product or firm then the Lift Contractor, should he elect to supply or use the equivalent, will be required to confirm that a full stock of relevant spares will be readily and promptly available at his local branch or depot.  These spares must be made available to the Purchaser’s maintaining contractor throughout the anticipated life of the installation, as declared in the summary of Technical and Constructional Details.

If the Lift Contractor wishes to substitute an alternative firm or product he must submit a written request to the Engineer enclosing samples and indicating the financial effect of his proposed change.

The Lift Contractor will not be allowed to proceed with any substitution until samples are approved, financial adjustment agreed, and the written approval of the Engineer has been given.

Abbreviations

The following abbreviations have been used:

BS	British Standards Specification

BSI	British Standards Institute

dBA	Decibels

FFL	Finished floor level

kg	kilograms

kW	kilowatts

m	metres

mA	milliamps

mg	millig

mm	millimetres

No.	Number

SWG	Standard Wire Gauge (Imperial)

Advertisements & Signboard

The Lift Contractor shall not, without first obtaining the permission of the Engineer, utilise or use any information and/or material from this Contract for advertising in such a manner that the building or project may be readily identified.  Within the site and its environs no display of signboards will be permitted without prior written agreement of the Engineer.

Work Covered Up

The Lift Contractor must give due notice to the Engineer when any work or material is intended to be covered up. In default thereof the work and/or material shall be uncovered at the Lift Contractor’s expense.

Warranty

The Lift Contractor shall Warrant that he has exercised, and will exercise, all proper skill and care in the design of the Works and in the selection of materials and goods, so far as the Works have been, or will be, designed by him, and so far as such materials or goods have been, or will be, selected by him.

In addition the Lift Contractor shall comply with, and satisfy any Performance Specification or requirement included in, or referred to in, his Tender as part of the Description of the Works.

Defects Liability Period

Will be for a period of 24 months commencing upon issue of the Taking Over Certificate for the second lift. Refer to Section 9 of this Specification in relation to details of maintenance requirements.

Site Waste Management

The Lift Contractor shall, if and when required, produce a Site Waste Management Plan (SWMP) PRIOR to commencement of the Works.

The Lift Contractor shall adopt the Purchaser’s SWMP and ensure compliance with the Environmental Protection Act 1990 (EPA) and the CDM Regulations 2015.

## QUALITY AND TOLERANCES

Guide Rails

Guide rails of the highest available standard and quality shall be installed such as to achieve the performance criteria laid down in Section 10.

The guide rails shall be plumb to + 3mm in verticality and + 2mm in distance between guide rails.

The Lift Contractor is required to demonstrate accuracy of alignment as part of the Witness Test as detailed in Section 8 of this Specification.

Regulations and Quality of Work

The Lift Contractor should refer to the Tender Documentation and the relevant clauses within this Specification.

The completed installation shall comply, in all respects, with the provisions of the latest editions of the following British Standards, including Draft Standards as follows:-

- BS476	Fire tests on building materials

- BS5499	Fire safety signs

- BS5655	Lifts & Service Lifts Parts 1 – 14 inclusive, where relevant

- BS7255	Safe Working on Lifts

- BS7671	The IET Wiring Regulations

- BS7980	Vehicle Lifts – Installation, maintenance, thorough examination and safe use – Code of practice

- BS8300	Design of Buildings to meet the needs of the Disabled

- BS8486-1 & -2	Examination & Test of New Lifts before putting into service. Specification for means of determining compliance with BS EN81

- BS9999	Fire Safety in the Design and Use of Buildings

- BS EN81-1	Electric Lifts

- BS EN81-2	Hydraulic Lifts

- BS EN81-3	Electric & Hydraulic Service Lifts

- BS EN81-21	New Passenger & Goods Passenger Lifts in Existing Buildings

- BS EN81-22	Electric Lifts with Incline Path

- BS EN81-31	Accessible Goods Only Lifts

- BS EN81-40	Stairlifts & Inclined Lifting Platforms Intended for Use by Persons with Impaired Mobility

- BS EN81-41	Vertical Lifting Platforms Intended for Use by Persons with Impaired Mobility

- BS EN 81-20 	Lifts for the Transport of Persons & Goods – Part 20: Passenger and Goods Passenger Lifts

- BS EN 81-28	Remote Alarm on Passenger & Goods Passenger Lifts

- BS EN 81-50	Examinations & Tests – Part 50: Design Rules, Calculations, Examinations & Tests of Lift Components

- BS EN 81-58	Examinations & Tests – Part 58: Landing Door Fire Resistance Test

- BS EN81-70		Disabled Persons Accessibility

- BS EN81-71		Vandal Resistant Lifts

- BS EN81-72		Firefighting Lifts

- BS EN81-73		Behaviour of Lifts in the Event of Fire

- BS EN81-77		Lifts Subject to Seismic Conditions

- BSEN81-80	Improvement of Safety of Existing Passenger & Goods Lifts

- BS EN81-82	Improvement of Accessibility of Existing Lifts for Persons Including Persons with Disability

- DD CEN/TS81-83	Existing Lifts. Rules for the Improvement of Resistance Against Vandalism

- BS EN ISO14798	Risk Assessment & Reduction Methodology

- BS8899	Code of Practice – Improvement of Firefighting & Evacuation Provisions in Existing Lifts

- PD ISO/TS18870	Requirements for Lifts Used to Assist in Building Evacuation

- DD CEN/TS81-76	Evacuation of Disabled Persons Using Lifts

- BS ISO22201	Programmable Electronic Systems in Safety Related Applications (All Parts)

- BS EN ISO25745	Energy Performance of Lifts, Escalators & Moving Walks (All Parts)

- EN131-2	Ladders – Requirements, Testing, Marking

- EN14122-1-4	Permanent Means of Access to Machinery: Parts 1 to 4

- BS ISO4190	Lift (Elevator) Installation (All Parts)

- EN1570-1	Lifting Tables Serving Up to Two Levels

- BS EN ISO14120	General Requirements for the Design & Construction of Fixed & Moveable Guards

- EN1993-1-1	Eurocode 3 – Design of Steel Structures – Part 1-1: General Rules and Rules for Buildings

- EN10305-1	Steel Tubes for Precision Applications – Technical Delivery Conditions – Part 1: Seamless Cold Drawn Tubes

- EN10305-2	Steel Tubes for Precision Applications – Technical Delivery Conditions – Part 2: Welded Cold Drawn Tubes

- EN10305-3	Steel Tubes for Precision Applications – Technical Delivery Conditions – Part 3: Welded Cold Sized Tubes

- EN10305-4	Steel Tubes for Precision Applications – Technical Delivery Conditions – Part 4: Seamless Cold Drawn Tubes for Hydraulic & Pneumatic Power Systems

- EN10305-5	Steel Tubes for Precision Applications – Technical Delivery Conditions – Part 5: Welded Cold Sized Square & Rectangular Tubes

- EN10305-6	Steel Tubes for Precision Applications – Technical Delivery Conditions – Part 6: Welded Cold Drawn Tubes for Hydraulic & Pneumatic Power Systems

- BS EN12015	Electromagnetic Compatibility - Product Family Standard for Lifts, Escalators & Moving Walks – Emission

- BS EN12016	Electromagnetic Compatibility - Product Family Standard for Lifts, Escalators & Moving Walks – Immunity

- EN125385-5	Steel Wire Ropes – Safety – Stranded Ropes for Lifts

- EN12600	Glass in Building – Pendulum Test – Impact Test Method & Classification for Flat Glass

- BS EN13015	Maintenance for Lifts & Escalators – Rules for Maintenance Instructions

- EN13501-1	Fire Classification of Construction Products & Building Elements – Part 1: Classification Using Data from Reaction to Fire Tests

- EN50205	Relays with Forcibly Guided (mechanically linked) Contacts

- EN50214	Flat Polyvinyl Chloride Sheathed Flexible Cables

- EN50274	Low-voltage Switchgear & Controlgear Assemblies – Protection Against Electric Shock – Protection Against Unintentional Direct Contact with Hazardous Live Parts

- EN60204-1	Safety of Machinery – Electrical Equipment of Machines – Part 1: General Requirements

- EN60529	Degrees of Protection Provided by Enclosures

- EN10025 (all parts)	Hot Rolled Products of Non-alloy Structural Steels – Technical Delivery Conditions

- EN12385-5	Steel Wire Ropes – Safety - Part 5: Stranded Ropes for Lifts

- EN60068-2-6 	Environmental Testing – Part 2: Tests – Test Fc: Vibration (Sinusoidal)

- EN60068-2-14 	Environmental Testing – Part 14: Tests – Test N.  Change of Temperature

- EN60068-2-27	Environmental Testing – Part 2-27: Tests – Test Ea & Guidance:  Shock

- EN60112	Method for the determination of the proof & the Comparative Tracking Indices of Solid Insulating Materials

- EN 60664-1	Insulation Coordination for Equipment within Low-voltage Systems – Part 1:  Principles, Requirements & Tests

- EN 60947-4-1	Low-voltage Switchgear & Controlgear – Part 4-1: Contactors & Motor-starters- Electromechanical Contactors & Motor-starters

- EN 60947-5-1	Low-voltage Switchgear & Controlgear – Part 5-1: Control Circuit Devices & Switching Elements – Electromechanical Control Circuit Devices

- EN61508-1	Functional Safety of Electrical/Electronic/Programmable electronic Safety-related Systems – Part 1: General Requirements

- EN61508-2	Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related Systems – Part 2: Electrical/Electronic/Programmable Electronic Safety-related Systems

- EN61508-3	Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related systems – Part 3: Software Requirements

- EN61508-7	Functional Safety of Electrical/Electronic/Programmable Electronic Safety-related Systems – Part 7: Overview of Techniques and Measures

- EN ISO 12100	Safety of Machinery – General principles for design – Risk assessment & risk reduction

- EN60664-1	Insulation Coordination for Equipment within Low-voltage Systems – Part 1: Principles Requirements & Tests

- EN60947-4-1	Low-voltage Switchgear and Controlgear – Part 4: Contactors & Motor-starters – Section 1: Electromechanical Contactors and Motor-starters

- EN60947-5-1	Low-voltage Switchgear & Controlgear – Part 5-1: Control Circuit Devices & Switching Elements – Electromechanical Control Circuit devices

- EN60947-5-5	Low-voltage Switchgear & Controlgear – Part 5-5: Control Circuit Devices & Switching Elements – Electrical Emergency Stop Device with Mechanical Latching Function

- EN61310-3	Safety of Machinery – Indication, Marking & Actuation – Requirements for the Location & Operation of Actuators

- EN61800-5-2	Adjustable Speed Electrical Power Drive Systems – Part 2: Safety Requirements. Functional

- EN61810-1	Electromechanical Elementary Relays – Part 1: General Requirements

- EN ISO12100	Safety of Machinery – General Principles for Design – Risk Assessment & Risk Reduction

- EN ISO13857	Safety of Machinery – Safety Distances to Prevent Danger Zones Being Reached by the Upper & Lower Limbs

- HD60364-4-41	Low-voltage Electrical Installations – Part 4-41: Protection for Safety – Protection Against Electrical Shock

- HD60364-4-42	Low-voltage Electrical Installations – Part 4-42: Protection for Safety – Protection Against Thermal Effects

- HD60364-6	Low-voltage Electrical Installations – Part 6: Verification

- IEC60227-6	Polyvinyl Chloride Insulated Cables of Rated Voltages up to & Including 450/750 V – Part 6: Lift Cables and Cables for Flexible Connections

- IEC60245-5	Rubber Insulated Cables – Rated Voltages up to and Including 450/750 V – Part 5: Lift Cables

- IEC60417	Database – Graphical symbols for Use on Equipment

- IEC60617	Graphical Symbols for Diagrams

- ISO1219-1	Fluid Power Systems and Components – Graphic Symbols and Circuit Diagrams – Part 1: Graphic Symbols for Conventional Use & Data-processing Applications

- BS EN1493		Vehicle Lifts

- BS EN12015&16	Electro Magnetic Compatibility

- BS EN12385-4&-5	Steel Wire Ropes

- BS EN13015		Maintenance for Lifts and Escalators

- BS EN60332-1&-2	Tests on Electric Cables under Fire Conditions

- BS EN ISO13857	Safety of Machinery: Safety Distances

- BS EN ISO16032	Acoustics – Measurement of Sound Pressure Levels from Service Equipment in Buildings

- BS ISO18738	Measurement of Lift Ride Quality

- DD222	Specification for Rack & Pinion Lifts

The Works shall comply with the following Acts, Regulations and Working Rules:

- The Construction (Lifting Operations) Regulations

- The Construction (General Conditions) Regulations

- The Construction (Health & Safety) Regulations

- The Construction (Work in Places) Regulations

- The Construction Products Regulations

- The Factories Act and all amendments thereto

- Health & Safety at Work Act

- The Electricity at Work Act

- The Management of Health & Safety at Work Regulations 1999

- The Provision and Use of Work Equipment Regulations 1998

- The Work Place (Health, Safety & Welfare) Regulations 1992

- The Construction (Design & Management) Regulations 2015

- The Reporting of Injuries, Diseases and Dangerous Occurrences Regulations

- The Supply of Machinery (Safety) Regulations 2008

- The Lifts Regulations 1997

- The Lifts Regulations 2016

- EU Lifts Directive 95/16/EC

- EU Lifts Directive 2014/33/EU

- The Lifting Operations and Lifting Equipment Regulations 1998

- The Building Regulations Part M2 and subsequent updates

- The Health & Safety (First-Aid) Regulations 1981

- The Work at Height Regulations 2005

- The Control of Noise at Work Regulations 2005

- The Control of Asbestos Regulations 2012

- The Waste Electrical and Electronic Equipment Regulations 2006

- The Site Waste Management Plans Regulations 2008

- The Equality Act 2010

- NHS Health Technical Memorandum HTM08-02 Lifts 2016

Site Inspection

The Lift Contractor shall be deemed to have satisfied himself as to the local conditions with regard to accessibility of the site; as to the full extent and nature of the Works; as to the supply of and conditions affecting labour; as to provisions for messing, toilets, carriage, cartage, unloading, tools, accommodations, scaffolding, hoisting, cranage, ladders, and anything other which may influence his Tender or his carrying out of the Works.

Component Life

All major components, including but not limited to, contactors, relays, push units, indicators, call-accepted indicators, door operators, door interlocks, shaft switches and associated equipment, components and materials shall have been type tested to a minimum of 1 million operations.

The Lift Contractor shall state the expected life of solid-state components.

Retention Bond

Prior to the commencement of the Works the Lift Contractor shall provide a Retention Bond in favour of the Purchaser to the value of 5% of the Contract Value. The Retention Bond shall be valid for the duration of the Works, and shall reduce to 2½% of the Contract Value for the duration of the Defects Liability Period.

The Form of Bond shall be that set out at Section 2 of this Specification.

Refurbishment Notice

The Lift Contractor shall include in his Tender costs for the provision of two Notice/Sample Boards which will illustrate, by means of a colour perspective detail drawing of the lift car interiors, and samples of materials, finishes and fixtures, along with a brief description of the Works including approximate time scales.

The Lift Contractor shall site these boards in a location within the site which is agreed with the Purchaser. Dimensions and format of boards to be agreed with the Purchaser.

.

CDM REGULATIONS

SECTION 3

CDM 2015 REGULATIONS

PRE CONSTRUCTION INFORMATION

3.	PRE-TENDER CONSTRUCTION INFORMATION

Construction (Design and Management) Regulations

3.1	DESCRIPTION OF PROJECT

General

The Project will be undertaken in accordance with the Construction (Design & Management) Regulations 2015.

The Lift Contractor will be expected to fulfil the duties of the Principal Contractor as set out in the CDM Regulations 2015 and associated HSE Guidance.  The attention of the Lift Contractor is drawn to the requirements arising under Regulations 8, 9, 10, 11, 12, 13, 14, 15 and Part 4 of the Regulations.

The Lift Contractor shall not commence any construction work until he has developed the Construction Phase Health & Safety Plan in accordance with the requirements of Regulation 12.  The completed plan shall be issued to the Principal Designer in sufficient time to allow for comment prior to commencement of the works.

The Lift Contractor shall ensure that all direct appointments that he may make in his capacity as Main Contractor or Construction Manager include provisions for the compliance of his trade or sub-contractors, suppliers and Designers with the relevant provisions of the CDM Regulations.

Preconstruction Phase Health & Safety

Client: National Museums Liverpool

Address: 127 Dale Street, Liverpool L2 2JH

Principal Designer & Engineer		TUV-SUD Dunbar Boardman

Location of Works: Merseyside Maritime Museum

Provide for all costs incurred by complying with and implementing statutory obligations in respect of Safety, Health and Welfare Regulations, including the Construction (Design & Management) Regulations 2015 appertaining to all personnel (including those employed by nominated sub-contractors) whose duties require them to be on the site.

The Lift Contractor shall cooperate with the Principal Designer and other Designers and Contractors, including the prompt provision of design and other information, and information required for the Health & Safety File, such as to meet the duties of Principal Contractor arising under the CDM 2015 Regulations.

The Project

The Project comprises the removal of the two existing hydraulic passenger lifts and the design, supply and installation of two new machine roomless design passenger lifts within the existing lift shafts including all associated Builders & Electrical Works.

The Project will also include additional items required in order to bring the lifts into line with current British Standards and Regulations.

The Existing Environment

The property is a large Maritime Museum which provides public gallery space and a restaurant located over six floors. The building is served by two passenger lifts which both serve all floors.

The lift equipment in part is coming to the end of its useful life and has been assessed for  replacement to bring this more in line with current standards and ensure future reliability and life expectancy.

During the course of the Works it is not anticipated that any other Contractors will require access to the lift other than those under this Contract.  The Lift Contractor shall be responsible for securing the work area and maintaining a Permit to Work system.

The building will remain fully operational during the course of the Works and the appointed Lift Contractor (including any appointed sub-contractors) must adhere to all Health & Safety procedures associated with undertaking this type of work in an occupied environment.

The Design

The Design of the Works is detailed elsewhere within this Specification.

The principle of the Design is to achieve, as far as is practicable, lift installations in accordance with current British Standards, the health and safety provisions contained within those Standards, current Regulation and the general requirements of the Health & Safety at Work Act 1974, together with all of the provisions of this Specification.

The Lift Contractor shall record and highlight on the construction drawings, including appropriate detail, all significant hazards and risks associated with the construction works which have not been eliminated and/or adequately mitigated in the Design of the Works.

The Lift Contractor shall record details of any significant residual hazards and risks affecting the Works and the Design, which could not be eliminated and/or adequately mitigated in the Design, on the final “as fitted” record drawings and in the H&S File.

The existing lift shafts have reduced clearances to the pits and the headroom which cannot be altered and therefore the design of the installation will need to accommodate these.

Construction Materials

The components and materials will include electrical and mechanical elements and construction materials which have been designed and manufactured to ensure reliable performance and service life and to minimise or eliminate risks.

The removal of any combustible or hazardous material will require that the necessary Health & Safety precautions be applied, as detailed in the COSHH Regulations.

Before any dismantling of machines is undertaken redundant mineral oil is to be removed into sealed containers which are designed, constructed and labelled in accordance with the COSHH Regulations.

All new materials and components utilised in the Works are to be properly designed and manufactured to suit their purpose and capable of providing reliable operation throughout the Service Life.  Where materials are detailed in the Specification the Lift Contractor shall utilise these or, if permitted and agreed in writing, approved equivalent alternatives.

Redundant materials shall become the property of the Lift Contractor to dispose of in a responsible manner taking due regard of applicable legislation and codes. These are to be removed from site expeditiously to an approved disposal site. The accumulation of rubbish/debris is not permissible except in designated storage areas, and then only if properly bagged and labelled. The Lift Contractor shall incorporate evidence of correct disposal which is to be retained within the H&S File.

All new materials are to be delivered as required and stored in approved storage areas, and shall be protected such as to prevent damage, and to protect persons from injury.

Site Waste Management

The Lift Contractor shall, if and when required, produce a Site Waste Management Plan (SWMP) PRIOR to commencement of construction works.

The Lift Contractor shall adopt the SWMP and ensure compliance with the Environmental Protection Act 1990 (EPA), the Site Waste Management Plans Regulations 2008 and the CDM Regulations 2015.

- Suitability of Material and Products

The Lift Contractor shall use materials and products which:

- Are new unless specified otherwise

- Are suitable for the services and conditions of use normally expected to apply after the installation is complete.

- Are able to withstand the testing and commissioning conditions specified.

- Do not initiate mould growth, support vermin, contain animal hair, contain crocidolite or support bacterial life.

- Do not involve the use of CFC’s at any stage of manufacture, installation or subsequent operation except where specified.

- Are free from objectionable odours of the maximum or normal working conditions of operation.

- Do not suffer deterioration at the maximum or specified conditions of operation.

- Are capable of being applied to a base surface without causing damage or deterioration of the base.

- Are not a fire hazard, and do not evolve dense or toxic fumes when subjected to excessive heat, such as a fire.

- When of similar type, are made by the same manufacture.

- Are, where applicable, in compliance with the provisions of the Construction Products Regulation 2013.

- Whenever possible ensure products are manufactured and/or stocked under one of the following;

BSI Kite Mark Scheme

BSE Safety Mark Scheme

from Firms of Assessed Capability to BS ISO 9000

from Stockists of Assessed Capability to BS ISO 9000

Deleterious Materials

No materials generally known to be deleterious are to be used in, or incorporated into, any temporary or permanent Works forming part of the Project.

In particular none of the following items are to be used

- Asbestos or asbestos based products

- Urea formaldehyde or materials which may release formaldehyde in quantities which may be hazardous with reference to the limits set by the HSE

- Material containing fibres less than three microns diameter or 200 microns long

- Lead or any material or product containing lead which may be ingested, inhaled or absorbed

- Polychlorinated biphenyl

- Fibres not sealed or otherwise stabilised to ensure that migration is prevented

- Vermiculite containing fibrous dust

- Polytetrafluoroethylene (IPTFE) except for pipe work jointing

- Calcium silicate bricks or materials

Or, any other products or materials, which are generally known within the Building Industry to be deleterious or hazardous to health or safety or to the durability of the property in the circumstances in which they are used.

- High alumina cement and/or concrete

- Wood wool slabs used as permanent shuttering

- Calcium chloride in admixtures for use in reinforced concrete

- Sea-dredged aggregates for use in reinforce concrete which do not comply with current British Standards

- Aggregates for use in concrete which do not comply with current British Standards

- Alkali reactive aggregates

The Lift Contractor shall check with the manufacturers and/or suppliers of products and materials in order to ensure that any product does not contain such material.  Any products and/or materials found to contravene this requirement shall be removed and replaced by the Lift Contractor at his own expense.

Anticipated Target Programme/Key Dates

The programme will be agreed between the Lift Contractor and the Purchaser in order to minimise inconvenience. It is anticipated that the Works will be completed in two consecutive phases.

The Lift Contractor shall confirm with his Tender the best possible material procurement/delivery periods and installation times which he is able to achieve.

It is anticipated that the following key dates should be achievable:

| Tender Advertised | 16.11.17 |
| --- | --- |
| Site Visits | 20/11/17 to 24/11/17h between 8am and 11am only, by appointment arranged via Roy.Forshaw@liverpoolmuseums.org.uk |
| Deadline for Questions | 29.11.17 |
| Response to Questions | 01.12.17 |
| Return of Tenders | 07.12.17 |
| Notification to all Bidders | 15.12.17 |
| Order Placed | January 2018 |
| Issue of Lift Contractors Drawing | February 2018 |
| Completion of Construction Phase H&S Plan | May 2018 |
| Delivery of Materials and Start of Site Works | June 2018 |
| Completion of Works | December 2018 |

CDM 2015 Duty Holders

Client:				National Museums Liverpool

Contact Name: Mike Collins

Address: 127 Dale Street, Liverpool L2 2JH

Tel: 0151-478-4664

Principal Designer:		TUV SUD Dunbar Boardman

Suite D, Chadwick House

Birchwood Park

Warrington

WA3 6AE

Contact Name: Paul Crosbie

Tel: 07971-149546

Designers:	The appointed Lift Contractor & TUV SUD Dunbar Boardman

Principal Contractor:		The appointed Lift Contractor

Contractors:	Any Sub-contractors appointed by the Lift Contractor

The Extent and Location of Existing Records & Plans

No architectural/structural drawings are available relating to the lift well or lift motor room.  The Lift Contractor is therefore required to undertake his own detailed survey of the existing situation of the lift well, lift motor room and associated structure (particularly in relation to the loads imposed and available clearances). The Lift Contractor shall visit the site and ascertain for himself the nature and extent of the Works and the conditions under which these are to be executed.

No claim by the Lift Contractor for additional payment shall be allowed on the grounds that he did not, or could not, foresee any matter which may in fact affect or have affected the execution of the Works.

The Lift Contractor shall be responsible for providing general arrangement, setting-out and construction drawings for the refurbished lifts as part of the Project and as detailed within the Specification together with any additional drawings required for any authorising body.

CLIENT’S CONSIDERATIONS & MANAGEMENT REQUIREMENTS

Planning & Management of the Construction Works

The Client has appointed TUV SUD Dunbar Boardman, who are Lift Consultants experienced in the design, specification and management of lift installation and replacement works, to prepare a Performance Specification and undertake the management of the Project.

Key safety goals include:

- No safety related incidents

- No accidents to employees, residents, contractors, subcontractors or members of the public

- A completed lift installation, suitable for use by disabled persons, that can be used, maintained and operated safely throughout its operational life

- Compliance with the requirements of the Lifts Regulations 2016 and EU Lifts Directive 2014/33/EU; and Harmonised Standards BS EN81-20 & 50: 2014; and BS EN81-70: 2003

- Handover of a Health & Safety File comprising a complete set of CDM 2015, Design and O&M documentation to the Client on completion of the Works

- Communication & Liaison between the Client & Others

The Lift Contractor and his sub-contractors shall, at all times, comply with the agreed Health & Safety procedures and particular those which directly affect the Health & Safety of personnel throughout the installation period of the Contract.  Any additional requirements with respect to emergency procedures and associated requirements are to be discussed/agreed with the Principal Designer and Engineer prior to the commencement of site works.

Method Statements and continuing re-evaluation of work sequences will be required and must be properly implemented by the Lift Contractor. Changes and revisions are to be recorded and/or minuted, and the Construction Phase Safety Plan amended accordingly, during the installation period.

Where unforeseen events may occur during the site works the Lift Contractor shall provide a suitable Safe System of Work which can be implemented to meet the requirements and circumstances of any design change, including assessments of all hazards involved and the necessary communication and liaison required to minimise the effect of these, both materially and with respect to human resources.

The Lift Contractor shall include for attending regular site meetings. The anticipated time scale will normally be once every two weeks, although the actual timing of such meetings shall be as required by the Engineer.

The Lift Contractor is responsible for ensuring that all of his engineers, operatives and sub-contractors are fully trained and made conversant with the required Health & Safety procedures and requirements, prior to commencement of any operations on site.  A Register of Inductions and Tool Box Talks shall be included in the Construction Phase Safety Plan.

Overlap with Clients’ Undertaking

The premises will remain fully operational during the course of the works on site.  The Lift Contractor shall ensure therefore that his engineers and operatives are aware of the requirements for safe access and the protection of work areas.

The Lift Contractor shall protect, uphold and maintain all underground services and overhead lines during the execution of the Works.

The Lift Contractor shall safeguard all reference points which indicate the presence of an underground service and will be held liable for any damage resulting due to any cause within his or his sub-contractor’s control which is occasioned to any service or marker and shall be held responsible for any costs or charges for making good.

The Lift Contractor shall comply fully and in all respects with the statutory requirements of the Control of Pollution Act 1974 and the Control of Noise at Work Regulations 2005.  The use of noisy items of plant, such as percussion drills and angle grinders, whilst permissible, shall be kept to a minimum. If necessary these activities are to be undertaken outside of the normal operating hours of the building.  Sufficient controls or working methods shall be applied in order to ensure that the risks (of exposure to high noise levels) to the Lift Contractor’s employees, sub-contractors or other persons likely to be affected, are reduced to as low a level as reasonably practical. The timing of all activities where a high level of noise generation cannot be avoided must be agreed with the Engineer prior to commencement.

At no time will the use of personal radios be permitted.

The Lift Contractor shall include for taking reasonable precautions to prevent workmen, including those employed by sub-contractors, from trespassing on adjoining owner’s property or any part of the premises which are not affected by the Works.

Security of the Site

The element of the construction site, comprising the lift well and entrances, shall be secured behind robust protective hoardings, which are to be securely fixed to the structure of the building. These shall be checked daily by the Lift Contractor.

The access to the site shall be via the staff entrance at times agreed with the Engineer. All protection to finishes and personnel routes shall be the responsibility of the Lift Contractor. Floor surfaces at each level shall be protected using ‘Cordex’ or equal approved hazard tape in order to avoid tripping hazards.

The existing machine rooms will be available to the Lift Contractor’s operatives as secure areas for the temporary storage of tools etc. during the works.

The Lift Contractor shall:-

Safeguard the Works, materials and plant against damage, theft or vandalism, including the provision of all necessary lighting for the security of the Works and the protection of the Public.

The Lift Contractor shall provide for carefully covering up and protecting all fixed or unfixed items of equipment throughout the duration of the Works until Taking-Over.  Any equipment which has become tarnished, corroded, degraded, or damaged in any way whatsoever, will not be accepted and shall be replaced by the Lift Contractor at his own cost.

The Lift Contractor shall provide for removing all rubbish from the site, both as this accumulates and at completion, including the removal of all temporary works associated with the provision of plant, signboards, temporary roads, temporary hoarding and temporary buildings.  Any damage or disruption arising as a result of the foregoing shall be made good. All packing cases and packing material shall be removed from site immediately the contents have been unpacked.  All waste and/or redundant materials shall be disposed of at an approved site and evidence provided for retention in the Health & Safety File.  Upon completion of the Works, the Lift Contractor shall fully reinstate the site to its original condition.

The Lift Contractor shall make adequate provision to protect the decorative finish to floors, walls and ceilings and areas adjacent to the Works, from damage, occurring accidental or otherwise, occasioned during the course of the Works. Any damage which does occur must be re-instated by the Lift Contractor to the satisfaction of the Engineer.

The Lift Contractor shall ensure that all Portable Appliances used at, or brought to the site shall be tested and marked in compliance with current Regulations.

The Lift Contractor shall ensure that all lifting equipment, including tackles and slings, is tested and marked in accordance with current Regulations.

The Lift Contractor shall ensure that all scaffolding is correctly installed to current Regulations, with installation and/or modifications, adjustments or adaptation, undertaken by authorised personnel only. Scaffolds shall be Inspected and Tagged and a register shall be retained on site.

The Lift Contractor shall issue to, or arrange for, his employees and sub-contractors to be provided with photographic ID Cards which are to be designed to the Engineer’s approval. These are to remain valid for the duration of the Works, and are to be carried at all times. Entry to the premises will be refused if a valid pass cannot be produced.

The Lift Contractor shall also comply with any other security measures which the Client may impose during the Works.

Welfare provision

Access to welfare provisions including, toilets and washing facilities, will be provided by the Purchaser on the basis that these are treated with respect and maintained in a clean and acceptable condition. It is a prerequisite that employees remove overalls prior to entering these areas.

Site Hoarding Requirements

The Lift Contractor shall install robust protective hoardings the design and construction of which is to be as detailed elsewhere in this Specification.

Entrance protection shall be provided by the Lift Contractor in accordance with Section 4 of this Specification.

It is imperative that any protective hoarding, barrier and work screen is maintained in a sound and secure condition always. Access doors are to be kept securely locked excepting for when the Lift Contractor’s engineers or Sub-contractors are working in the immediate vicinity.

Hoardings shall not be dismantled and/or removed without the express agreement of the Engineer.

Site Transport Arrangements & Vehicle Movement Restrictions

The Lift Contractor’s attention is drawn to the requirement that he is to restrict the flow of vehicles to times as agreed with the Engineer, and must allow in his Tender, for all necessary precautions necessary to protect the occupants of the premises and the members of the public, and to maintain access at all times.

The only form of site transport envisaged is that of delivery vehicles to the loading bay area of the property and small handling trolleys within the building.

Delivery of large assemblies or components shall be co-ordinated with the Engineer. The Lift Contractor shall, at all times, supervise offloading and vehicle movements which are to be undertaken during periods of low use of the areas involved.

The Lift Contractor shall provide, and display in the appropriate position, all necessary signs in accordance with the Ministry of Transport system of advance warning signs, as required by the Policy Authority and the responsible Highway Authority. The Lift Contractor shall include for all costs and charges for complying with all other regulations and directions, including obtaining permissions in relation to any road closure, cranes, etc.

Client Permit to Work System

The Client does not operate a Permit to Work system at the premises. However, the Lift Contractor will be expected to manage and monitor access to the work area for the lift and ensure that all operations are conducted in accordance with his own safe working system.

Fire Precautions

The fire alarms and procedures will be reviewed with the Lift Contractor at a pre-start meeting to be held with the Engineer and Client’s representative. The Lift Contractor shall provide fire extinguishers appropriate for any Hot Works. Any Hot Works shall be properly supervised and only undertaken during times and for durations which have been advised to, and agreed with, the Engineer.

Only the Lift Contractor’s employees or sub-contractors who have been properly trained in the use of such equipment shall be permitted to use such equipment. The Lift Contractor shall ensure that proper safety precautions, in compliance with good practice and statutory requirements, are applied and maintained for the duration of the use of the equipment.

Should the Lift Contractor or his sub-contractors have a requirement to use either oxyacetylene or electrical welding equipment on site the Lift Contractor shall first seek the permission of the Engineer, who will not unreasonably withhold such permission.

The Lift Contractor shall include all necessary equipment to control fumes and smoke generated by such operations.

Emergency Procedures & Means of Escape

Emergency procedures, means of escape and first aid facilities (which shall meet the requirements of The Health & Safety (First-Aid) Regulations 1981), will be reviewed at the Pre-Start Meeting.

No-go areas & other specific authorization requirements

The Lift Contractor is required to limit his area of operations to the motor rooms, shafts and any hoarded area of the landings.

The Lift Contractor’s normal access areas will be limited to the motor rooms, wells, entrance lobbies and immediate staircase, as well as agree welfare and washroom facilities. All operatives shall restrict their access to the generally agreed site access and work areas.

The area of the shaft pit, motor room and hoarding shall be designated hard hat areas. The Lift Contractor shall ensure that all of his employees and sub-contractors are issued with, and wear, hard hats whilst working in these areas.  Adequate spare hard hats shall be made available on site for visitors.

Confined Spaces

No confined spaces in the regulatory sense are envisaged. In cases where work is to be undertaken at the head of the lift well, or in the lift pit, where access and egress may be inhibited, the Lift Contractor shall establish a Safe System of Work together with provisions for communication and rescue.

Site Rules & Discipline

The Lift Contractor shall comply with the Client’s Building Rules which will be issued following appointment of the successful contractor.

The Lift Contractor shall, at all times, ensure that his employees, whether for installation works or service work, act in a responsible manner whilst on the Client’s premises.

The Lift Contractor shall ensure that all employees and sub-contractors are issued with, and wear at all times, personal protective equipment. This should comprise, as a minimum, overalls bearing the company name or logo, safety footwear, eye protection, hearing protection and hard hat.

Each of the Lift Contractor’s employees who are required to visit the premises are expected to carry identification which must be produced on request to duly authorised representatives of the Client.

The Client reserves the right to refuse access to or to reject any of the Lift Contractor’s employees or sub-contractors in the event that their actions are considered to be disruptive or detrimental to the operation of the premises or to the progress of the Works.

The Lift Contractor shall ensure that all work areas are left safe and secure following completion of each day’s work, with all access keys returned to the Client’s Representative.

Construction Skills Certification Scheme

All the Lift Contractor’s engineers and sub-contractors shall have passed the relevant level of CSCS test and be in possession of a valid card.

The Lift Contractor must refuse access to any operative who is not carrying a valid card.

Parking Restrictions

Parking for one vehicle will be made available in the vicinity of the site.

ENVIRONMENTAL RESTRICTIONS & EXISTING ON-SITE RISKS

Safety Hazards

Known potential existing safety hazards and environmental restrictions which are to be taken into account and addressed by the Lift Contractor in his Construction Phase H&S Plan include the following:

- Loading, off-loading and distribution of materials will be undertaken in areas accessible to site visitors and members of the public, some of whom may be elderly and have mobility limitations.

- Limited space is available for vehicle manoeuvring and turning of vehicles.

- Hydraulic oil stored in the existing lift motor room tank unit is to be removed from site. This presents a risk of contamination if spilt onto surrounding areas or into adjacent drains.

- Limited storage space is available and redundant materials are to be removed on a daily basis.

- Wiring for the fire alarm smoke detector at the top of the lift shaft is to be retained and reinstated during the strip out of redundant lift material.

Health Hazards

Contaminated Land

The Lift Contractor shall observe the environmental controls detailed in The Contaminated Land (England) Regulations 2000 as enforced by the Environment Agency or Local Authority and seek specialist advice before commencing work.

KNOWN EXISTING HAZARDS

Known potential existing health hazards to be taken account of and addressed by the Lift  Contractor in his construction phase plan are as follows:

Asbestos

There are no known asbestos containing materials present in the work areas or equipment covered by this project (refer to asbestos survey/register appended to this Specification).

However, clear and explicit instructions must be issued by the Lift Contractor to all operatives and sub-contractors involved with the works on site, such that if during the course of the works material is encountered which it is reasonably suspected may contain any form of asbestos, they should respond as follows:-

- Cease work in the vicinity of the suspect material immediately.

- Report immediately by telephone, and confirm by facsimile within two hours, to the Engineer.

- Do not recommence work until instructed to do so by the Engineer.

Mineral Oil

- The existing drive/tank unit, hoses and jack contain hydraulic oil, which will require appropriate protective clothing, gloves etc. to be worn by operatives handling the removal of the redundant equipment. All oil must be disposed of in accordance with the relevant legislation and guidance.

SIGNIFICANT DESIGN & CONSTRUCTION HAZARDS

Significant Design Assumptions (Work methods, sequences and other control measures)

The lift design shall be in compliance with the Harmonised Standards BS EN81-20: 2014 and BS EN81-50: 2014 providing an assumption of compliance with the Essential Health & Safety Requirements of EN Lifts Directive 2014/33/EU and with the Lifts Regulations 2016. The lift shall be subject to witness test in line with BS 8486-1:2007 Standard on completion.

The lift installation method is proprietary to the Lift Contractor and detailed installation Method Statements, Risk Assessments and layout drawings shall be provided by the Lift Contractor. These shall be incorporated into the Construction Phase Plan.

The removal of the existing lift shall be undertaken by the Lift Contractor’s operatives who must be experienced in this type of work.

It is envisaged that the existing lift well equipment can be electrically isolated and the lift car suitably suspended, applying a double set of tested lifting equipment each of which is suitably de-rated by 50% of SWL, from the existing lifting beam, which shall be tested prior to use. The lift car may then be utilized as a working platform to dismantle equipment in the upper section of the lift well and lower this into the pit area for dismantling and removal from site via the basement floor into the loading bay. It is envisaged that the lift machine room equipment can be electrically isolated, mechanically and electrically disconnected and removed from site.

Comprehensive and detailed Safe Systems of Work, Method Statements, Risk Assessments and Control Measures are to be provided and agreed with the Principal Designer/Engineer prior to commencement.

The associated builders and electrical work shall be undertaken by the Lift Contractor. It is envisaged that the works are to be undertaken using traditional construction trades working from a traditional scaffold structure or temporary platform installed within the lift well. The Lift Contractor shall provide comprehensive and detailed Safe Systems of Work, Method Statements and Risk Assessments for all builder’s and electrical works tasks.

Coordination of Ongoing Design and Design Changes

It is envisaged that the Lift Contractor shall provide detailed lift design drawings together with details of the required builder’s works alterations and any modifications to the lift well and lift motor room. These are to be reviewed and agreed with the Engineer. Any subsequent design changes which may arise are to be channeled through the Principal Designer/Engineer, recorded in the Construction Phase Plan, and detailed on the Construction and the final As-Built Drawings.

The Lift Contractor shall record and highlight, including appropriate detail, any significant hazards and risks associated with the Construction Works, which have not been eliminated and/or adequately mitigated in the Design of the Works, on the Construction Drawings.

The Lift Contractor shall record details of any significant residual hazards and risks affecting the Works and the Design, which could not be eliminated and/or adequately mitigated in the Design, on the Final “As Fitted” record drawings and in the H&S File.

Information on Significant Risks Identified During Design

- Refer to the Lift Contractors Design Risk Assessment for compliance with the Lifts Regulations 2016 and EU Lifts Directive 2014/33/EU.

- Refer to following Dunbar & Boardman indicative risk assessments.

- Materials Requiring Particular Precautions

- Disposal of redundant hydraulic oil.

PRINCIPAL CONTRACTOR CONSTRUCTION PHASE PLAN DEVELOPMENT

The Lift Contractor shall develop the Health & Safety Plan in accordance with Regulation 12 of the CDM 2015 Regulations.

A copy of the Construction Phase Health & Safety Plan shall be provided to the Principal Designer and Engineer prior to commencement of any works.

During the course of the Project a copy of the Plan will be held on site by the Lift Contractor’s Senior Engineer. This shall be updated with any necessary amendments agreed during the regular site meetings.

At completion of the Project the Lift Contractor shall provide the Operating and Maintenance Manuals and the Health & Safety information, including assessments of residual risks, to the Principal Designer for incorporation into the Health & Safety File, which is to be provided to the Client.

- THE HEALTH & SAFETY FILE

The Health & Safety File shall be produced in accordance with the CDM 2015 Regulations and the Guidance provided by HSE. Relevant information obtained from the Lift Contractor, Designers, Contractors and other parties during the course of the Project shall be collated by the Principal Designer for issue to the Client on completion of the Project.

In order to produce the file the Principal Designer requires the cooperation of the Lift Contractor and other Designers and Contractors who shall to provide information expeditiously, and whenever required, throughout the course of the Project. In particular the Operating and Maintenance Manuals, which are detailed later in this Specification, these are to be provided at the latest by the date of Taking-Over, accepting that the final installation Test Certificates may not be available until completion of Witness Tests.

The information to be included must be specific to those Health and Safety issues relevant to the Project and Works and shall cover the whole installation life cycle including development, maintenance and subsequent demolition.

- Dunbar & Boardman Risk Assessments

(Based upon BS ISO 14798:2013)

| LIFT SPECIFICATION RISK DOCUMENTATION |  | Document No. LSRD |
| --- | --- | --- |
| Contract Name – Merseyside Maritime Museum |  | NOTE: The hazards identified should not be considered to be an exhaustive list. You are also advised to make reference to BS EN81-80:2003, for significant hazards associated with existing lift installations and implement appropriate control measures. This document is intended as a reminder of the possible consequences of certain activities/actions and is not a reflection on your skill and experience. If you identify any other potential hazards, please ensure the master document is suitably amended. |
| Lift Identity & location – 2 No. public lifts |  |  |
| Assessment conducted by: P. Crosbie Date: 10.05.17 | Signed: |  |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) | S | F | Initial Risk Rating (S x F) | Persons at Risk | Control Measures/Corrective Actions | S | F | Final Risk Rating (S x F) | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G1 | Equipment Remains Unexpectedly Live | Electric Shock due to: - Faulty switchgear - Poor insulation or earthing - Inadequate switch marking - Live interconnected wiring - Car lighting or other high voltage equipment in controller - Charge remaining on DC link capacitors on VVF drives - Equipment not PAT tested - No rubber mats - No main switch lock off facility - Missing or broken covers - Tripping hazards - Inadequate lighting | 4 | 4 | 16 =VH | E CO O | Motor room to be designed to allow adequate access for working in accordance with Electricity at Work Regulations and be well lit and free of tripping hazards. Lift Contractor to ensure all staff are adequately trained in safe working practices. All portable appliances to be tested and marked with valid PAT certification. Lift Contractor to provide lock-off facilities to main switches and rubber mats to BS921 at front and rear of controllers. Wherever practical, inspection of electrical systems should be carried out only after the equipment has been isolated from the power supply. When appropriate, to safeguard accidental reconnection by others, the main supply must be “locked-off” and “tagged out” to clearly indicate that work is in progress. All readily accessible live conductors must be covered by an insulating material, e.g. rubber shrouds, or be positioned so they are safe. All equipment must be properly earthed. All doors to control cabinets must be closed and secured after use. A “treatment for electric shock” notice should be displayed in appropriate locations, as recommended by the Guidance to the Electricity at Work Regulations. | 2 | 2 | 4 = L | - Acceptable risk |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) | S | F | Initial Risk Rating (S x F) | Persons at Risk | Control Measures/Corrective Actions | S | F | Final Risk Rating (S x F) | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G2 | Manual Handling of Equipment | Injury due to: - Items heavier than they appear - Incorrect lifting method - Lack of mechanical handling equipment - Lack of assistance for heavy load - Lack of protective footwear - Sharp edges | 2 | 4 | 8 = M | E CO | All items to be marked with their weight. Lift Contractor to provide mechanical handling equipment to move items which cannot be safety man handled. Safety footwear to BS EN ISO 20345 and protective Kevlar or rigger gloves must be worn. | 2 | 2 | 4 = L | - Acceptable Risk |
| G3 | Use of Percussion Drill/Angle Grinder or Hand Tools | Damage to hearing by percussion drilling or accident while using angle grinder/hand tools. | 3 | 5 | 15= VH | E CO V O | Lift Contractor to observe Principal Contractors disciplines for noisy works and ensure full compliance with the Control of Noise at Work Regulations 2005. Non-percussive drills should be used wherever practical to reduce the risks from noise and vibration. Lift Contractor to ensure all staff using or working near percussion drilling equipment/angle grinders etc. are equipped with suitable ear defenders/protective goggles and that they use protective equipment and have been instructed on their correct use. All portable appliances to be tested and marked with valid PAT certification. Unless battery powered or hand tools are employed, a residual current earth leakage device (RCD) designed to BS EN 61008-1 must be used. | 2 | 2 | 4 = L | - Acceptable Risk |
| G4 | Use of Mineral Oil | Risk of illness from contact with mineral oils | 3 | 3 | 9 = M | E CO | Consultant to specify low risk or bio-degradable oils where available. Lift Contractor to provide COSHH data sheets for any substances involved. The area should be well ventilated and PPE should include the use of disposable overalls | 2 | 2 | 4 = L | - Acceptable Risk |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  |  |  | 2 Minor Injury |  |  |  |  |  | 1 Highly Improbable |  |  |  |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |  |  |  |  |
| 3 Serious Injury |  |  |  | 4 Major Injury |  |  |  |  |  | 4 Occasional |  |  |  |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |  |  |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk |  | Public |  |  | P | Client | CL |  |  |  |  | Employee |  | E |  | Contractors |  | CO | Visitors | V |  |  |  |  | Others |  | O |
| No: | Activity/Location Materials/Tools etc (Cause/Trigger) |  | Hazards Identified - (Effect) |  |  |  |  | S | F |  | Initial Risk Rating (S x F) |  | Persons at Risk |  | Control Measures/Corrective Actions |  |  |  |  |  |  | S | F | Final Risk Rating (S x F) |  | - Residual Risk |  |
| G5 | Use of Welding/Grinding Equipment |  | Danger of fire due to dry grinding or welding on site |  |  |  |  | 3 | 4 |  | 12 = H |  | P CL E CO V O |  | Principal Contractor to establish regime of Hot Works including permits. Lift Contractor to ensure site staff are aware of procedures and work to them. Lift Contractor to provide all necessary PPE, safety and fire precautions, certified as necessary and ensure they are maintained throughout the Hot Work process. As a minimum, fire extinguishers must be readily available and members of the public and other non essential staff excluded from the agreed work area. If gas welding equipment is used it must be inspected prior to use for damage to valves, hoses and for leaks and must not be used if defective. The work area must be well ventilated and any smoke detectors temporarily disarmed. |  |  |  |  |  |  | 2 | 2 | 4 = L |  | - Acceptable Risk |  |
| G6 | Use of Paint Spraying Equipment |  | Danger of inhalation of fumes from site spraying or painting |  |  |  |  | 3 | 3 |  | 9 = M |  | CL E CO |  | Wherever practical, off-site application of paint specified by Consultant. Otherwise, Lift Contractor must use low fume materials where available and provide COSHH data on all materials used. Lift Contractor to provide PPE and any necessary protection and extraction necessary to comply with the COSHH Regulations. |  |  |  |  |  |  | 2 | 2 | 4 = L |  | - Acceptable Risk |  |
| G8 | Delivery/Removal of Lift Equipment |  | Danger of tripping or being struck by equipment being removed or delivered to site. |  |  |  |  | 3 | 4 |  | 9 = M |  | P CL E CO V O |  | Contractor to provide temporary barrier protection and notices on agreed access route for deliveries. The access route must not be accessible to the public. Any floor protection to be taped in place. All deliveries to be co-ordinated with the Engineer/Purchaser. |  |  |  |  |  |  | 3 | 2 | 6 = M |  | - Acceptable Risk |  |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) | S | F | Initial Risk Rating (S x F) | Persons at Risk | Control Measures/Corrective Actions | S | F | Final Risk Rating (S x F) | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| G9 | Possible Asbestos Contamination Within the Lift Area | Health risk due to inhalation of asbestos fibres from: - Brake linings - Contactor arc shields - Door insulation - Pipework/ductwork lagging - Machine room or shaft panelling/wall cladding | 3 | 4 | 12 = H | E CO | The owner (or ‘Duty Holder’) shall furnish a copy of the Asbestos Register called for by the Control of Asbestos Regulations 2006. Contractor to arrange specialist analysis, identification and recommended action then submit a report to Design Team. Contractor to arrange recommended action in accordance with specialist report. Any removal & disposal shall be carried out by a registered Contractor fully in accordance with the Health & Safety at Work Act and all relevant Health & Safety Executive Guidance Notes. | 3 | 2 | 6 = M | - Acceptable Risk |
| G10 | Installation of Mirrors or Glass Doors/Decorative Panels | Injury from broken glass | 3 | 3 | 9 = M | E CO | Design team to specify laminated glass and mirrors with safety backing. Protective gloves to be worn when handling glazed panels. | 3 | 2 | 6 = M | - Acceptable Risk |
| G11 | High Voltages on Auxiliary Lift Equipment Termination Points. | Danger of electric shock | 4 | 3 | 12 = H | E CO O | Lift Contractor designer to ensure all auxiliary wiring within the lift machine room, lift shafts and lift car are of a maximum 55 volts where practically possible. (PD6519-1:1995 & IEC 60479-1:1994 refer). All connections and enclosures where higher voltages are present are to be identified with appropriate signage. | 3 | 2 | 6 = M | - Acceptable Risk |
| G12 | Alterations to Existing Electrical Supplies | Danger of electric shock | 4 | 3 | 12 = H | E CO | Lift Contractor to issue Method Statement and Risk Assessment on working procedure on existing electrical supplies that require alteration during the scope of the works. If the existing supplies cannot be identified and isolated then works are not to proceed and must be reported to the Engineer and site contact. | 2 | 2 | 4 = L | - Acceptable Risk |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) | S | F | Initial Risk Rating (S x F) | Persons at Risk | Control Measures/Corrective Actions | S | F | Final Risk Rating (S x F) | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LS1 | Shaft Access During Lift Installation | Danger of falling down lift shaft during construction and installation of lift. | 4 | 3 | 12 = H | P CL E CO V O | Principal Contractor to protect entrance openings to lift shaft so there is no risk of falling. Lift Contractor to provide method statement with safe system of working. Lift Contractor to ensure that all staff have adequate safety equipment and are instructed for its use and that they must ensure their activities do not endanger others. | 3 | 2 | 6 = M | - Acceptable Risk |
| LS2 | Working on Car Top - Limited Headroom | Danger of Engineer striking head on slab over lift shaft whilst working on car top. | 2 | 5 | 10 = H | E CO | The headroom must be designed to meet the requirements of BSEN81 so there is headroom above the lift car to provide a space sufficient to accommodate persons travelling on top of the lift. Limit switches in compliance with BS7255 must be installed to prevent movement of the lift car beyond a defined point to create this safe space. Suitable danger notices to be provided on car top by Lift Contractor. | 2 | 2 | 4 = L | - Limit switch could fail to stop the lift |
| LS2A | Working on Car Top - Headroom Not Compliant with BSEN81 | Risk of Engineer being crushed whilst working on car top. | 4 | 5 | 20=VH | E CO | Lift Contractor to develop a safe system of working taking into account the existing constraints and then seek approval of his Notified Body for this deviation from the standard. As a minimum, electrically interlocked props and limit switches must prevent movement of the lift car beyond a defined point to create the safe space required by BSEN81 & BS7255. Travel in the up direction must not be attempted unless it is essential. | 2 | 2 | 4 = L | - Acceptable Risk |
| LS3 | Working in the Lift Pit | Danger of Engineer being crushed below the descending car whilst working in pit. | 4 | 4 | 16=VH | E CO | Pit depth and position of stop switches to be in accordance with BSEN81. Consultant to specify provision of guide clamps or props in pit. Lift Contractor to provide clamps or props along with notice instructing on their use. Prior to entering pit, verify the correct operation of the landing locks and the pit emergency stop switch. Use props on hydraulic units and do not go under a traction unit that has a load in the car. | 4 | 2 | 8 = M | - Pit stop switch may subsequently fail |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) |  | S |  | F |  | Initial Risk Rating (S x F) |  | Persons at Risk |  | Control Measures/Corrective Actions |  | S |  | F |  | Final Risk Rating (S x F) |  | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LS3A | Working in the Lift Pit – Pit Depth Not Compliant with BSEN81 | Danger of Engineer being crushed whilst working in pit due to existing pit depth not being compliant with BSEN81. |  | 4 |  | 5 |  | 20=VH |  | E CO |  | Consultant to specify provision of guide clamps or props in pit. Lift Contractor to provide clamps or props along with notice instructing on their use. Prior to entering pit, verify the correct operation of the pit emergency stop switch. Use props on hydraulic units and do not go under a traction unit that has a load in the car. Lift Contractor to develop a safe system of working taking into account the existing constraints and then seek approval of his Notified Body for this deviation from the standard. A “Permit to Work” system must be operated in the interim period. |  | 3 |  | 2 |  | 6 = M |  | - Permit to work system ineffective |
| LS6 | Working on Lift Landing | Danger of falling down existing shaft from landings during works. | 4 |  | 4 |  | 16=VH |  | E CO |  | Contractor to provide lockable hoarding to each entrance where the doors have been removed in accordance with the Designers specification, taking due care to avoid restricting access through building, means of escape, etc. Hoardings to be fitted with suitable notices warning of risks. Hoardings to be kept locked. Contractor to operate a “Permit to Work” system, ensuring all staff work to them and are aware of risks. |  | 4 |  | 2 |  | 8 = M |  | - Unauthorised persons may enter while hoardings are open |  |
| LS5 | Working on Car Top | Danger of falling from car top during maintenance or inspection |  | 4 |  | 4 |  | 16=VH |  | E CO |  | Design Team to include in car design for safety barriers and harness anchor point. Contractor to provide suitable harness to all staff working on lift, with instructions to their use. Contractor to provide suitable notices on car top. Health & Safety file and O&M Manuals to contain information and warnings. |  | 4 |  | 2 |  | 8 = M |  | - Harness may not be worn |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) | S | F | Initial Risk Rating (S x F) | Persons at Risk | Control Measures/Corrective Actions | S | F | Final Risk Rating (S x F) | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MR1 | Working in Machinery Area | Danger of Engineer having inadequate space for safe access of equipment. | 3 | 3 | 9 = M | E CO | The machine room area, height, access and layout of equipment to be in accordance with BSEN81, Health & Safety at Work Act and the Electricity at Work Regulations. | 3 | 1 | 3 = L | - Acceptable Risk |
| MR1A | Working in Existing Machinery Area | Danger of Engineer having inadequate space for safe access of equipment. | 3 | 4 | 12 = H | E CO | Since the machine room is existing, the Lift Contractor shall select and lay out equipment to achieve the clearances recommended in BSEN81, and ensure that the mandatory provisions of The Health & Safety at Work Act and the Electricity at Work Act are achieved. | 3 | 2 | 6 = M | - It may not be possible to be fully compliant due to space restrictions. |
| MR2 | Working in Machinery Area | Danger of injury by unguarded machinery. | 3 | 3 | 9 = M | E CO | Motor room and lift shaft to be kept locked. Lift Contractor to paint all moving parts safety yellow and provide guarding in accordance with Machinery Directive and PUWER Regulations. A remote gear isolation switch should be fitted to act as an emergency stop whilst working near unguarded sheaves or ropes. | 2 | 2 | 4 = L | - Guarding could be inadequate or have been removed |
| MR3 | Working in Machinery Area | Danger of injury to Contractor’s staff due to inadequate lifting facilities. See also item G7 | 4 | 3 | 12 = H | E CO | Lifting beam requirements to be shown by Lift Contractor in his design drawings. Structural Engineer to design fixings to suit. Suitable lifting beams to be provided in head of shaft by Principal Contractor. Beam to be tested and marked with its SWL. Certificates to be kept in site records. | 3 | 2 | 6 = M | - Acceptable Risk |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| No: | Activity/Location Materials/Tools etc (Cause/Trigger) | Hazards Identified - (Effect) | S | F | Initial Risk Rating (S x F) | Persons at Risk | Control Measures/Corrective Actions | S | F | Final Risk Rating (S x F) | - Residual Risk |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MR4 | Entering or Leaving Hydraulic Machine Room | Danger of tripping over bund wall to pump room door. | 2 | 4 | 8 = M | E CO | Bund wall to be marked using suitable hazard warnings by Principal Contractor. | 2 | 2 | 4 = L | - Acceptable Risk |
| MR5 | Working in Machinery Area | Danger of falling from raised machine room plinth | 3 | 4 | 12 = H | E CO | Design team to specify supply and installation of adequate cat ladders and guard rails to comply with current Regulations. Contractor to ensure these are fitted as part of his commissioning tests. | 3 | 2 | 6 = M | - Acceptable Risk |
| MR6 | Working in Machinery Area | Danger of moving equipment in multiple motor room | 3 | 4 | 12 = H | E CO | Contractor to install suitable fixed barriers around all retained components in motor room. Carry out Risk Assessments and establish a safe method of working. | 2 | 2 | 4 = L | - Acceptable Risk |
| MR7 | Entering plant rooms, lift shaft or pit | Danger of hostile atmosphere & build up of toxic gases within lift motor room and pit. Lack of oxygen/explosive atmosphere | 4 | 3 | 12 = H | E CO O | Design Team to provide adequate information to allow Contractors to prepare Method Statement. Design Team to check statement prior to commencement of work. Contractor to ensure site staff are fully aware of risks and work to the method statement. Contractor to provide tested and certified gas detectors and fully functional respiratory protective equipment. A contingency Rescue Plan shall be ready for activation. Atmospheric tests must be conducted to ensure that the oxygen supply is within safe limits (e.g. 19% +) and safe working conditions exist, before entry is made into the plant rooms, lift shaft or pit. In each case a permit to work system shall be operated | 2 | 2 | 4 = L | - Acceptable Risk |

| Risk Rating Criteria |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SEVERITY (S) |  |  |  |  |  | FREQUENCY (F) |  |  |  |  |  |  |  |  |  |  |
| 1 Negligible |  | 2 Minor Injury |  |  |  | 1 Highly Improbable |  |  |  | 2 Improbable |  |  |  | 3 Remote |  |  |
| 3 Serious Injury |  | 4 Major Injury |  |  |  | 4 Occasional |  |  |  | 5 Probable |  |  |  | 6 Highly Probable |  |  |
| Risk Rating Multiples: 1 - 4 LOW = Acceptable risk; 5 – 9 MEDIUM = Investigate and where practical reduce the risk; 10 – 14 HIGH = Action must be taken to reduce the risk; 15 – 24 VERY HIGH = Risk is too high to START work or continue. work must stop |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Persons at Risk | Public |  | P | Client | CL |  | Employee | E | Contractors |  | CO | Visitors | V |  | Others | O |

| DUNBAR & BOARDMAN - HAZARD IDENTIFICATION CHECKLIST |  |
| --- | --- |
| JOB NO. N.W1700021 | DATE: 20.09.17 |
| PROJECT: Merseyside Maritime Museum | ACTIVITY: Full replacement of 2 No. passenger lifts |

(To be read in conjunction with Risk Analysis Sheets)

| Activity | HAZARD (tick off relevant hazards) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Radiation Chemical & Metal Splash | Confined spaces | Fall From Height | Struck by Mobile Plant | Trip | Collapse | Manual Handling | Moving Object | Electricity | Contact with moving machine | Fire | Hazardous Substance | Noise & Vibration | Explosion |
| LIFTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - New Installation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Modify Existing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Removal of Existing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ESCALATORS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - New Installation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - Removal of Existing |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Builders Works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electrical Works |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Asbestos Removal |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

- Signed:          Name: Paul Crosbie

SCHEDULE OF BUILDERS WORK

SECTION 4

SCHEDULE OF BUILDERS WORK

The work described in this section is to be provided by the Lift Contractor or his Sub-contractor and is to be included within the Tender price.

Attendances

Attendances as set out in the Preliminaries including: -

Storage and accommodation;

Temporary lighting and power;

Scaffold as required for the Lift Contractor’s preferred method of discharging the Works.  All scaffolding used is to be designed and installed in compliance with the requirements of BS EN12811: 2003, CITB TG20:13, the CDM Regulations 2015 and the Health & Safety at Work Act, together with any other Guidance, Regulation or Statutory requirement which may apply to the site and/or Works.

The scaffolding installation may be altered, modified, moved and or revised only by authorised and approved scaffolding operatives, and shall be inspected, tested and tagged periodically through the duration Works.

- Dismantling

The Lift Contractor is to allow for dismantling of all redundant lift and associated equipment and the expeditious removal of the same from site.

On completion of the dismantling element of the works, the Lift Contractor shall include for the preparation of, and any alteration to, the building fabric, which is required to accommodate the new lift equipment.

The redundant materials shall be disposed of by the Lift Contractor in a responsible manner, taking due regard of all relevant Regulations, and the Lift Contractor shall include for the payment of all relevant Taxes or charges associated with this within his Tender.

- Steelwork

The Lift Contractor shall dismantle any redundant steelwork and supply and install all necessary new steelwork which is, or may be, required to accommodate the new lift equipment within the lift machine room and lift shaft.

Existing Equipment (Maintenance)

As part of the removal/dismantling process the Lift Contractor shall retain all key parts of the existing equipment recovered from the first/early phases of the Works for use as spares in order to support maintenance of the equipment being retained during later or other phases of the Works.

The Lift Contractor shall provide a list of equipment which is to be retained and agree this with the Engineer prior to commencement of any removal/dismantling works.

# Lifting Beam

Prior to commencement of the Works, the Lift Contractor shall supply and install within the lift shaft.  These shall be purpose designed such as to accommodate the weight of the lift car, counterweight or complete lift machine assembly.

The beams shall be designed in accordance with the requirements of the equipment to be lifted and those of BS EN1993-6. The installed beams shall be tested in accordance with the requirements of BS2853: 2011.

Prior to use the installed beams shall be tested and a label affixed indicating the safe working load in compliance with the requirements of PUWER, LOLER and the Health & Safety at Work Act 1974.

Pit Ladder (fixed)

In cases in which the depth of the lift well pit does not exceed 2.5 M and/or in cases in which a separate pit access door is not provided, the Lift Contractor shall supply and install a fixed access ladder in the lift pit(s).

The access ladder shall be easily accessible from the landing entrance door and shall be permanently and securely fixed to the building fabric.

The design and construction of the access ladder shall be such as to withstand the weight of one person based upon a minimum force of 1500 N.

The access ladder shall be designed in accordance with the requirements of BS EN81-20: 2014 and BS EN131-2: 2010+A1:2012 and shall be constructed in steel with a suitable anti-corrosion finish.

The ladder shall be constructed from steel uprights, which provide for safe and easy hand grasping, and which extend vertically from the base of the pit floor to a minimum of 1.1 M above the landing sill of the pit access landing entrance. The uprights shall be of width not exceeding 35 mm and depth not exceeding 100 mm.

The ladder shall incorporate flat steel treads which shall be of minimum clear width 280 mm, with a flat tread of minimum 25 mm and maximum 35 mm in depth, and which shall be spaced equally at vertical intervals of not less than 250 mm and not exceeding 300 mm. The upward surface of each tread shall be non-slip by way of permanent surface finish.

The access ladder shall be designed and installed such that a minimum clear distance of 200 mm is attained between the rear of each tread and the wall of the pit or any other element of the building fabric or equipment.

Pit Ladder (Alternative Design)

Should it be impossible to safely accommodate a fixed ladder within the lift pit, the Lift Contractor shall provide a suitable alternative access ladder the design and construction of which shall be in accordance with the requirements of the designs designated Type 1, Type 2a, Type 2b, Type 3a, Type 3b or Type 4, set out at Annexe F of BS EN81-20: 2014, and to the approval of the Engineer.

The Lift Contractor shall state at Section 10 of this Specification in the Technical Details of the Tender Return which of the ladder Type Designs he has included for in his Tender.

The ladder shall be permanently housed and stored in the lift well pit such that this cannot be removed from the lift well and/or used for other purposes.

The distance between the edge of the landing entrance and the ladder in its stored position shall not exceed 800 mm.

The distance between the edge of the landing entrance and the centre of the ladder treads when the ladder is in the deployed position shall not exceed 600 mm.

When in the deployed position the first tread of the ladder shall be as close as possible to the level of the landing sill.

If, when in the deployed position, the ladder is within the travel path of the lift car, or whenever there is a risk that the ladder may come into contact with moving machinery, then the ladder, and/or its storage bracket/mounting, shall be equipped with an electrical safety device which prevents operation of the lift whilst the ladder is in the deployed position and when the ladder is not in the stored position.

In each design case the ladder, when in use, shall be such that this is secured to the landing sill and/or, the base of the pit and/or, the wall of the lift well, such as to ensure safe access and to prevent tipping-over of the ladder.

In the case of retractable and/or folding ladder designs these shall be such as to prevent the shearing or crushing of hands or feet during use and during deployment and during storage following use.

In the case of moveable and/or foldable access ladders these shall be designed and constructed such that the weight of this does not exceed 15 kg and such that handling and storage may be safely undertaken at the landing sill and lift well pit.

In the case that the ladder is stored upon the pit floor the ladder shall not, when in its stored position, encroach upon the pit refuge spaces.

Shaft Dividing Screens (existing)

The existing shaft dividing screens shall be retained. The Lift Contractor is to inspect all fixings for security and repair as necessary.

The complete screen is to be thoroughly cleaned and wire brushed and re-painted with two coats of oil based machine paint to an approved colour.

Protective Screens on Landings (Full Hoardings)

The Lift Contractor shall provide sketch drawing of his proposed landing protective screens. The drawing shall detail the design, the materials to be used, the method of construction and the manner in which the protective screen is to be secured to the building fabric.

Prior to the commencement of works on site the Lift Contractor shall provide rigid protective screens at each lift landing entrance.  The screens shall be securely capped at a minimum height of 2.5 M.  Each screen shall enclose such working space as is available, but shall not obstruct access and/or means of escape to routes, stairways and landings.  Each screen shall incorporate a hinged and lockable access door to a clear height and width to suit the Lift Contractor’s requirements.

The screens shall be constructed from smooth faced plywood or MDF board, with sufficient softwood bracing as to provide rigidity and security.  Polythene sheeting which is covered with sheet(s) of hardboard over the entire area shall protect the floor area within the protective screen.

The Lift Contractor must include for meeting the additional requirements of the Building Control Officer, wherever applicable, as to the construction, and in particular the fire resistance, overall dimensions and exact positioning of protective screens, access doors and frames.  Note: any protective screen on a fire escape route must be a minimum ½ hour fire rated including the doors and surround.

The access door/s shall be fitted with suited locks such that each door can be positively locked from the outside by way of a key, and can be opened from the inside without the use of a key, even when locked from the outside. In addition, two shoot-bolts shall be fitted on the inside of each such door. All doors shall be fitted with self-closers in order to prevent these being inadvertently opened.

All fixings shall be such that these cannot be removed from the outside of the screen and shall not cause any damage to the decorative finishes.  The Lift Contractor shall maintain the screens and doors in a safe condition throughout the duration of the Works and shall not remove these until directed to do so by the Engineer.

Within each hoarding a handrail, mid-rail and toe board shall be provided in order to protect any open void. These may be removed temporarily for working only when the lift car is safely positioned at that landing and on the basis that these are re-instated before the lift car is moved.

The screens shall be decorated to complement the surrounding décor, with a minimum of two coats of emulsion paint, in a colour to be agreed.

The Lift Contractor shall maintain the finish of the screens throughout the works and to the satisfaction of the Engineer and shall ensure that any dirty marks are removed from the landing side of the screen as and when these arise.

Danger notices warning of the nature of works and any exposed voids, complete with ‘apology for inconvenience’ signage, shall be prominently displayed on the screens.

Dust and Debris Screens

The Lift Contractor shall provide suitable temporary screens formed of polythene sheeting such as to prevent the passage of dust and debris from the lift under construction to the lift which is in service. The screen shall be securely fixed to the permanently installed shaft division screen, with the method of securing and the final arrangement of the screens subject to the approval of the Engineer.

The temporary screens shall be retained in place throughout the Works and until completion of the Contract, and shall be removed only upon instruction of the Engineer.

Making Good

The Lift Contractor shall make good all damage to the fabric or finishes in the building and its surroundings, whether scheduled or inadvertent, which has been occasioned by his Works. These shall be reinstated in materials and or finishes which match the existing. In the event that matching material proves difficult to obtain, alternatives shall be offered for consideration prior to the making good being put in hand.  Particular care is to be taken in relation to the decorative finishes to floors and walls around the lift landing entrances.

The extent of making good shall be defined for estimating purposes as the full front wall of the lift shaft from floor to ceiling up to 2 M from each architrave horizontally.  This may be varied prior to commencement by mutual agreement between the Lift Contractor and Engineer.

Shaft Painting

The Lift Contractor shall clean down the shaft and pit, remove all debris, grease and oil, and then treat the shaft walls and soffit with two coats of white emulsion paint.

The pit floor shall be cleaned, degreased and then sealed using two coats of an anti-slip, oil proof, and proprietary floor paint.

At the completion of the Works, any damage to these finishes shall be repaired to the satisfaction of the Engineer.

Landing Fixture Apertures

The Lift Contractor shall include for additional cutting of the existing apertures to accommodate the new landing pushes / indicators in the front wall.

The pushes shall be fixed at a height in compliance with Part M2 of the Building Regulations and the provisions of BS EN81-70 and BS8300.

The lift landing indicators shall be as detailed elsewhere in this Specification.

The Lift Contractor shall include for making good the existing apertures in an equivalent matching finish to the existing, and to the satisfaction of the Engineer.

Decommissioning and Removal of Lifts

The Lift Contractor shall include for all decommissioning and removal of the existing lift equipment.  Except as otherwise stated in this Specification materials of any kind obtained from dismantling shall become the property of the Lift Contractor. The Lift Contractor shall dispose of such materials in a responsible manner, taking due regard of all relevant Regulation, but in all cases, shall remove the materials from the premises promptly, and as soon as dismantled, and at all times expeditiously and cleanly. The Lift Contractor shall include for all taxes and/or other statutory fees associated with the disposal of the materials.

Prior to commencement of the Works the Lift Consultant shall identify any items of equipment which the Lift Contractor shall carefully remove and deliver to an agreed location within the premises for re-use by the Purchaser on other installations.

As part of the Works the Lift Contractor shall ensure that personnel have received the correct safety induction and have available all of the necessary tools and plant, complete with required test certification, and all personal protective equipment necessary to undertake the work.

In cases where the removal process involves the use of Hot Work Permits, these shall be obtained in accordance with the Purchaser’s requirements.

Where Oxy-propane equipment is to be used then the personnel involved shall have a minimum of two years’ experience and training certificates shall be provided. A Fire Watchman must also be present and shall continue to be present for a period of one hour following completion of the process.

In terms of manual handling, all dismantled materials shall be broken down into adequately manageable sections, ready for disposal, and using mechanical methods wherever possible, and shall be subject to the Engineers approval.

SCHEDULE OF ELECTRICAL WORK

SECTION 5

# SCHEDULE OF ELECTRICAL WORK

The works described below are to be provided by the Lift Contractor or his sub-contractor and are to be included in the Tender Price.  All works are to be carried out and completed in full compliance with the current edition of BS7671 the IEE/IET Regulations and the Electricity at Work Act.

Mains Switch and Wiring (Intake retained & new switch fuse)

All electrical wiring, conduit and trunking is to be replaced throughout the installation. Should the Lift Contractor wish to retain any item he must seek and obtain the Engineer’s approval in writing.

The existing main isolation switches shall be retained and the new supplies diverted to the location of a new suitably rated lockable switch fuse isolation switch to be located within the vicinity of the control panel. The location of this may be either within the existing machine room or at the head of the shaft. In compliance with the earthing requirements of this Specification, an earthing conductor having a cross sectional area complying with the current edition of the BS7671 IEE/IET Regulations shall be provided between the distribution board and the lift control panels.

The Lift Contractor shall provide and install all necessary trunking, conduits, wiring and accessories from the main isolation point for the 3-phase and single phase supplies in the existing machine room to the installations.

Mains Supply Cable

The Lift Contractor shall test to satisfy himself that the existing electrical main supply riser cable is adequately rated, including earth loop impedance and the required number of conductors and earth conductors, and in a satisfactory condition to be re-used to supply the new lift installation and shall provide a certificate from a NICEIC Registered Electrician.

If the Lift Contractor should find that existing cable is not adequate, he shall allow for providing a new cable and show the cost for this in the appropriate part of the Fixed Price Summary.

The new cable to the new switched main isolator shall be p.v.c. sheathed XLPE insulated and steel wire armoured and all jointing and cleating shall be in full compliance with the current edition of BS7671 the IEE/IET Wiring Regulations.

Consumer Unit

The Lift Contractor shall provide a suitably sized electrical consumer unit to be located within each lift machine room and fed from a separate single-phase supply.  Should the existing main supply not be adequate, the Lift Contractor shall include for a separate suitably rated single-phase supply to be run from the intake room to feed this board.

All of the existing circuits are to be diverted and fed from the consumer unit. These include, but may not be limited to:

- Auto dialler/Communications Unit

- Car lighting.

- Machine room/machinery space lighting.

- Machine room/machinery space socket outlets.

- Shaft lighting.

- Shaft socket outlets.

Each sub-circuit shall be identified with an engraved label and protected by an MCB and an RCD designed to operate at 30mA.

Lift Machine Room Lighting (Retained)

The existing lift machine room lighting, both primary and emergency, is to be retained without alteration.

All retained, and any new, light fittings shall be fitted with suitable guards in accordance with the PUWER Regulations.

Machinery Lighting

The Lift Contractor shall install new fluorescent light fittings within the lift machinery area such as to provide a minimum level of illumination of 200 lux at any point within the machinery area. This lighting may form part of the lift shaft lighting and shall be controlled by a switch (or switches) located adjacent to the landing entrance access door(s) and/or machinery area access and shall be fitted at a convenient height.

The machinery area lighting shall provide the minimum levels of illumination in all areas of the machinery area such as meet the requirements of BS EN81-20 and the PUWER Regulations.

The fluorescent light fitting closest to the lift controller and/or equipment located within the machinery area shall be utilised as an emergency light and shall derive its alternative power source from an auto-recharge unit fitted with nickel-cadmium cells.  The unit shall have a minimum duration of 3 hours and a maximum recharge time of 12 hours.

The light fittings shall be suitably guarded in accordance with the PUWER Regulations.

Shaft Lighting (Existing Retained)

The Lift Contractor may retain the existing shaft lighting and, where found necessary to comply with the requirements of BS EN81-20, including minimum levels of illumination, modify the existing installation in order to comply with the provisions set out in BS EN81-20.

Prior to completion of the Works, all light fitting diffusers/lenses are to be removed, fittings thoroughly dusted out and the lenses cleaned and any defective lamps replaced.

The fluorescent light fittings at the top of the shaft and in the pit area shall each incorporate an emergency light facility, with an alternative power source derived from an auto-recharge unit fitted with nickel-cadmium cells.  These units shall have a minimum duration of 3 hours and a maximum recharge time of 12 hours.

The existing electrical supply to the shaft lighting shall be diverted from the existing source and connected to the consumer unit, which is being installed as part of these works.

The shaft light switch in the lift pit shall be readily accessible from the landing, and shall be located within 0.75 M of the inner edge of the landing entrance door frame and at a height not less than 1.0 M above the landing sill level.

Socket Outlets

The Lift Contract shall provide, within the lift machine room, machinery area/s, pulley room and lift pit, switched 13 amp three pin double socket outlets, each with integral RCD which shall be designed to operate at 30mA. The electrical supplies to these socket outlets shall be derived from the consumer unit located within the lift machine room/machinery area.

SCHEDULE OF EQUIPMENT

SECTION 6

# Schedule of Equipment

| Number & Type of Lift | 2 No. Electric Passenger lifts |
| --- | --- |
| Capacity | Min. 20 Person / 1500Kgs |
| Speed | 1m/s |
| Levels Served | B, G, 1, 2, 3 & 4 |
| No. of Stops | 6 |
| Machine Position | Within head of shaft |
| Location of Lift Machine room/Machinery Area | Within shaft. Control panels within existing machine room if feasible. |
| Drive Systems | Gearless VVVF |
| Duty Cycle | 180 Start per hour |
| Levelling Accuracy | +/- 3mm |
| Power Supply | Existing |
| Control Systems | Duplex full collective |
| Control Features | Fire recall (EN81-73). Provision to isolate car call pushes. |
| Signal & Operating Fixtures | In full compliance with EN81-70. Position indicators and direction arrows on all floors. |
| Car Dimensions | Maximum achievable within existing shafts. |
| Car & Landing Entrances | 2 panel centre opening. Clear opening 2000mm x 1000mm |
| Landing Frame | Small frame with steel infill side panels to duplicate existing arrangement. |
| Door Tracks | Brass |
| Architraves / Side Infill Panels | Coloured patterned stainless steel |
| Shaft Dimensions | As Existing |
| Arrangement | To suit equipment design |
| Minimum Clear Opening | 1000mm x 2000mm |

# Schedule of Finishes and Designated Materials

The successful Lift Contractor shall provide car design samples of all agreed finishes prior to manufacture or approval of the car design.  The samples shall be provided on a presentation board produced from A4 size white card.

Each selected finish shall be fully described on the presentation board inclusive of British Standard or manufacturer’s numbers and codes were applicable.

Materials applied for the car interior décor shall be designed and manufactured in accordance with the requirements of BS EN13501-1 as follows:

Car Flooring – Cfl-s2

Car walls – C-s2, d1

Ceiling – C-s2, d0

Mirrors or glass materials shall be designed, constructed and installed such as to comply with the requirements of Mode B or C of BS EN12600, and Annex C should the material become broken.

## Schedule of Finishes and Designated Materials

| Floor Covering | Amtico Heavy Duty Vinyl to Selection |
| --- | --- |
| Landing doors & architraves Landing push stations & indicator back plates Car doors & car front Lower car walls Car operating panel | Rimex Colour Tex Range or Steel Color Coloured Patterned range NB – Final finishes subject to change but contractors are requested to price on the above ranges |
| Upper side car walls | Back painted glass – RAL colour to selection |
| Rear car upper wall | Single piece silver tint clear safety mirror |
| Car ceiling | White Painted aluminum flat suspended ceiling with oversplill LED lighting to 4 sides and 2 No. LED linear downlighters both incorporating emergency lighting. |

### Car Interior

The Lift Contractor shall state the maximum weight of finishes allowed for in Section 10.

| Car Capacity Details | The details of capacity expressed in metric terms in compliance with BS EN81-20 and BS 5655 requirements shall be engraved in the car station panel and filled with an epoxy resin, colour to approval. |
| --- | --- |
| Operating Panel | Stainless steel as detailed above. Flush mounted with car wall. Car preference key switch. Alarm, open door and close door push buttons. Alarm and open door push buttons to remain illuminated under loss of main power supply. LCD floor position indicator. Car call acceptance indication. Full compliance with EN81-70. To be located in right hand side car wall. Lift serial No. to be engraved in the car station panel and filled with an epoxy resin, colour to approval. NB – Provision to isolate individual car calls to be provided. |
| Front Wall | As detailed above |
| Side Walls | As detailed above |
| Rear Walls | As detailed above |
| Hand Rail | Brushed stainless steel tubular handrail to both side walls. Design and installation in accordance with EN81-70. |
| Ventilation | Ventilation apertures shall be provided at the upper and lower levels. These shall be designed such as to prevent the passing of a rigid rod of 10 mm in diameter from the car interior, and shall be protected on the exterior of the car by the provision of deflectors to prevent foreign objects being passed through. The effective area of ventilation apertures shall be not less than 1% of the available car area at each of the upper and lower apertures. Clearance around the lift car doors may be utilized to provide up to 50% of the required effective area. Forced ventilation is to be provided from an exhaust fan mounted on the car roof and it shall be fitted with covers to afford protection against accidental damage by personnel, both internally and externally. The type and design shall be submitted for approval. It shall be designed to provide a minimum of five air changes per hour and is to be controlled by a key switch in the car station suitably engraved to depict its use. With the key switch in the off position, the fan will be connected into the emergency alarm circuit and operation of the alarm will cause the fan to come into operation. A variable timer is to be provided with an operating range of zero to 45 minutes and after operation of the alarm, the fan will continue to operate for the duration of the timer setting. |
| Suspended Ceiling | White painted aluminum flat suspended ceiling with overspill lighting to 4 sides and 2 x LED linear down lights including emergency. |
| Lighting | The design of the lighting shall be such as to provide a minimum lighting intensity of 100 lux on the control devices and at any point 1 M above the floor and not less than 100 mm from any wall. |
| Skirting | Rimex Colour Tex Range or Steel Color Coloured Patterned range |
| Floor covering | Amtico to selection |

## Final car details must be submitted for approval

Car Interior (Equality Act 2010)

The lift car interior shall comply fully with the requirements of BS8300 and BS EN81-70 including but not limited to:-

- All wall finishes shall be non reflective and contrast with the floor covering.

- If the space within the lift car is inadequate to allow a wheelchair to be turned around, (i.e. less than 1500 mm x 1500 mm), a safety mirror shall be fitted on the rear wall of the lift car in order to aid wheelchair manoeuvring.

- Mirrors shall incorporate measures to avoid creating confusion for lift users with impaired vision, including a minimum vertical distance of 300 mm between the floor of the lift car and mirror.

- Each lift car shall have a handrail on at least one side wall. The rail shall have a cross sectional dimension of between 30 mm and 45 mm, with a minimum radius of 10 mm for gripping and a minimum projection of 35 mm clear.  The centerline of the handrail shall be positioned 900 mm above the lift car floor + 25mm and projecting ends shall be closed and turned inwards in order to reduce risk of injury.

- The design of the lighting shall be such as to provide a minimum lighting intensity of 100 lux on the control devices and at any point 1 M above the floor and not less than 100 mm from any wall. Spotlights should be avoided.

- The light fitting nearest the car operating panel shall act as an emergency light in the event of failure of the normal lighting supply, and shall include an alternative supply from an auto recharge unit fitted with maintenance free nickel cadmium batteries.  The light shall provide a minimum lighting intensity of 5 lux for 1-hour measured at a point 1 M above the floor in the center of the lift car. The minimum duration for the light shall be 3 hours with a maximum re-charge time of 12 hours.

- Lift car interior operating panel to be a minimum of 400 mm from any adjacent wall. The alarm and door open push buttons, which shall be the lowest of the push buttons in the lift car, shall be positioned at a height not less than 900 mm above the car floor. The operating pushes shall be positioned at a height of between 900 mm and 1200 mm above the lift car floor. Two car operating panels to be used in larger lifts.  Single operating panels to be on right hand side wall, for centre opening doors and on slam side for side opening doors.

- The pushes shall be tonal contrast to the panel and the panel to the surrounding wall. An LED call registered illuminated signal shall be incorporated within the halo symbol of each push and each push button shall incorporate an audible signal to confirm operation. The Exit floor push shall protrude 5mm beyond the other floors and be coloured green, with green illumination. The Alarm button system shall be provided with an additional yellow illuminated pictogram to indicate the alarm has been given, and a green illuminated pictogram to indicate that the alarm has been registered. The key operated independent service switch shall, when switched to ‘Independent Service’, isolate the lift car from all landing calls. The lift car shall respond to only to car interior calls, and on a single call basis only, and shall park with the doors open. The key operated car interior light switch shall be suitably shrouded and incorporate a test position for the lift car emergency lighting.

- Operating panels shall be a tonal contrast from surrounding wall.

- An alphanumeric digital lift car position indicator, or alternatively a scrolling message type position indicator, shall be provided within each lift car operating panel at a height between 1600 mm and 1800 mm above the lift car floor.  The visible part of the floor numbers shall be between 30 mm and 60 mm.

- Materials causing allergies shall not be used in the lift car or landing fittings.  In general these are detailed in BS EN 81-70 but are not exhaustive.

- Car ventilation shall be designed so that it is able to be easily cleaned on a regular basis.

Car Décor

The car enclosure shall be designed and constructed in accordance with the requirements of BS EN81-70 and BS EN81-20.

All materials used in the design and construction of the lift car enclosure and roof shall be non-flammable.

Materials applied for the car interior décor shall be designed and manufactured in accordance with the requirements of BS EN13501-1 as follows:

Car Flooring – Cfl-s2

Car walls – C-s2, d1

Ceiling – C-s2, d0

Mirrors or glass materials shall be designed, constructed and installed such as to comply with the requirements of Mode B or C of BS EN12600, and Annex C should the material become broken.

TECHNICAL SPECIFICATION

SECTION 7

PREFERRED EQUIPMENT

Following considerations of the intent of the project to provide high quality installations suitable for intensive use along with the technical issues the reduced head room and pit depth pose the supplier and equipment below are considered to offer the preferred solution.

This issue has been discussed and agreed in conjunction with National Museums Liverpool and has been based upon a review of recent installations and the performance of suppliers and their ability to provide an effective technical solution and offer the required level of support throughout the procurement and installation phases of projects.

| Supplier | Berchtenbreiter GmbH Contact tim.smith@berchtenbreiter-gmbh.de |
| --- | --- |
| Hoist Machine & Drive | Ziehl Abegg |
| Lift Control Panel | New Lift or Kollmorgen |
| Car Door operator | Selcom Pegasus Plus |
| Landing Entrances | 2 Hour Fire rated Selcom Pegasus |
| Car & Landing Pushes | New Lift or Lift Store |
| Signalisation | New Lift or Stentorgate |
| Safety Gear | Cobianchi |

Alternative solutions may be considered providing they offer an equal or better level of quality to the preferred equipment detailed above. The decision of the client and Tuv-Sud Dunbar Boardman as to the accepted solution will be final.

7	INFORMATION FOR APPROVAL, NOTICES AND TECHNICAL SPECIFICATION

Information for Approval and Notices

The Lift Contractor must take all necessary dimensions on site during the progress of the works.

Before commencing work, 2 copies of the following working drawings shall be submitted for approval of the Engineer.

Item	Description

- General arrangement and builders work detail, shaft and machine room.

- Car enclosure, car doors, landing entrance complete with frame fixing details (where applicable).

- Car design, Perspective and Manufacturing Drawings.

- Sketch drawing of proposals for landing protective hoardings.

- Car operating panel engraving details.

- Landing push and indicator details.

After approval 2 copies of each shall be submitted for use during the duration of the Contract.  Electronic copies shall also be provided in Auto Cad 2000 format or equal as advised.

The Lift Contractor shall submit, no later than the date of submission of the initial General Arrangement Drawings, a schedule of the electric power and lighting requirements for the lift installations.

The information shall be complete in all respects and will include confirmation of the kW ratings, full load and starting currents, fuse ratings, permitted volt drop and a line diagram of the switch gear arrangement in the machine room, for the 3-phase and single-phase supplies.

Any additional requirements for ancillary equipment, such as communications or diagnostics, shall be fully detailed with all information on cabling and terminations.

On completion of the work, the Lift Contractor shall provide and fix in the machine room a suitably mounted “straight line” and “as wired” set of wiring diagrams of all electrical apparatus of the lift as actually wired and fitted and showing the arrangement and markings of all connections.  These diagrams shall be plastic encapsulated or equivalent finish to approval.

Similarly, nomenclature detailing all symbols and forms of identification used on the equipment drawings or circuit diagrams applicable to the equipment, encapsulated in plastic of equivalent to approval, shall be mounted alongside the circuit diagrams.

Full information in respect of the heat output and operating temperature range of the equipment is to be provided.

## Notices

All danger, warning or advisory notices as may be required by LOLER or PUWER, and by BS EN 81-20, BS EN81-50, BS EN81-72, BS5655 and BS7255, which are applicable to this Contract, shall be provided and installed by the Lift Contractor.  These shall comply in all respects with the requirements of British Standards and shall be relief engraved on plastic laminate or equivalent material with 12 mm minimum height lettering.

All notices shall be screw fixed.  Self-adhesive notices will not be accepted.

Hand Winding Notice (Machine Room-less)

The Lift Contractor shall provide and install diagrammatic and written hand-winding instructions which shall be mounted in an appropriate and prominent position where these may easily be read when carrying out emergency hand-winding operations.

The instructions shall be specific to the site and to the lift equipment and machinery installed.

The notice shall be a minimum of 500 mm wide x 500 mm high and shall be in English and clear and legible.

The design of the notices shall comply in all respects with the requirements of BS EN81-20, BS EN81-50, BS5655, BS7255 and LOLER and PUWER.

Notices (Electrical)

The Lift Contractor shall supply and install, adjacent to the lift main switch fuse, an Electric Shock Notice, which is in accordance with the Electricity at Work Act,

The Lift Contractor shall supply and install a notice upon the electrical consumer unit which identifies the all of the circuits and their particular fuse ratings.

The Lift Contractor shall supply and install, to all electrical switches within the lift machine room and/or machinery areas, a permanently fixed label identifying their function.

MACHINE AREA (MACHINE ROOMLESS)

Lift Machine

The gearless machine shall comprise a slow speed traction sheave directly coupled to an electric motor and incorporating an electro-mechanical brake.  The whole assembly shall be carried on various steelwork mounted on up-stand piers of reinforced concrete or fabricated steel.  Transmission of vibration to the fabric of the building shall be prevented by the use of proprietary anti-vibration mountings.  The Lift Contractor is to ensure that his offer includes for all necessary steelwork to accommodate the lift machine. The lift machine shall be configured such as provide safe access for maintenance and adjustment processes.  The whole assembly is to be designed and tested to sustain contract load plus 25% over-load, and shall be designed constructed and installed in accordance with the requirements of BS EN81-20.

The hoisting motor shall be a Single Speed Low Slip AC Induction Motor, which is designed specifically for use with inverters, and rated for the duty set out in this Specification. The synchronous speed of the motor shall not exceed 1500 rpm. The design and construction of the motor shall be in accordance with the requirements of the BS EN60034 Standards.

Suitably designed motor protection shall be provided and shall be by way of thermistors which are embedded in the motor windings. Minimum of three separate thermistors shall be used.

The design shall be such as to incorporate an electronic sensor in the control system which shall be configured to monitor the motor speed control encoder/device such that the electronic sensor shall detect any error and/or fault condition which may arise and operate to isolate the motor electrical supply within 3 seconds of an error or fault condition arising.

The motor shall bear a name-plate which clearly sets out the manufacturer’s details together with the motor design information and serial number.

A suitable design permanent and resilient metal sign shall be installed at the hand-wheel end of the motor casing shall clear designate the direction of rotation and corresponding movement of the lift car.

All moving parts of the lift machine shall be suitably guarded in accordance with the requirements of this Specification and those of BS EN ISO14120 and BS EN81-20. All prime movers shall be painted in safety yellow.

The lift machine shall incorporate a means of manual operation the design and application of which shall be such that the manual effort required to move the lift car, in the empty car and loaded to rated load plus 10% conditions, shall not exceed 150 N.

In the case of a permanently installed flywheel/handwinding wheel this shall be guarded in accordance with the requirements of BS EN81-20 and the requirements of this Specification.

The direction of the lift car movement corresponding to the rotation of the handwinding wheel shall be permanently marked upon the lift machine, and in close proximity to the location of the handwinding wheel.

The brake release device together with any detachable handwinding wheels or tools shall be painted in safety yellow and shall be mounted upon a purpose made tool rack which shall incorporate clear and detailed instructions for use in relation to handwinding and passenger emergency release.

In cases in which the design of the lift machinery is such that the manual effort required to move the fully loaded lift car upwards is in excess of 400 N, and/or if no mechanical means of emergency operation in accordance with c.5.9.2.3.1 of BS EN81-20 is provided, the Lift Contractor shall supply and install a means of emergency electrical operation which is designed, constructed and installed in accordance with the requirements of Section 5.12.1.6 of BS EN81-20 and with the requirements of this Specification.

The lift machine brake shall be of spring applied, electrically released design and shall be of heavy-duty construction complete with the necessary brake shoe/pad to brake drum/disk contact surface area to suit the load and speed of the lift. The design of the brake shall be such that this shall incorporate no less than two separate brake shoes/pads which are configured such as to be self-aligning. Each brake shoe/pad shall incorporate its own specific actuation device and guided compression spring and housing. The lift machine brake shall, in all respects, be designed and constructed in accordance with the requirements of BS EN81-20 and BS EN81-50

The machine brake, unassisted by any other equipment of the lift, shall be designed such that this shall safely stop the lift machine when the lift car loaded with 125% of rated load, is travelling downwards at rated speed, such that the average retardation of the lift car shall not exceed that arising during safety gear and/or buffer operation.

The design of the lift machine brake shall incorporate redundancy such that all of the mechanical components of the brake, including any solenoid plunger, which are involved in the application of the braking action on the brake drum shall be provided in two separate sets. Each of the two sets of braking components shall be designed and constructed such as to apply a braking effort which is sufficient to decelerate, stop and hold the lift car, loaded at rated load and travelling downwards at rated speed; and when travelling upwards with the lift car empty.

The brake drum/disk shall be coupled by direct and positive mechanical means to the lift machine traction sheave, winding-drum or sprocket.

The lift machine brake solenoid shall be designed for a DC electrical supply sourced from suitably rated rectifiers in the lift control system. The supply shall be controlled by at least two electromechanical devices which shall be designed and applied in accordance with the requirements of Section 5.10.3.1 of BS EN81-20. These electromechanical devices shall be designed and configured such that if, whilst the lift is stationary, one of these has failed to open the electrical circuit to the machine brake solenoid, then further movement of the lift car shall be prevented. The effect of any stuck-at-failure monitoring of this system shall be such as to prevent further movement of the lift car.

Alternatively, the lift machine brake shall incorporate an electrical monitoring circuit which is designed and configured in accordance with the requirements of Section 5.11.2.3 of BS EN81-20. In case in which this method is applied the Lift Contractor shall provide a Certificate of Type Examination which is in accordance with the requirements of Section 5.6 of BS EN81-50.

The design shall be such that electrical current shall not be applied to the lift machine brake solenoid unless the lift drive motor has been powered. The brake shall be designed to apply instantly and automatically in the event of interruption of the power supply to the solenoid.

The lift machine brake shall be designed such as to incorporate a means whereby the brake may be released manually, by way of continuous manually applied pressure, in order to enable hand winding of the lift machine. The design and construction of the means of manual release shall be such that this cannot cause a failure of the braking function.

In cases in which the lift machine is installed within the lift well it shall be possible to test each of the braking sets from outside of the lift well.

Traction and Diverter Sheave

All lift machine traction sheaves and rope diverter pulleys shall be painted yellow, and suitably designed rope restraints shall be installed such as to prevent the suspension ropes from leaving the sheave/pulley grooves.

The lift machine traction sheave shall have sufficient diameter to ensure that the ratio between traction sheave and suspension rope diameter is not be less than 40:1.

The roping system shall be 2:1

Roping Arrangement (Machine Room-less)

Each lift shall be designed such that the lift car is configured in an underslung arrangement and applying a 2:1 suspension roping arrangement. Lifts cars configured in an overslung arrangement may also be considered, to suit the manufacturer’s standard arrangement, but subject to the approval of the Engineer.

Overhead rope diverter sheaves shall be located outside of the footprint area of the lift car in order to ensure safe operation, safe access for maintenance and to minimise headroom requirements.

The rope diverter sheaves which are located below the lift car platform shall be configured in a manner such as to minimise the effects of offset forces from the ropes and to allow the lift car to be satisfactorily statically balanced at all points in the lift travel.  All diverter sheaves shall have a minimum sheave to rope diameter ratio of 40:1.

The Lift Contractor shall supply and fix all necessary steelwork to support the diverter sheaves and suspension rope hitches for each lift.

The location for the governor shall be in the lift shaft.  The Lift Contractor shall provide a means to remotely trip and reset the governor from outside of the lift shaft.

Machinery Guarding – General Requirements

The design and construction of machinery guards shall meet with all of the requirements of Section 1.4 of The Supply of Machinery (Safety) Regulations 2008 and with the requirements of PUWER 1998, BS EN81-20 and BS EN81-50, the Lifts Regulations 2016 and EU Lifts Directive 2014/33/EU, and shall be fully compliant with the requirements of BS EN ISO14120: 2015 Safety of Machinery - Guards - General Requirements for the Design and Construction of Fixed and Moveable Guards.

All guarding shall be designed and constructed to offer adequate, clear and satisfactory viewing of the components guarded in order to meet maintenance, lubrication and inspection requirements. Wherever possible this shall be achieved without requiring the complete removal of the guard.

Machinery guards shall be designed to be of suitable size and weight to permit ease of handling and shall be designed such that these may only be removed with the aid of a tool.  The guards shall be designed in order that they do not cause hazardous crushing or trapping points with reference to parts of the machinery being guarded or other guards. Wherever practicable, guards shall be designed such that these are unable to remain in place without their fixings.

The guards shall be so constructed as not to have exposed sharp edges, corners or other hazardous projections.  Welded, bonded or mechanically fastened joints shall be of sufficient strength, number and spacing to ensure the stability and rigidity of the guard so that it remains secure under all foreseeable loading conditions.  In particular guards shall be designed to withstand reasonably foreseeable impact from parts of the machinery and any ejected solid or fluid materials.  All fastenings shall be fitted with lock nuts, spring washers or other features to ensure these are resistant to machinery vibration and remain attached to the guard/machine.

Guards shall be formed from materials that allow the protective properties of the guard to be maintained throughout the foreseeable life of the machinery.  Supports, frames and all infill materials shall be selected from a range to provide a rigid and stable structure and to resist deformation.  The materials selected for the construction of the guard are to be resistant to foreseeable oxidation and corrosion and other environmental factors. This may be achieved through the application of suitable protective coatings.

Guarding - Sheaves

The traction and divertor sheaves (and over-head and lift shaft pulleys) shall be guarded by suitably designed perforate, removable guards which shall be designed and constructed in full compliance with all of the requirements of Section 1.4 of The Supply of Machinery (Safety) Regulations 2008 and with the requirements of PUWER 1998, BS EN81-20 and BS EN81-50, the Lifts Regulations 2016 and EU Lifts Directive 2014/33/EU, and shall be fully compliant with the requirements of BS EN ISO14120: 2015 Safety of Machinery - Guards - General Requirements for the Design and Construction of Fixed and Moveable Guards.

All guarding shall be designed and constructed such as to offer adequate, clear and satisfactory viewing of the components guarded in order to meet maintenance, lubrication and inspection requirements. Wherever possible this shall be achieved without requiring the complete removal of the guard.

All guards must be securely held in place by fixing/securing systems which may be opened/released only by the application of suitable tools.  These fixing/securing systems shall remain attached to the guard when the guard is removed. Suitable tools shall be supplied and installed on the tool-board to ensure easy access for maintenance.

Brake

The lift machine brake shall be of spring applied, electrically released design and shall be of heavy-duty construction complete with the necessary brake shoe/pad to brake drum/disk contact surface area to suit the load and speed of the lift. The design of the brake shall be such that this shall incorporate no less than two separate brake shoes/pads which are configured such as to be self-aligning. Each brake shoe/pad shall incorporate its own specific actuation device and guided compression spring and housing. The lift machine brake shall, in all respects, be designed and constructed in accordance with the requirements of BS EN81-20 and BS EN81-50

The machine brake, unassisted by any other equipment of the lift, shall be designed such that this shall safely stop the lift machine when the lift car loaded with 125% of rated load, is travelling downwards at rated speed, such that the average retardation of the lift car shall not exceed that arising during safety gear and/or buffer operation.

The design of the lift machine brake shall incorporate redundancy such that all of the mechanical components of the brake, including any solenoid plunger, which are involved in the application of the braking action on the brake drum shall be provided in two separate sets. Each of the two sets of braking components shall be designed and constructed such as to apply a braking effort which is sufficient to decelerate, stop and hold the lift car, loaded at rated load and travelling downwards at rated speed; and when travelling upwards with the lift car empty.

The brake drum/disk shall be coupled by direct and positive mechanical means to the lift machine traction sheave, winding-drum or sprocket.

The lift machine brake solenoid shall be designed for a DC electrical supply sourced from suitably rated rectifiers in the lift control system. The supply shall be controlled by at least two electromechanical devices which shall be designed and applied in accordance with the requirements of Section 5.10.3.1 of BS EN81-20. These electromechanical devices shall be designed and configured such that if, whilst the lift is stationary, one of these has failed to open the electrical circuit to the machine brake solenoid, then further movement of the lift car shall be prevented. The effect of any stuck-at-failure monitoring of this system shall be such as to prevent further movement of the lift car.

Alternatively, the lift machine brake shall incorporate an electrical monitoring circuit which is designed and configured in accordance with the requirements of Section 5.11.2.3 of BS EN81-20. In case in which this method is applied the Lift Contractor shall provide a Certificate of Type Examination which is in accordance with the requirements of Section 5.6 of BS EN81-50.

The design shall be such that electrical current shall not be applied to the lift machine brake solenoid unless the lift drive motor has been powered. The brake shall be designed to apply instantly and automatically in the event of interruption of the power supply to the solenoid.

The lift machine brake shall be designed such as to incorporate a means whereby the brake may be released manually, by way of continuous manually applied pressure, in order to enable hand winding of the lift machine. The design and construction of the means of manual release shall be such that this cannot cause a failure of the braking function.

In cases in which the lift machine is installed within the lift well it shall be possible to test each of the braking sets from outside of the lift well.

Stop Switches (Machine Room)

The Lift Contractor shall supply and install a stopping device which is in accordance with the requirements of Section 5.12.1.11 and Section 5.11.2 of BS EN81-20

The design and construction of the stopping device shall be in accordance with the requirements of BS EN60947-1-1.

The Lift Contractor shall supply and install, on or near to the stopping device, a suitable sign marked ‘STOP’.

The stopping device shall be installed adjacent to the lift machine in a position and at a height where this is readily accessible to personnel in an emergency situation.

Hand Winding Equipment (Machine Room-less)

The Lift Contractor shall provide a suitable means by which the lift machine may be safely hand wound, in a controlled manner, from a suitable and safe position which is external to the lift shaft.

The means provided shall be designed and constructed in accordance with the requirements of BS EN81-20.

If the means is in any way reliant upon the lift car and counterweight being out of balance in order to achieve movement of the lift car then the lift contractor shall install a suitable means of ensuring that the lift car may be safely moved under an out of balance condition.

In the case of a detachable or removable handwinding device an electrical safety device, which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20, shall be installed at the lift machine such that the device is actuated whenever the handwinding device is attached to the lift machine, and that electrically powered movement of the lift machine is prevented whenever the handwinding device is attached.

The design and application of the means shall be such that the manual effort required to move the lift car shall not exceed 150 N.

In the case of a permanently installed flywheel/handwinding wheel this shall be guarded in accordance with the requirements of BS EN81-20 and the requirements of this Specification.

The direction of the lift car movement corresponding to the rotation of the handwinding wheel shall be permanently marked upon the device, in close proximity to the location of the handwinding point.

The brake release device together with any detachable handwinding wheels shall be painted in safety yellow and shall be mounted upon a purpose made tool rack which shall incorporate clear and detailed instructions for use in relation to handwinding and passenger emergency release.

Electrical Emergency Operation

The Lift Contractor shall provide an optional extra cost to supply and install a suitable electrical emergency operation system, which is designed and constructed in accordance with the requirements of BS EN81-20.

The system shall incorporate a separate battery power supply and automatic charging system, and shall be design and constructed such as to be capable of moving the fully loaded lift car, in either direction of travel, at a speed not exceeding 0.3 m/sec, to a landing such that passenger release may be safely effected.

The provision shall include a means to readily and accurately indicate the position of the lift car to the person undertaking the emergency operation.

In all cases a manually operated means emergency operation, which is designed and constructed in accordance with the requirements of c.5.9.2.3.1 of BS EN81-20, shall be provided in addition to the emergency electrical operation.

The means to operate the emergency shall be located in the lift machine room or, in the machinery cabinet or, in the emergency and tests panel.

The system shall incorporate a self-checking ‘fail safe’ facility in order to ensure full functionality and battery condition at all times. In the event of malfunction or failure a signal shall be initiated in the lift controller fault logging system (or BMS system if fitted) and the lift car shall home automatically to the nearest floor and park with its doors open.

Floor Level Indication During Hand-Winding

In order to assist emergency hand-winding/lowering operations, the Lift Contractor shall supply and install a unit which incorporates an activation switch, a digital lift car position indicator and an audible electronic sounder. The unit shall be installed adjacent to the lift machinery hand lowering device.  When the activation switch is placed in the “ON” position and the lift car is position which is within the unlocking zone of any landing, the digital indicator will read the floor of the particular landing and the audible sounder shall activate.  The unit shall have a separate electrical supply which is configured to supply a self-contained low voltage, auto re-charge battery pack with rechargeable nickel cadmium batteries.

The hand-winding activation switch is to be of the changeover type, with the normally open contacts configured to operate the audible sounder and the normally closed contacts configured to open the lift safety circuit preventing operation of the lift whilst the activation switch is in the ‘ON’ position.

Over-speed Governor (Machine Room-less)

A robustly designed and constructed overspeed governor complete with governor rope and tension pulley frame shall be provided. The design and construction shall be such that the overspeed governor rope and its terminations shall remain intact during engagement of the safety gear.

The design of the overspeed governor shall be such that the tensile force produced in the governor rope when the governor is tripped shall be at least twice the force necessary to operate the safety gear and in no case less than 300 N.

The design and construction of the overspeed governor shall be such that the maximum distance between tripping shall not exceed 250 mm relative to the movement of the governor rope.

The design, construction and installation of the overspeed governor, together with its associated components, shall be in accordance with the requirements of BS EN81-20. Electrical devices shall be designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20.

The overspeed governor shall be subject to Type Examination in accordance with the requirements of Section 5.4 of BS EN81-50, the Lifts Regulations 2016 and Directive 2014/33/EU, and a Type Examination Certificate which is in accordance with the requirements of c.5.4.3 of BS EN81-50 shall be provided and a copy retained in the lift O&M Manual.

The overspeed governor shall be designed such as to meet the requirements of the particular lift speed and safety gear design, and in accordance with the respective electrical and mechanical tripping speeds specified in BS EN81-20. The governor rope shall be easily detachable from the safety gear such as to ease testing and maintenance.

The pitch diameter of the overspeed governor and of its tension and diverter pulleys shall be no less than 30:1 in relation to the diameter of the governor rope.

The governor rope shall be tensioned by way of a pulley and tension weight which shall be securely guided. Breakage or excessive stretch of the governor rope shall be detected by an electrical device which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20.

The governor rope shall be designed and constructed in accordance with the requirements of BS EN12385-5 and with a minimum safety factor equivalent to eight times the tensile force generated in the governor rope and based upon a friction factor of 0.2 for traction governors.

The overspeed governor shall be located such that this is readily accessible and reachable for maintenance and testing purposes from outside of the lift well. This requirement may, with the agreement of the Engineer, be dis-applied providing that all of the following provisions are met:

- The design shall be such that the governor may be remotely tripped from outside the well, and;

- That the governor is readily accessible from the lift car roof or pit, and;

- The mechanical reset of the governor is automatic upon raising of the lift car, and the governor electrical devices may be reset by remote means.

A means shall be provided for testing purposes to allow the governor to trip when the car is travelling at normal speed.

The direction of rotation corresponding to the operation of the safety gear shall be permanently and indelible marked upon the governor.

Governors which incorporate adjustable speeds shall be sealed such that adjustment causes the seal to be broken.

Governor and pulley guards shall be provided and shall be designed in accordance with the requirements of BS EN81-20, BS EN ISO14120 and the requirements of this Specification, and such as to allow the governor trip mechanism and switches to be reset without the need for removal of the guard. The data plate details shall be repeated on the top of the guard.

Control Panels (Machine Room-less) – To be located within existing machine room

The control equipment shall be totally enclosed in a steel cabinet with louvered ventilation and hinged doors exposing all components for accessibility, and design and constructed in accordance with the requirements of Sections 5.10 and 5.11 of BS EN 81-20. Forced ventilation fans complete with suitable filters shall be applied wherever necessary in order to ensure the correct operating environment for the control components.

The control and drive system, together with its various elements of equipment and enclosures, shall be designed and constructed in accordance with the requirements of BS EN81-20, BS EN50274, BS EN60204-1, BS EN60529, BS EN60664-1, BS EN60947-4-1, BS EN60947-5-1, BS 60800-5-2, BS EN61810-1, HD60364-4-41, HD60364-4-42 and HD60364-6.

All main components including circuit boards, transformers, power supplies, relays, contactors, fuses, overloads and associated equipment shall be suitably identified, by way of permanent indelible labeling, and a nomenclature compatible with the circuit diagrams shall be provided.

The hoist/pump motor windings shall be protected by way of suitable thermistors which shall be electrically connected to detection units which are designed to provide a level of protection commensurate with the motor manufacturer’s recommendations.

All solid state/thermistor/micro-processor based control circuits shall be fed from electrical power supplies providing the correct voltage, and with all necessary over and under voltage and current protection devices, such as to ensure their correct and safe operation. Circuits shall be designed in accordance with current British Standard requirements such that in case of failure this is to a safe condition.

A device shall be incorporated within each controller which will detect a loss of one phase of main electrical supply or a reversal of the phases.  Where the device detects either of these conditions a switch, relay or contactor shall be rendered open circuit removing the supply to all relevant contactors and control panel circuitry, and preventing movement of the lift.

Lift speed regulation over the range between no load and full load shall be within 5% of the contract speed.

The entire lift installation shall run normally when the supply voltage varies to a limit of +10% and -6% of the declared supply voltage.

The electrical supply to the drive motor shall be controlled be at least two independent contactors. If, when the lift is stationary, the main contacts of one of the contactors should fail to fail to open any further movement of the lift shall be prevented. Alternatively a stuck-at-failure monitoring system shall achieve the same result. Alternative systems of protection, which shall be designed and constructed in accordance with the requirements of BS EN81-20 may be proposed of the approval of the Engineer.

The controller shall prevent the lift machine starting unless the car door is in the closed position and all landing doors are in the closed and locked position.

A means of lift position indication based upon a digital display shall be provided within the control panel.

Permanent provision shall be made for inserting lift car and landing calls within the cabinet and this shall remain accessible and functional at all times, and for isolating landing calls, remote commands and to disable automatic door operation.

An inspection control station which is designed and constructed in accordance with the requirements of Section 5.12 of BS EN81-20 shall be incorporated in each of the control panels. The lift shall remain in inspection mode until all inspection control stations are set to the normal operation condition.

A landing and car door bypass device shall be provided in the lift controller. The device shall be designed and constructed in accordance with the requirements of Sections 5.11.2 and 5.12.1.8.3 of BS EN81-20. The device shall be protected against unintended use and protected mechanically by means of a permanently installed robust and secure guard or by way of a plug socket combination. The device shall be marked ‘Bypass’ and that activation status of the device shall be clearly marked. When operated the Bypass Device shall: normal operation including that of automatic doors shall be prevented; the bypassing of the lift landing door contacts and locks and the lift car door contacts and locks shall be possible, although the simultaneous bypassing of both car and landing door contacts and locks shall be prevented; a separate monitoring signal shall be provided such as to provide a check that the car door is in the closed position during lift movements with the car door bypassed; movement of the lift car shall be possible only under inspection control operation or emergency electrical control operation;  and audible signal at the lift car (minimum 55 dB(A) measured 1 M below the lift car) and a clearly visible flashing light under the lift car shall be activated during movement of the lift car. In the case of manually operated doors or gates the simultaneous bypass of the landing door contacts and landing door locks shall be prevented.

The controller shall incorporate a device which is configured such as to verify the correct operation of the lift door contact circuits whenever the lift car is within the unlocking zone, the car door is open and the landing door lock is released. The device shall monitor the monitor the condition of the electrical device which proves the closed condition of the lift car door, the electrical device proving the locked condition of the landing door locking device and the monitoring signal associated with the ‘Bypass’ device, in order to detect malfunction and to prevent the normal operation of the lift.

Where required, and/or where required by this Specification, an Emergency Electrical Control Operation device shall be provided ,and shall be designed and constructed in accordance with the requirements of Section 5.12.1.6 of BS EN81-20.

All wiring within the control panel cabinet shall be properly and securely terminated.  Any spare wires which are run to the panel shall be properly segregated and insulated from any live circuits and components and shall be suitably identified.

A rubber isolation mat, which is design and constructed in accordance with the requirements of BS EN61111, shall be provided in front of the control panel cabinet and at the rear of the panel in case where access may be required.

Portable and/or hand held devices which permit the interrogation of the lift control system shall be provided to the Purchaser complete with detailed instructions for safe use of the device. The device shall be provided free of any additional charge, hire, rental, lease or license and the device and its associated software shall remain functional the service life of the lift installation.

The controller shall incorporate a means to detect the temperature of the lift machine room and configured such as to isolate the lift in accordance with the requirements of BS EN 81-20 should the temperature limit of the equipment be exceeded.

The control system shall be designed to meet the requirements of BS EN12015 and BS EN12016 in relation to Electro-Magnetic Compatibility (EMC).  A valid Declaration of Conformity shall be provided as evidence of compliance.

Drive System (VVVF)

The lift drive control system shall be of the variable voltage variable frequency AC type utilising full flux vector or direct torque control of an AC motor, to provide smooth, stepless acceleration/deceleration and stopping cycles and to achieve a floor level stopping accuracy of +5 mm.

The drive system shall be closed loop system utilising a tacho generator and/or digital encoder directly coupled to the hoist motor or geared machine high-speed shaft, to provide a speed feedback/motor shaft position reference.

Speed regulation between no load and full load shall be within 5% of the contract speed.

The entire lift installation shall run normally when the supply voltage varies to a limit of +10% and -6% of the declared supply voltage.

The electrical supply to the drive motor shall be controlled be at least two independent contactors. If, when the lift is stationary, the main contacts of one of the contactors should fail to fail to open any further movement of the lift shall be prevented. Alternatively a stuck-at-failure monitoring system shall achieve the same result. Alternative systems of protection, which shall be designed and constructed in accordance with the requirements of BS EN81-20 may be proposed of the approval of the Engineer.

The drive system shall prevent the machine starting, unless the car door is in the closed position and all landing doors are in the closed and locked position.

The control and drive system, together with its various elements of equipment and enclosures, shall be designed and constructed in accordance with the requirements of BS EN81-20, BS EN50274, BS EN60204-1, BS EN60529, BS EN60664-1, BS EN60947-4-1, BS EN60947-5-1, BS 60800-5-2, BS EN61810-1, HD60364-4-41, HD60364-4-42 and HD60364-6.

The drive system shall be designed to meet the requirements of BS EN12015 and BS EN12016 in relation to Electro-Magnetic Compatibility (EMC).  A valid Declaration of Conformity shall be provided as evidence of compliance.

Control System (Duplex Full Collective)

An interconnected duplex full collective control system shall be provided with the following features:-

- The system shall be microprocessor based and incorporate the facility for future installation of “fault logging” and remote monitoring equipment complying with BS EN627.

- Lift car and landing calls shall be registered and retained in the system after operation of the respective lift car or landing push button.

- The lift car and landing calls relative to the direction of lift car travel shall be cancelled marginally prior to or during the opening of the lift doors at the appropriate landing.

- Lift car calls shall be answered in the order in which destinations are reached, irrespective of the sequence in which these are registered.

- Whilst no calls are in the system any landing call registered shall be immediately responded to by the nearest available car.  If a landing call is registered whilst the lifts are already responding to other calls, then a lift car shall stop only in response to calls in the current direction of lift car travel.

- The lifts shall be arranged to park randomly at the last floor of call. A facility shall be provided for “homing” one of the lift cars to the main floor level, parking with its doors closed. This parking feature shall be readily disenabled if required without recourse to tools or devices.

- An adjustable timing device shall be incorporated in the system and which will allow a predetermined time for passengers to enter or leave the lift car prior to the lift doors commencing to close in respect to responding to a further landing call. The registration of a car call shall override this timer and the doors shall immediately start to close.  Operation of the landing push in the direction in which the lift car is set to travel shall cause the doors to immediately stop and to re-open.

Diagnostics

The lift control system shall incorporate facilities for fault and event diagnostics in the form of a microcomputer which shall be capable of being interrogated at the controller.  The information shall be presented as a digital display and, if coded, the appropriate key shall be listed on a label fixed to the interior of the controller and in the O&M Manuals.

The following list of faults and events shall be the minimum requirement, as detailed in BS EN627:

Code		Fault

00		No faults recorded.

01		Safety circuits interrupted.

02		Lock circuit interrupted whilst running.

03		Failure of normal door closing sequence.

04		Car stopped outside door unlocking zone.

05		Stuck call button.

06		Lift failed to start.

07		Low voltage on the lift logic supply.

08		Not allocated.

09		Failure of the self-test procedure.

10		Run-time limiter operated.

11		Position lost.

12		Excessive temperature of drive system.

13		Failure of normal door opening sequence.

Code		Event

40		No events recorded.

41		Main lift supply switched off.

42		Inspection control mode.

43		Fire service mode.

44		Data logging OFF (Engineer on site).

45		Car preference mode.

46		Emergency power operation.

Code		Alarm Code for Lifts

90		Alarm button pressed.

The record shall be held in the memory of the microcomputer in real time and shall be retained in rolling sequence of up to 5 timed occurrences of each of the listed fault or event. The system shall incorporate a facility for recognising and reporting that there have been more than 5 recurrences of any one fault or event and the first and last shall be retained in the memory.  Upon clearance of a fault, the date and time shall be recorded and the next occurrence of the fault shall be reported as the first.

The equipment shall be configured such that a micro-computer may be applied to interrogate the system and through a serial link to a remote location or modem into a communication network, whereby each lift may be interrogated.

The remote equipment shall be capable of receiving data transmitted in the following minimum format:

- V21 class 300 baud, asynchronous half duplex; and

- Standard ASC11 code.

The memory shall be maintained by a back-up battery supply against a mains power failure for a minimum of 100 hours.

If the information at the controller is accessed by a portable reader, then one such reader shall be supplied to become the Purchaser’s property, together with one copy of the operating manual containing a key to the codes and all operational and servicing information relevant to the diagnostics system.

Fire Alarm Automatic Recall (BS EN81-73:2016)

Behaviour of Lifts in the Event of Fire.

The lifts shall operate in accordance with the requirements of BS EN81-73:2016.

The lift controller shall be configured such as to include a fire recall mode which may be initiated on receipt of electrical signals provided by an automatic fire detection and alarm system, or where applicable, by way of the manually operated system.

The fire recall system shall be capable being activated by the operation of voltage free contacts or by way of a manually activated recall switch.

If, at the time of activation, the doors are closed, the lift car shall travel non-stop to the designated floor where the lift shall remain inoperable.

If, at the time of activation, the lift car is at a landing, other than the designated landing, with open doors an audible signal shall sound within the lift car and shall continue until the doors are closed. If after 20-seconds the doors are not closed the door protection devices shall be rendered inactive and the doors shall close with reduced kinetic energy, not exceeding 4 J, and with an acoustic warning signal in operation during the door closing cycle. The lift shall then travel non-stop to the designated landing.

If, at the time of activation, the lift car is descending, the lift car shall continue to the designated landing without stopping and on arrival the lift doors shall open.

If, at the time of activation, the lift car is ascending, the lift car shall decelerate and stop normally at the next available floor and shall then return to the designated landing where the doors shall open.

On arrival of the lift car at the designated landing an audible speech message and a visual signal, each indicating “Fire alarm – lift out of service – exit now”, shall be initiated within the lift car.   The doors shall remain open for 20-seconds after which the doors shall close and the lift shall be removed from service, with only the lift car interior door open and emergency alarm buttons remaining operational.

If the design of the building provides for more than one designated landing then separate pairs of volt free contacts, or suitable signalling system, shall operate in order to recall the lift car and park this at the appropriate designated landing following the same control sequence as is set out here above.

A prohibition sign, which is designed in accordance with the requirements of BS EN81-73, and based upon an International ‘NO ENTRY’ sign shall be provided on each lift landing in a position in which this is easily visible. An addition sign stating “Do not use lift in the event of fire” shall be installed in conjunction with the prohibition sign.

When the recall device is operated all of the lift safety devices shall remain operational, and all of the lift landing and lift car controls (excepting for the door open and emergency alarm push buttons) shall be rendered inoperative. All existing calls in the system shall be cancelled.

A visual signal located in the lift car operating panel shall be illuminated, and shall remain illuminated until the lift is returned to normal operation.

If at the time the recall device is activated the lift is on inspection control, under emergency electrical operation and/or under any other maintenance control, audible and visual indicators installed in the lift motor room, at each lift machinery space, on the lift car top, and in the lift pit shall automatically activate and shall remain activated until the lift is returned to normal control whereupon the lift shall immediately revert to fire recall operation, and the audible and visual signal shall cease.

All audible signals shall be designed and constructed to provide a sound level which is adjustable between 35 d(B) A and 65 d(B) A and shall be set at 55 d(B) A. The sound produced shall be such that this differs from other signals used on the installation in order to enable maintenance staff to easily identify the condition.

LIFT CAR FRAME AND ENCLOSURE

Car Frame

The car enclosure shall be carried within a steel frame which is of substantial construction, formed with angle and channel sections which are suitably braced and stiffened.  The lift car frame shall be designed and constructed such as to sustain a fully loaded car plus 25% overload, together with the dynamic loads and forces arising during use, during loading, and during safety gear and buffer operation, without permanent deformation. In the case of Goods Passenger Lifts, or Mobility Scooter use the calculation of the rated load shall be increased such that the design and construction of the lift car frame and plaftorm shall be such as accommodate the additional loads and forces imposed by the handling devices and/or Mobility Scooters.

During the operation of safety devices the lift car floor shall not incline in excess of 5% from its normal position under the full load range of the lift car.

The lift car enclosure shall suitably isolated from the lift car frame by way oil resistant isolation rubbers which are of suitable resistance and density.

On the underside of the lift car provision shall be include for statically balancing the lift car. The design and construction of the static balancing system shall ensure that the complete lift car and its attachments can be statically balanced without exceeding the design parameters relating to the overall weight of the complete lift car and sling assembly and the lift safety equipment.

A toe guard, designed and constructed in accordance with the requirements of Section 5.4.5 of BS EN81-20, and manufactured in not less than 16 SWG steel, shall be installed beneath the lift car sill complete with adequate bracing to the lift car platform steelwork. The toeguard and bracing shall be painted as detailed within this Specification.

All exposed metal work shall be painted with machine paint, in a colour to the approval of the Engineer, and as detailed in this Specification.

The design of the lift car frame, platform and entrances, including sills and mountings, shall be such as to accommodate the loads imposed during loading and unloading of the lift car and shall be designed based upon a minimum loading of:

In the case of Passenger Lifts 40% of lift car rated load;

In the case of Passenger Lifts which carry Class C wheelchairs and/or mobility scooters 60% of lift car rated load;

In the case of Goods Passenger Lifts 60% of lift car rated load.

A data plate shall be fitted to the cross head of the lift car frame which shall provide details of the suspension rope type, construction, diameter and length along with weight of the lift car and the contract speed all expressed in SI Units.

Car Enclosure

The car enclosure shall be constructed in zinc-coated mild sheet steel and each panel shall be flanged and bolted to give an enclosure of rigid and robust construction which is design and constructed in accordance with the requirements of BS EN81-20.  The exterior of the panels are to be treated with anti-drumming compound and noise absorption pads are to be fitted between the car frame and enclosure.  All exposed metal work to the exterior of the enclosure is to be treated with machine paint, in a colour to approval of the Engineer.

The design and construction of the car enclosure shall be such as to ensure that each wall of the lift car shall resist, without permanent deformation in excess of 1 mm and elastic deformation in excess of 15 mm, a force of 300 N evenly distributed over an area of 5 cm2 in round or square section and applied at right angles at any point from within the lift car.

The design and construction of the car enclosure shall be such as to ensure that each wall of the lift car shall resist, without permanent deformation in excess of 1 mm, a force of 1000 N evenly distributed over an area of 100 cm2 in round or square section and applied at right angles at any point from within the lift car.

The design and construction of the car roof shall be such as to have sufficient strength to safely support the maximum number of persons for who refuge spaces are provided under Section c.5.2.5.7.1 on BS EN81-20. And, the design and construction of the car roof shall be such as to ensure that this shall resist, without permanent deformation, a force of 2000 N applied at any position on an area of 0.3 M x 0.3 M.

The external perimeter of the lift car roof shall be equipped with a toe board which shall be of minimum height 100 mm.

The surface of the external car roof shall be of non-slip design and construction.

The lift contractor shall mark upon the car roof, using an indelible material, the locations of the refuge spaces and the extent of these.

All materials used in the design and construction of the lift car enclosure and roof shall be non-flammable.

Materials applied for the car interior décor shall be designed and manufactured in accordance with the requirements of BS EN13501-1 as follows:

Car Flooring – Cfl-s2

Car walls – C-s2, d1

Ceiling – C-s2, d0

Mirrors or glass materials shall be designed, constructed and installed such as to comply with the requirements of Mode B or C of BS EN12600, and Annex C should the material become broken.

The Lift Contractor shall submit a constructional drawing of the car bodywork for inspection and comment before proceeding with manufacture.

To ensure that vibration is not transmitted to the car enclosure, a minimum clearance of 3 mm shall be maintained between the car enclosure and the steelwork of the sling.

Car Top Balustrade

In all cases in which the distance between the outer edge of the lift car roof and the wall of the lift well, measured horizontally and perpendicular to the lift car roof, exceeds 0.3 M the Lift Contractor shall supply and install a balustrade in accordance with the requirements of BS EN 81-20.

The design and construction of the balustrade shall include; a handrail; an intermediate bar positioned at half the height of the balustrade, and; a toe board, of minimum height 0.1 M, fitted around the external perimeter of the lift car roof.

The height of the balustrade, in its fully extended position, shall be not less than 1.1 M and the balustrade shall be located at a maximum distance of 0.15 M from the edges of the car roof. The distance between the outer edge of the handrail and any component of the lift or part of the lift well shall in no case be less than 0.1 M.

The design of the balustrade shall be such that this shall resist, without elastic deformation in excess of 50 mm, the application of a force of 1000 N applied horizontally and at right angles at any point at the top of the balustrade.

In cases in which the available headroom clearance is insufficient to accommodate a barrier of 1.1 M in height a suitably designed extendable barrier, which is designed and constructed in accordance with the requirements of BS EN81-20, and which has been approved by the Lift Contractor’s Notified Body, may be applied. Such designs shall incorporate electrical interlock safety switches, which are designed and constructed in accordance with Section 5.11.2 of BS EN81-20, and configured such that the lift cannot be operated on ‘Normal’ operation whilst the barrier is extended, and such that the extension of the barrier is necessary in order to enable the lift car top inspection control operation.

A suitable warning notice shall be provided on each rail in order to warn of the danger of leaning over the rail.

The rail shall be manufactured in galvanised steel and suitably painted in a colour to the approval of the Engineer.

Lift Car Apron

An apron, designed and constructed in accordance with the requirements of Section 5.4.5 of BS EN81-20, and manufactured in not less than 16 SWG steel, shall be installed beneath each lift car entrance sill complete with adequate bracing to the lift car platform steelwork. The apron and bracing shall be painted as detailed within this Specification.

The apron shall extend for at least the full width of the clear landing entrance and shall extend vertically downwards by at least 750 mm. The lowest edge of the apron shall be formed to provide a chamfer of angle of at least 60° and which shall extend in the horizontal plane for not less than 20 mm.

Only countersunk screws will be accepted such that the surface, at all points on each panel, is smooth and flush. Any projections on the face of the apron shall not exceed 5 mm and any projections in excess of 2 mm shall be chamfered at least 75° to the horizontal.

The design, construction and installation of the apron shall be in accordance with the requirements of BS EN81-20 and such that this is capable of withstanding a force of 300 N, which is applied at right-angles to the fascia from the landing side, and at any point on the lower edge, and evenly distributed over an area of 5 cm2 in round or square section. The apron shall resist without permanent deformation in excess of 1 mm and without elastic deformation in excess of 35 mm.

Lift Car Apron BS EN81-21 – Electrically Deployed Extending Apron

If a fixed apron designed and constructed in accordance with the requirements of Section 5.4.5 of BS EN81-20 is not possible each car entrance sill shall be fitted with an extendable apron. The extendable apron, in its extended position, shall meet with the requirements of Section 5.4.5 of BS EN 81-20:2014, with the height of the fixed vertical section of the apron at least equal to the extension of the door unlocking zone above the landing sill.

In ALL cases in which a BS EN81-21 form of extending apron is employed each of the lift car doors shall be equipped with a locking device which is designed and constructed and installed in accordance with the requirements of Section 5.3.9.2 of BS EN81-20:2014.

The design and construction of the apron shall be such that this is retracted during normal lift operation and is automatically extended on the opening of any landing by way of the emergency unlocking key, and in the case of the isolation of, or a loss of, the electrical power supply. In each case the lift car entrance apron/s shall move automatically into the extended position.

The extending apron shall be equipped with a safety switch designed in accordance with the requirements of Section 5.11.2 of BS EN81-20 and which shall prevent normal operation of the lift whenever the apron is not in the fully retracted position.

The return of the apron to the retracted position shall be possible automatically in cases in which all of the lift landing entrance doors are closed and locked; or by manual intervention from the lowest landing, the pit floor or the lift car roof, by way of an appropriate means.

Whenever the apron is in the deployed or extended position a direction dependant electric safety device, which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN 81-20, shall prevent downwards movement of the lift car whilst under inspection and/or emergency operation whilst the lift car is positioned within the zone where the un-retracted lift car apron could come into contact with the pit floor.

General

The apron shall extend for at least the full width of the clear landing entrance. The lowest edge of the apron shall be formed to provide a chamfer of angle of at least 60° and which shall extend in the horizontal plane for not less than 20 mm.

Only countersunk screws will be accepted such that the surface, at all points on each panel, is smooth and flush. Any projections on the face of the apron shall not exceed 5 mm and any projections in excess of 2 mm shall be chamfered at least 75° to the horizontal.

The design, construction and installation of the apron shall be in accordance with the requirements of BS EN81-20 and such that this is capable of withstanding a force of 300 N, which is applied at right-angles to the fascia from the landing side, and at any point on the lower edge, and evenly distributed over an area of 5 cm2 in round or square section. The apron shall resist without permanent deformation in excess of 1 mm and without elastic deformation in excess of 35 mm.

The final design shall be subject to the approval of the Engineer.

Safety Gear (Traction)

A robustly designed and constructed safety gear shall be fitted to the underside of the lift car. The safety gear shall be of the progressive type and operated by a suitably designed overspeed governor which is designed and constructed to match the characteristics of the safety gear. The safety gear shall be designed, constructed and installed such that this is capable of safely stopping and sustaining the descending lift car complete with rated load, by locking this to the guide rails. The safety gear shall operate at the tripping speed of the overspeed governor and in the case of a breakage of the suspension means.

The design of the safety gear shall be such that this will release automatically by movement of the lift car in the upwards direction of travel and shall reset such that the safety gear is immediately enabled for further operation. The design shall be such that the release may be affected under all load conditions up to and including rated load.

The design, construction and installation of the safety gear, together with its associated components, shall be in accordance with the requirements of BS EN81-20. Electrical devices associated with the safety gear shall be designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20.

The safety gear shall be subject to Type Examination in accordance with the requirements of Section 5.3 of BS EN81-50, the Lifts Regulations 2016 and Directive 2014/33/EU, and a Type Examination Certificate which is in accordance with the requirements of c.5.3.5 of BS EN81-50 shall be provided and a copy retained in the lift O&M Manual.

In all cases the average retardation of the lift car in the case of free fall shall be between 0.2 gn and 1.0 gn.

In cases in which a bi-directional safety gear is installed such as to prevent uncontrolled ascent or unintended movement of the lift car, this shall comply in all respects with the above requirements excepting that when actuated, the overspeed governor and safety gear shall be designed such that engagement of the ‘upwards’ direction elements of the governor and safety gear shall be released by movement of the lift car in the ‘downwards’ direction.

Safety gears incorporate adjustable speeds shall be marked with the range of speeds and the instructions shall be included in the lift O&M Manual.

Protection against Unintended Movement of the Lift Car

The Lift Contractor shall supply and install a safety device which shall detect and prevent unintended movement of the lift car at a landing whilst the landing door is not in the locked position and the car door not in the closed position.

The device shall detect unintended movement of the lift car and shall by way of a suitably designed actuation system, cause the lift car to stop, and remain stopped, in accordance with the distance constraints set out at Section 5.6.7 of BS EN81-20.

The design, construction and installation of the safety device, together with its associated components, shall be in accordance with the requirements of BS EN81-20. Electrical devices associated with the safety device shall be designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20.

In the case that the lift machine brake is used as a means of preventing/stopping unintended movement this shall be designed and constructed in accordance with the requirements of Section 5.9.2.2.2. of BS EN81-20. The brake shall incorporate self-monitoring of correct lifting and dropping of the braking mechanism and verification of the braking force. The self-monitoring function shall be subject to Type Examination in accordance with the requirements of Section 5.8 of BS EN81-50, the Lifts Regulations 2016 and Directive 2014/33/EU.

The unintended movement device shall incorporate, in the form of specific system design, a means of detection, a means of actuation and a stopping means. Suitable stopping means may include: additional safety gears on the lift car or counterweight; lift machine sheave brakes; rope brakes or an equivalent to the approval of the Engineer.

The combined system of detection, actuation and stopping means shall form an integrated system which shall be subject to Type Examination in accordance with the requirements of Section 5.8 of BS EN81-50, the Lifts Regulations 2016 and Directive 2014/33/EU. .

The Lift Contractor shall state the type of device and the means detection, means of actuation and stopping means in Section 10 of this document.

Ascending Car Over-Speed Protection

The Lift Contractor shall supply and install a safety device which shall detect, prevent and stop uncontrolled ascent of the lift car.

The device shall be operational during normal lift operation and during manual rescue operations.

The design, construction and installation of the safety device, together with its associated components, shall be in accordance with the requirements of BS EN81-20. Electrical devices associated with the safety device shall be designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20.

The device shall detect uncontrolled ascent of the lift car and shall by way of a suitably means, cause the lift car to stop, and remain stopped, in accordance with the requirements set out at Section 5.6.6 of BS EN81-20.

In the case that the lift machine brake is used as a means of preventing/stopping uncontrolled ascent of the lift car this shall be designed and constructed in accordance with the requirements of Section 5.9.2.2.2. of BS EN81-20. The brake shall incorporate self-monitoring of correct lifting and dropping of the braking mechanism and verification of the braking force. The self-monitoring function shall be subject to Type Examination in accordance with the requirements of Section 5.8 of BS EN81-50, the Lifts Regulations 2016 and Directive 2014/33/EU.

The uncontrolled ascent protection device shall incorporate, in the form of specific system design, a means of detection, a means of actuation and a stopping means. Suitable stopping means may include: additional safety gears on the lift car or counterweight; lift machine sheave brakes; rope brakes or an equivalent to the approval of the Engineer. During operation of the device the retardation of the empty lift car shall not exceed 1 gn

The combined system of detection, actuation and stopping means shall form an integrated system which shall be subject to Type Examination in accordance with the requirements of Section 5.7 of BS EN81-50, the Lifts Regulations 2016 and Directive 2014/33/EU. .

The Lift Contractor shall state the type of device and the means detection, means of actuation and stopping means in Section 10 of this document.

Suspension Rope (Machine Room-less)

The requirements regarding suspension are as follows:-

- In the case of traction lifts at least four suspension ropes shall be used, and in the case of hydraulic lifts at least four suspension ropes for each hydraulic jack.  Their nominal diameter shall not be less than 11 mm with a minimum safety factor of 12:1 and which shall be calculated in accordance with the requirements of BS EN81-50: 2014 and calculated based upon the worst case scenario.

- The characteristics and tensile strength of the wire ropes shall be in accordance with the requirements of BS EN12385-5.

- Each of the ropes shall be independently attached at its termination. Terminations shall be designed and constructed in accordance with the requirements of BS EN 81-20: 2014 and shall be fitted with a means of equalization and an isolated car hitch by means of springs or other method to the approval of the Engineer.  The roping arrangement shall be 2:1.

- Acceptable means of termination include self-tightening wedge type sockets in accordance with the requirements of BS EN13411-6 or BS EN13411-7; ferrule secured eyes in accordance with the requirements of BS EN13411-3; or swage terminal in accordance with the requirements of BS EN13411-8. In all cases the design and construction of the rope termination shall be such as to achieve not less than 80% of the minimum breaking load of the rope.

- During the servicing of the lift it shall be possible, by means of adjustment of nuts on the rope terminations, to shorten the ropes by 150 mm or more. The design shall be such that the termination shall not work loose following installation or adjustment

- Following installation an anti-twist rope (6 mm) shall be fitted through the rope terminations in order prevent rotation.

- A data plate shall be fixed to the lift car cross head giving the details of the suspension ropes type, construction, diameter, length and lift car weight, all expressed in SI Units.

- Ropes and their terminations shall be installed in full compliance with the manufacturer’s data and instructions, a copy of which shall be made available at the request of the Engineer, and which shall be included in the Operation & Maintenance Manuals.

Alternative means of suspension will be considered only on the basis that the design has been formally approved by a Notified Body, and in accordance with EU Lifts Directive 2014/33/EU and the requirements of BS EN81-20 and BS EN81-50, and strictly on the basis that the Lift Contractor has provided full details of the proposed design at the time of Tender.

Load Weighing Devices (Duplex)

The car sling or platform shall incorporate an automatic load-weighing feature.  The device shall be operated when the lift car is overloaded such that lift operation is prevented whenever the load in the lift car reaches or exceeds 110% of the rated load.

When operated the device shall prevent normal starting of the lift car, including re-leveling (re-leveling shall remain operative in the case of hydraulically driven lifts) and prevent the closing of the lift doors. In the case of manually operated doors or gates these shall remain unlocked. The device, when operated, shall cancel any preliminary lift starting functions.

When operated the device shall cause an audible and visible warning signal, which shall be located within the lift car interior, and fitted in the car station, to be activated to indicate the ‘overload’ condition.

The design shall be such as to include a means of self checking and the device shall ‘fail to safe’ such that it is not possible for an overloaded lift to operate.

The load-weighing feature shall also detect when the car is loaded to 80% load and will cause the lift to by-pass other landing calls in the current direction of travel.  The final load figures shall be agreed with the Engineer during the Commissioning Tests.

The “overload” and “load weighing” switches may be fixed to the underside or top of the car sling but if mounted on the top, these shall be provided with suitable protection against damage.

Guide Shoes (Roller)

The lift car and counterweight shall be fitted with fully adjustable roller guide shoes.  The design of the shoe shall incorporate a keeper plate to ensure the retention of the lift car and counterweight in the correct relationship to the guide rails in the event of roller, tyre or bearing failure.  Contact pressure between the roller tyres and the surface of the guiderails, in all planes, shall be achieved by the provision of fully adjustable external springs in conjunction with slots in the fixing baseplate of the shoe assembly.  All bearings utilised shall be lubricated and sealed for life by the manufacturer.

Mechanic’s Control Station (Lift Car Top)

A Mechanic’s Control Station, which is in compliance with the requirements of Section 5.12.1.5 of BS EN81-20, and the requirements of BS7255, shall be installed on the lift car top.

The design of the Mechanic’s Control Station shall be in accordance with the requirements of c.5.12.1.5.2.4 of BS NE81-20.

The Mechanic’s Control Station shall incorporate an ‘Inspection Control Switch’ which is designed in accordance with the requirements of Section 5.11.2 of BS EN81-20. The Inspection Control Switch shall be of bi-stable design and shall be suitably protected against involuntary or accident operation. The inspection control switch

Switches which are of rotary design shall incorporate a mechanical means (non-friction) of preventing the rotation of the stationary element.

In addition the Mechanic’s Control Station shall incorporate direction push buttons, designated ‘UP’ and ‘DOWN’ and a push button designated ‘RUN’. These push buttons shall be suitably protected against involuntary or accidental operation.

The design and construction of these push buttons shall be such that these operate in a constant pressure mode. Movement of the lift car shall be possible only by way of simultaneous constant depression of the ‘RUN’ button and one of the ‘UP’ or’ ‘DOWN’ directional buttons. The design of the push buttons shall be in accordance with the requirements of c.5.12.1.5.2.3 of BS EN81-20, and these shall be configured such that operation of the ‘RUN’ and ‘UP’ or ‘DOWN’ buttons may be performed simultaneously by a person using only one hand.

The Mechanic’s Control Station shall incorporate a stopping device which is designed and constructed in accordance with the requirements of c.5.12.1.11 of BS EN81-20.

The Mechanic’s Control Station shall be design with a minimum level of protection of IPXXD in accordance with BS EN60529.

The Inspection Control Switch, when switched to the ‘INSPECTION’’ mode of operation, shall:

- Neutralise the normal controls of the lift;

- Neutralise the lift emergency electrical operation function;

- Disable the levelling and re-levelling functions;

- Prevent automatic operation of the lift door equipment; and

- Permit power operated closing of the lift doors by way of the operation of one of the direction push buttons of the Mechanic’s Control Station; or additional switches, incorporated into the Mechanic’s Control Station, and suitably protected against involuntary or accident operation, which control the operation of the doors.

- Prevent the lift car from overrunning the normal stopping positions.

- Maintain all lift safety devices in a functional and operational condition.

When in use the Mechanic’s Control Station shall limit the speed of the lift car to a maximum of 0.63 m/sec and, to 0.3 m/sec whenever the vertical distance above any standing area on the lift car top is 2.0 M or less.

In cases in which more than one Mechanic’s Control Station is provided (lift pit or machinery space, etc) and when more than one of these is switched to ‘INSPECTION’ mode, movement of the lift car shall be possible only by the simultaneous operation of the same control function switches of each Mechanic’s Control Station.

The Mechanic’s Control Station shall be located such that this is readily operable from within of horizontal distance of 0.3 M of a refuge space.

A stopping device, which is designed and constructed in accordance with the requirements of c.5.12.1.11 of BS EN81-20, shall be located in a readily accessible position and not more than 1.0 M from the entry point to the lift car top. This device may be that incorporated in the Mechanic’s Control Station if this is located with 1.0 M of the car top entry point, or may be a separate device.

Incorporated into the Mechanic’s Control Station shall be a switched 13 amp three pin socket outlet with integral RCD operated at 30mA.  A minimum 100 watt inspection lamp fitted with a protective guard shall be mounted on the Station and controlled by a switch fitted adjacent to it.

The inspection lamp, or an additional emergency light unit complete with protective guard, shall be provided with emergency backup by means of a battery and charger, giving a minimum 3 hours duration and maximum 12 hours recharge. The light shall provide a minimum light intensity of 5 lux for a minimum period of 1-hour, measured at the engineer alarm initiation device and at a point 1 M above the floor of the car roof at the centre of the car roof.

A lift car top communication system, designed and constructed in accordance with the requirements of BS EN81-20 and BS EN81-28, shall be incorporated into, or mounted adjacent to the Station, together with clear instructions as to its use.

Mechanic’s Control Station (Lift Well Pit)

A permanently installed Mechanic’s Control Station, which is in compliance with the requirements of Section 5.12.1.5 of BS EN81-20, and the requirements of BS7255, shall be installed in the lift well pit.

The design of the Mechanic’s Control Station shall be in accordance with the requirements of c.5.12.1.5.2.4 of BS NE81-20.

The Mechanic’s Control Station shall incorporate an ‘Inspection Control Switch’ which is designed in accordance with the requirements of Section 5.11.2 of BS EN81-20. The Inspection Control Switch shall be of bi-stable design and shall be suitably protected against involuntary or accident operation. The inspection control switch

Switches which are of rotary design shall incorporate a mechanical means (non-friction) of preventing the rotation of the stationary element.

In addition the Mechanic’s Control Station shall incorporate direction push buttons, designated ‘UP’ and ‘DOWN’ and a push button designated ‘RUN’. These push buttons shall be suitably protected against involuntary or accidently operation.

The design and construction of these push buttons shall be such that these operate in a constant pressure mode. Movement of the lift car shall be possible only by way of simultaneous constant depression of the ‘RUN’ button and one of the ‘UP’ or’ ‘DOWN’ directional buttons. The design of the push buttons shall be in accordance with the requirements of c.5.12.1.5.2.3 of BS EN81-20, and these shall be configured such that operation of the ‘RUN’ and ‘UP’ or ‘DOWN’ buttons may be performed simultaneously by a person using only one hand.

The Mechanic’s Control Station shall incorporate a stopping device which is designed and constructed in accordance with the requirements of c.5.12.1.11 of BS EN81-20.

The Mechanic’s Control Station shall be design with a minimum level of protection of IPXXD in accordance with BS EN60529.

The Inspection Control Switch, when switched to the ‘INSPECTION’’ mode of operation, shall:

- Neutralise the normal controls of the lift;

- Neutralise the lift emergency electrical operation function;

- Disable the levelling and re-levelling functions;

- Prevent automatic operation of the lift door equipment; and

- Permit power operated closing of the lift doors by way of the operation of one of the direction push buttons of the Mechanic’s Control Station; or additional switches, incorporated into the Mechanic’s Control Station, and suitably protected against involuntary or accident operation, which control the operation of the doors.

- Prevent the lift car from overrunning the normal stopping positions.

- Maintain all lift safety devices in a functional and operational condition.

When in use the Mechanic’s Control Station shall limit the speed of the lift car to a maximum of 0.63 m/sec and, to 0.3 m/sec whenever the vertical distance above any standing area in the lift well pit is 2.0 M or less.

In cases in which more than one Mechanic’s Control Station is provided (lift car top or machinery space, etc) and when more than one of these is switched to ‘INSPECTION’ mode, movement of the lift car shall be possible only by the simultaneous operation of the same control function switches of each of the Mechanic’s Control Stations.

The Mechanic’s Control Station shall be located such that this is readily operable from within of horizontal distance of 0.3 M of a refuge space.

A stopping device, which is designed and constructed in accordance with the requirements of c.5.12.1.11 of BS EN81-20, shall be incorporated into the Mechanic’s Control Station.

An electrical reset switch shall be provided and shall be configured such that this is operated from outside of the lift well, either by operation in conjunction with the emergency unlocking means provided to the door which gives access to the pit; or which located outside of the well and which is accessible to authorised persons only.

The return of the lift to Normal operation shall only occur when:

- The landing doors providing access to the pit are closed and locked;

- All of the stopping devices in the pit are set to their ‘Run or ‘Normal’ mode;

- When an electrical reset switch located outside of the lift well, is operated.

A lift well pit communication system, designed and constructed in accordance with the requirements of BS EN81-20 and BS EN81-28, shall be incorporated into, or mounted adjacent to the Station, together with clear instructions as to its use.

CAR SIGNAL AND OPERATING DEVICES

Operating Panel (Side Wall)

The lift car interior operating devices shall be incorporated within the side wall of the lift car and integral with it, in a position which is in compliance with the requirements of Part M2 of the Building Regulations and those of BS EN 81-70.  Faceplate designs will not be accepted.

A key operated independent service switch, door open push and alarm push buttons shall be provided in addition to the required lift floor call push buttons.

A visual indicator and audible buzzer shall be provided in order to signify “car overloaded”. The alarm and door open push buttons shall be permanently illuminated including under emergency lighting operation. The alarm and door open push buttons, which shall be the lowest of the push buttons in the lift car, shall be positioned at a height not less than 900 mm above the car floor. The operating pushes shall be positioned at a height of between 900 mm and 1200 mm above the lift car floor in order to aid accessibility.

The design of the push buttons shall be such as to meet the requirements of BS EN 81-70, and shall be in a single or double column arrangement and of the “micro” movement type.  The key switches, door open button and alarm button and the overload indicator shall all be of the same design and manufacture as the push buttons. Each push button shall be arranged to illuminate to indicate call acceptance and the method of illumination shall be by light emitting diodes (LED).

The pushes shall be tonal contrast to the panel and the panel to the surrounding wall.

An LED call registered illuminated signal shall be incorporated within the halo symbol of each push and each push button shall incorporate an audible signal to confirm operation.

The Exit floor push shall protrude 5mm beyond the other floors and be coloured green, with green illumination.

The Alarm button system shall be provided with an additional yellow illuminated pictogram to indicate the alarm has been given, and a green illuminated pictogram to indicate that the alarm has been registered.

The key operated independent service switch shall, when switched to ‘Independent Service’, isolate the lift car from all landing calls. The lift car shall respond to only to car interior calls, and on a single call basis only, and shall park with the doors open.

The key operated car interior light switch shall be suitably shrouded and incorporate a test position for the lift car emergency lighting.

An alphanumeric digital lift car position indicator, or alternatively a scrolling message type position indicator, shall be provided within each lift car operating panel at a height between 1600 mm and 1800 mm above the lift car floor.  The visible part of the floor numbers shall be between 30 mm and 60 mm.

All of the equipment shall be designed, constructed and installed in accordance with the requirements of B EN81-20 and BS EN81-70.

The car-operating panel shall incorporate the lift manufacturer’s name, the lift serial number, the CE Mark and the reference number of the Notified Body.

Emergency Signal (Audible Alarm)

An audible alarm signal shall be fixed in an approved position within 5 metres of the lift shaft or within the lift shaft.  A secondary alarm signal shall be provided on the roof of the lift car.  They shall give a minimum audible level of 90 dBA at 1 metre outside the shaft area.

The supply shall be obtained from an auto-recharge unit of approved make fitted with nickel cadmium batteries. Minimum duration 3 hours maximum recharge time 12 hours.

The Lift Contractor shall supply and fix the auto-recharge unit either in the lift machine room/machinery area or on the lift car roof.

The signal will be actuated by the “alarm” push in the lift car station.  A pair of volt-free contact terminals is to be incorporated for the emergency telephone function.

Emergency Auto Dialling

An auto-dialling emergency communications system which is designed, constructed and installed in accordance with the requirements of BS EN81-20, BS EN81-28 and the Lifts Regulations 2016 shall be provided in each lift car and electrically connected to the machine room/machinery space. The system shall include as a minimum:-

- A speaker unit shall be suitably mounted and concealed behind the lift car front panel. The unit shall be fitted with an integral steel baffle plate for protection against vandalism and a volume control which shall not be accessible from within the lift car.

- A call/speaker unit mounted on the car top and in the pit.

- A main power pack and control unit mounted on the lift car roof and connected to the speaker by communications grade cabling.

- The auto-dialler shall be activated by the operation of the “alarm” push and will then automatically dial the first of a sequence of pre-programmed telephone numbers.  When the operator answers, the system will allow two-way “hands-free” conversation and a pre programmed voice message shall identify the lift number and its precise location.  e.g. “Lift alarm activated on passenger lift 3 at Dunbar & Boardman House, 95 Spencer Street, Birmingham B18 6DA, please press star to acknowledge this call.”  This voice prompt shall continue at preset intervals until acknowledgement has been given. Two-way communication shall be possible throughout this period. If the call has not been acknowledged within an adjustable period of 30 seconds, the call will terminate and move onto the next number in the sequence.  Similarly, failure to connect with the first number will initiate dialling to the second pre-programmed number.  This cycle of automatic dialling shall continue to all programmed numbers until acknowledgement of the call has been registered.  When the call has been acknowledged then an adjustable call duration of 2 minutes will be allowed.  This period may be extended or the call terminated by following the advice of voice prompt messages.

- The following features will be incorporated:-

220-240 volt mains supply

8 hours battery back-up

3 programmable numbers to 10 digits

programming by portable programmer

3 second response delay

2 minutes time out per conversation

System generated self-test of auto-dialler, at least once every 3 days

BT approval

Voice enunciation of instruction, to minimise engraving.

- Provide an acoustic coupler or, when a remote proximity device is installed, an inductive loop system with sufficient field strength to be suitable for its purpose, along with suitable indication of its availability for hearing aid users.

- A green illuminated pictogram to indicate the call/alarm has been registered.

- Adjustable volume to ensure a sound level of between 35 and 65 dBA.

The Lift Contractor shall include for all costs of reprogramming the auto-dialler system and/or changing the telephone numbers in order to suit the Purchaser’s requirements, in the case that the Lift Contractor is not awarded the Maintenance Contract upon completion of the Defects Liability Period, or at any subsequent time.

Voice Synthesiser

The voice synthesiser shall be of the digital type capable of on-site programming and shall include, as a minimum, for the transmission of the following messages.

- Arrival at the floor and its designation.

- Preparing to depart.

- Doors about to close.

- Remove obstruction from the doors.

- Lift failed to start, please press door open push.

- Lift overloaded.

The synthesiser shall have an additional facility for incorporating and processing a further 10 separate phrases.

Final detail in respect of the voice type and the wording of the individual messages to be transmitted shall be subject to the Engineer’s approval.

The voice synthesiser shall have an inductive loop system with sufficient field strength to be suitable for its purpose, along with suitable indication of its availability for hearing aid users.

The sound level shall, as a minimum, be adjustable between 35 dB(A) and 65 dB(A), and with a facility to increase the sound level such as to meet site conditions. The final sound level shall be to the approval of the Engineer.

- Audio Induction Loop System

The Contractor shall provide an audio induction loop system in the car to assist the hard of hearing.

This shall be designed, constructed and installed in accordance with the requirements of BS7594 and BS EN60118-4: 2015 and shall be capable of providing a minimum magnetic field strength, over a covered area, of 100mA RMS per metre.

Induction loop system signage shall be provided on the car control station below the car load plate on the car operating panel. This shall be an engraved sign with blue infill. Stickers shall not be accepted.

The outputs of the speech synthesis unit and the emergency auto-dialler shall be linked into the loop system amplifier, via transformer isolated inputs, which shall provide a corresponding electric current in the loop, proportional to the source input signal. The electric current in the induction loop will produce a magnetic field which can be detected by hearing aid users with their hearing aids set on the ‘T’ or ‘MT’ settings.

The induction loop circuit shall also generate sufficient magnetic field strength at a height of not more than 1200 mm above floor level of the lift car, to ensure wheelchair users have equal benefit from the loop system, with minimal electrical interference.

The frequency response shall cover the range 80Hz to 5kHz ± 1.5dB relative to 1kHz at low level, measured as loop current with no metal loss correction.

The induction loop cable shall be run around the perimeter of the lift car ceiling in a concealed location, with non metallic containment, providing 300mm separation from electrical switching equipment on the car e.g. door operator, which may provide interference to the magnetic field.

In circumstances where the loop can only be installed above the car roof, the system shall include a “Metal loss correction” adjustment to compensate for the reduction in field penetration.

The induction loop field strength shall be tested as part of the commissioning procedures of the lift and demonstrated to the engineer using a calibrated Magnetic Field Strength Meter and Loop Listening Device.

Automatic Power Operation of Car and Landing Doors (with nudging)

The automatic door operator shall provide quiet controlled motion of the car and landing doors throughout the full extent of the opening and closing cycles.  A solid guard shall be fitted to the operator driving mechanism.  The whole of the operator and its associated devices shall be mounted on steel members forming part of the car sling and under no circumstances shall the operator be fitted directly to the car enclosure.  The following requirements shall also be maintained:-

- It shall be driven by an electric motor in both opening and closing directions and tested for compliance with BS EN81-20 in relation to closing force and for kinetic energy by using an approved device.  Any reduction gearbox shall utilise steel/bronze gearwheels.  Nylon/plastic gears will not be acceptable.

- Provision shall be made for the site adjustment of the opening and closing cycles of the car and landing doors and these adjustments shall be independent from each other.

- In the case of glass panel construction lift car and/or landing doors a device which limits the door opening force to 150 N and which stops the door in the opening cycle in the event of an obstruction shall be provided.

- Car doors shall only operate on normal service while the car is in the levelling zone of a particular floor.

- A “door open” button shall be provided in the car and it shall be operative only while the car is stationary with the car door coupled to a landing door.

- The design of the door operator shall be such that the prevention of the door closing movement shall initiate an automatic re-opening of the door.

- In the event of the doors being obstructed or held open, then after a pre-determined period, the doors shall close at reduced speed and an audible warning will sound until the doors are closed.  The lift shall normally “park” with the doors closed.

- Couplers shall be of the metal type of robust construction, being of the same manufacture as the door operator and landing locks.

- The design and construction of the door operator and associated equipment shall be such that when the lift car is stopped within the unlocking zone it shall be possible, applying a force not exceeding 300 N, to open the lift car and landing door by hand from the interior of the lift car, and from the landing once the landing door has been unlocked, either by the car door or by way of the landing locking device release key.

- The design and construction of the door operator and associated equipment shall be such that when the lift car is stopped within 1.2 M of a landing it shall be possible to open the lift car doors from the corresponding landing without the need for tools, other than for the landing locking device release key and/or a specific tool which is permanently retained with the lift installation.

- Car doors shall be fitted with a device to ensure that they remain closed and interlocked when the lift is outside the levelling zone. The device shall be designed and constructed in accordance with the requirements of Clause 5.3.9.2 of BS EN81-20: 2014 and shall be subject to Type Examination in accordance with the requirements of Section 5.2 of BS EN81-50: 2014 and the Lift Contractor shall provide a Type Examination Certificate which is in accordance with Annexe A of BS EN81-50: 2014.

Locking Devices and Switches for Car and Landing Entrances

The car door contacts, car and landing door locking devices and “pick-up” mechanism shall be of the same manufacture as the door operator and properly aligned for correct operation.

The landing and car doors shall be provided with electro-mechanical interlock devices, which shall prevent operation of the lift under any circumstances, unless all lift car and landing doors are in the closed position, and are locked both electrically and mechanically.

Provision shall be made for fully opening each landing door by an authorised person by the aid of a release key which shall be designed such as to fit an unlocking device which is incorporated into in one door panel.  The release aperture on the visible face shall be fitted with a 3 mm raised circular stainless steel bezel secured in position, or by way of a fixed escutcheon plate with a profile aperture suitable for the specific type of release key.  No fixing screws shall be visible from the landing.

The design of the release key shall be in accordance with Section 5.3.9.3 of BS EN 81-20: 2014, and shall be of steel section or cast materials and the access to each lock shall be restricted to this key.  The force necessary to operate and release the door shall be such that unauthorised use of the release mechanism (by the use of screwdriver, pliers etc) will not be possible.

In order to enable safe egress from the lift pit the Lift Contractor shall provide an additional, permanently installed device, which allows a person standing on the base of the pit to safely unlock the pit access landing entrance door. The device shall be designed and constructed in accordance with Clause c.5.3.9.3.5 of BS EN81-20: 2014.

All locking devices shall be designed and constructed in accordance with the requirements of Section 5.3.9 of BS EN81-20 and in particular Clauses c.5.3.9.2, c.5.3.13 and c.5.3.14 (lift car door devices); and Clauses c.5.3.9.1, c.5.4.9.4 and c.5.3.11 (lift landing door devices), and shall be subject to Type Examination in accordance with the requirements of Section 5.2 of BS EN81-50: 2014.

Lift Contractor shall provide a Type Examination Certificate which is in accordance with Annexe A of BS EN81-50: 2014.

The lock circuit voltage shall be given in the Tender Particulars in Section 10 of this Specification.  If this is designed to be in excess of 50v then suitable warning notices, in accordance with the relevant standards, shall be provided on each lock cover to warn of the hazard within.  Additionally, a suitable residual current device (RCD) or similar earth leakage circuit breaker shall be incorporated in the lock control circuitry to minimise the risk of electrocution.

Door Detector

The car door panels shall be fitted with an electronic device, which will provide a protective zone for the full width and height of the doors.

The principle of operation shall be an infra-red curtain of light. The device shall remain operational throughout the complete closing cycle of the doors to within 20 mm of the door closed position.  The device shall have the facility to detect persons and/or objects as these approach the entrance. The device shall be capable of detecting objects and/or obstacles of 50 mm in diameter. When the device is obstructed, it shall cause the doors to immediately stop and then fully re-open after which the doors will re-commence the normal closing cycle.

The device shall be equipped with green / red LED’s which will indicate doors fully open / doors closing.

Whenever the device is deactivated and/or in failure mode the kinetic energy of the combined lift car and landing doors shall be reduced to 4J or less and a distinct acoustic warning signal shall operate whilst the doors are closing.

The device shall fail safe in the event of a fault developing within the unit which results in door protection being lost.

The device location shall be given in the Tender Particulars in Section 10.

Car and Landing Doors (Fire Rated)

The lift landing entrances and doors and frames shall be 2-hour Fire Rated and subject to Fire Resistance Test in accordance with the requirements of BS EN81-58. The Lift Contractor shall issue a Test Report and a Declaration of Performance in accordance with the requirements of BS EN81-58.

Door panels shall be of double skin construction and the sheet steel shall be a minimum of 16 swg such as to assure the continuing integrity of these for the life of the lift installation and the prevailing site conditions.  The face of the door panels shall maintain a fixed running clearance in relation to the architrave or door entrance surround and provision for adjusting this dimension shall be provided.  All fixings and attachments of each individual door panel shall be adequately reinforced to ensure that distortion of the door panel cannot occur.

The design and mechanical strength of the lift car and landing entrance door panels and frames shall be such that these meet the requirements of Section 5.3.5.3 of BS EN81-20: 2014.

The lift car and landing entrance doors shall be equipped with devices which ensure that the door panels are retained in position in the event of failure of a guiding element. The door panels and retaining devices shall be tested in accordance with the requirements of c.5.3.5.3.4 of BS EN81-20: 2014 and of Section 5.14 of BS EN81-50: 2014. The Lift Contractor shall provide a Test Report in accordance with c.5.14.5 of BS EN 81-50: 2014.

When the doors are in the closed position the clearances between door panels, between door panels and uprights and lintels and sills shall not exceed 6 mm, which shall be measured from the back of any recess.

The clear entrance of landing doors shall match that of the car doors and in no case shall the clear entrance width of the landing doors exceed that of the car doors by more than 50 mm at any side.

Each panel shall be located in its bottom track by means of two sliding shoes, each having an offset vertical flange secured to the well side of the door, so that the shoe can be easily replaced without lifting the panel. In addition a robust mechanical retaining shoe/bracket, formed in metal, shall be incorporated into the design of each door panel such that the panel shall be securely retained in the sill in the event that the door shoes should fail or of physical impact to the door panel.

Each door panel shall be suspended from the top track assembly by hangers fitted with at least two polyurethane rollers with anti-friction bearings and a steel restraint boss to prevent the suspension becoming dislodged from the track.

The landing doors shall be provided with mechanical spring closers for automatic closing of the doors when manually opened.  At no time shall the springs operate in tension.

Each landing door panel to be fitted with a reinforced sight guard and the return edge shall be not less than 50 mm wide to mask the shaft side of the landing panel.  The guard shall be finished to match the doors.  No fixings to be visible on the exposed faces.

The non-driven door panels of each lift car and landing entrance shall be fitted with an electrical interlock, or alternatively, may be mechanically coupled in accordance with Sections 5.3.11 and 5.3.14 of BS EN81-20: 2014.  Any air cord inter-connections shall be of steel construction.

The design of the lift car and landing entrances systems, including sills and mountings, shall be such as to accommodate the loads imposed during loading and unloading of the lift car and shall be designed based upon a minimum loading of:

In the case of Passenger Lifts 40% of lift car rated load;

In the case of Passenger Lifts which carry Class C wheelchairs and/or mobility scooters 60% of lift car rated load;

In the case of Goods Passenger Lifts 60% of lift car rated load.

Landing Door Closers

The lift landing entrance doors shall be fitted with gravity weight closers which are designed and constructed such as to ensure self-closing of the doors when these are opened manually.  The gravity weights shall be retained in fully enclosed retaining enclosures such that the weight when in travel is suitably secure and is guided such as to ensure silent operation.

Car & Landing Sills

The lift car and landing entrance door sills are to be designed and manufactured in a heavy section brass or bronze extrusion.  The sills shall be securely bolted on to RSA angles which shall be fixed to the front wall of the lift shaft with proprietary fixings. The number of fixings used shall be calculated to accommodate the maximum point loading which may be applied.  Any packing between the brass or bronze and RSA sill or treadplate shall be continuous such that no voids shall exist on completion and that deflection of the sill cannot occur.

Landing Fascias

Fascia panels manufactured from a minimum of 16 SWG zinc-coated mild sheet steel shall be fitted between the header of each entrance and the sill of the floor above.

The panels shall be rigidly braced and any fixings or brackets used for mounting or to achieve rigidity shall be of steel.

The design, construction and installation of the fascia shall such that this is in accordance with the requirements of BS EN81-20 and such that this is capable of withstanding a force of 300 N applied at right-angles to the fascia, and evenly distributed over an area of 5 cm2 in round or square section, and applied at any point on the fascia, without permanent deformation, and without elastic deformation in excess of 15 mm.

The surface of the fascia panels and their joints shall be continuous and hard and smooth throughout the height and width of the shaft.

Each fascia panel shall exceed the full width of the widest entrance by 200 mm on either side.

Only countersunk screws will be accepted such that the surface, at all points on each panel, is smooth and flush

Following installation the fascia shall be site painted with hand brushing cellulose colour to match all other site steelwork.

Architraves (Stainless)

Architraves shall be provided at each level served and must be manufactured from 16 SWG stainless sheet steel.  After site erection, they shall be supported by form work and back filled with cement grout for a minimum of two thirds of their height, if required to meet the Fire Certificate.  Side and header members must be bolted together and welding will NOT be accepted.  Finish and pattern of material are as identified in the Finishes Schedule.

Landing Signal and Operating Devices (Duplex/Side by Side)

The landing signal and operating units shall comprise of robustly constructed steel or PVC back boxes, which are of rectangular form and let into appropriate cut-out preparations in the landing structural walls. The unit shall contain the push units and have cover plates manufactured from 12 SWG stainless steel.

The cover plates shall be secured by semi-secret fixings such as recessed captive grub or socket headed screws. Visible screw heads will not be accepted. Cover plates shall provide an adequate overlap of the wall box and the method of securing shall allow for adequate adjustment in order to overcome any error in the positioning of the back boxes.

Landing controls will be arranged as a single riser with a push station located on the central structural pier between landing entrances at each floor.

Each landing push station shall be fitted with one or two push units to suit the requirements of the control system.  The design and construction of the units shall be in accordance with the requirements of BS EN81-70. The units shall be positioned and arranged in accordance with the requirements of BS EN81-70. The visible section of each push shall incorporate a pressel, with a translucent halo and symbol, which are suitably finished to contrast in colour and tone with that of the cover plate.  Each push pressel shall be arranged to illuminate to indicate call acceptance.  The method of illumination shall be by light emitting diodes (LED).

Each push shall have an audible signal to confirm operation. The push stations shall be installed at a height which ensures a minimum dimension of 900 mm above Finished Floor Level to the centreline of any push and a maximum height of 1100 mm above Finished Floor Level the centreline of the highest push.

The push plate shall be in tonal contrast to the surrounding wall.

Tactile Symbols

All car and landing pushes shall incorporate tactile markings which are in accordance with the requirements of BS EN81-70 and on the pressel or adjacent to the push.  The means of achieving tactile markings shall be to the Engineer’s approval and full details are to be provided with the Tender.

The floor designation shall be a tonal contrast to the push pressel.  The pressel shall be a tonal contrast to the plate.

Each push shall have an audible confirmation of operation.

Each landing push plate shall have a tactile indication of the floor level.

Landing Position Indicators and Direction Arrows

Landing signal devices shall be provided at all floors and shall comprise of an alpha numeric display combined with an audible enunciator.

The display shall be of the LCD type to the approval of the Engineer, installed behind a tinted polycarbonate mask providing a display of alpha/numeric characters of minimum 40 mm in height. The enunciator shall be of a soft tone gong or electronic sounder design and shall be contained within the unit. The enunciator shall provide different sounds for ‘UP’ and ‘DOWN’ directions of lift travel e.g. one sound up, two sounds down.

As the lift car moves in the lift well its position shall be indicated by the changing the alpha numeric display.  As the lift car approaches the landing at which it is to stop in order to discharge or receive passengers, the tone shall sound in order to announce the imminent arrival of the lift car and the display shall switch to an arrow indicating the next direction of lift travel from the landing.  This directional signal shall be maintained until the lift doors close and the lift car moves away from the landing.

All other levels direction arrows with enunciators shall be provided having a matrix of LED’s or other display to match the main floor with a minimum visible height of 40mm.  These shall illuminate as the lift nears a floor where it is to stop and answer a call, to indicate the direction that the lift will depart from the landing and the enunciator will sound as above.

The lift position indicators shall be supplied as individual units and shall be located between 1800 mm and 2500 mm from Finished Floor Level, and adjacent to their respective lift landing entrances and shall be provided complete with cover plates to match those of the landing push stations.  The indicator shall be located above the entrance in the horizontal position.

The indicator shall provide an angle of view of at least 140 from any position in the lift landing lobby.

The devices shall be design and constructed in accordance with the requirements of BS EN81-70.

LIFT SHAFT, COUNTERWEIGHT & PIT

Guides and Fixings (New Lifts)

The Lift Contractor shall supply and install “T” section machined steel guide rails complete with purpose designed brackets, bolts and fixings, all designed, constructed and installed in accordance with the requirements of BS EN81-20 and BS EN81-50.

Both the lift car and counterweight sets of guide rails shall be plumbed and aligned with each other. And, “tram lining” will not be allowed.

The guide rail system, inclusive of brackets and fixings, shall be designed to suit the configuration of the lift shaft and the loads imposed by the lift, lift equipment and the means of loading of the lift car, including motorised wheelchairs.

The design and installation of the guide rail brackets shall be such as to accommodate settling of the building structure and/or shrinkage of concrete. The design and installation of the fixings shall be such as to prevent rotation which could release or compromise the integrity of the system

The vertical pitch of fixings and size of guide rails shall be selected and designed such as to accommodate the maximum loading that may be imposed upon this at any time and without excessive deflection of the guide rails.

The guide rails, fixings and the pitch of fixings shall be designed such that the maximum deflection criteria detailed in BS EN81-20 is not exceeded. The necessary proof calculations, based upon the BS EN81-50 method, shall be made available at the Engineers request. The Lift Contractor shall include for the possible failure of any non-metalic elements of the guide rail fixings in the calculation of permissible deflection.

The design of the guide rails, brackets and fixings shall be such as to accommodate the loads imposed during loading and unloading of the lift car and shall be designed based upon a minimum loading of:

In the case of Passenger Lifts 40% of lift car rated load;

In the case of Passenger Lifts which carry Class C wheelchairs and/or mobility scooters 60% of lift car rated load;

In the case of Goods Passenger Lifts 60% of lift car rated load.

Counterweight and Screen (New Lifts)

The Lift Contractor shall supply and install robustly constructed channel frame type of counterweight which shall be designed to securely house a number of multiple section filler weights commensurate with the design of the lift installation.

The filler weights shall be of either cast iron or flame cut mild steel construction.

The complete counterweight shall be balanced by the suspended weight of the lift car and its attachment together with 45% to 50% of the contract load of the lift car.

The Lift Contractor shall include provision for securely clamping the filler weights into position such that under no circumstances, including operation of the lift car or counterweight buffers, can the filler weights become dislodged from the counterweight frame.  The whole counterweight assembly shall be site painted with safety yellow proprietary machine paint.

In cases in which extension sections are attached to the bottom of the counterweight in order to provide an allowance for adjustment of the runby after normal stretching of the suspension ropes, these extension sections shall be fabricated from rolled steel sections, and shall be securely bolted to the underside of the counterweight and accurately aligned with the striking surface of the buffer(s).

The Lift Contractor shall supply and install, at the base of the counterweight guides, a counterweight screen rigidly constructed in expanded mesh in accordance with the requirements of c.4.2.4.1 of BS EN ISO 13857:2008.

The counterweight screen shall extend upwards from the lowest point of counterweight travel (including the stroke of the counterweight buffer), or a point not greater than 300 mm, whichever is the lower, to a minimum height of 2.0 M above the pit floor.

The counterweight screen shall extend for a minimum of the full width of the counterweight.

In the case that the horizontal distance between the counterweight guide rails and the wall of the lift well should exceed 300 mm the areas at the sides of the counterweight and counterweight guide rail shall be guarded using materials of the same design and specification as that of the counterweight screen.

In cases in which chain or rope compensation is applied that counterweight screen may be designed to accommodate slots which shall be of the minimum width necessary in order to safely accommodate the compensation.

The design and construction of the counterweight screen shall be such as to accommodate a force of 300 N evenly distributed over an area of 5 cm2 in round or square section, applied at any point on the screen, without deflection such that the screen should come into contact with the counterweight.

The design of the counterweight screen shall be such that a minimum clearance of 50 mm is maintained at all times between the lift car and the counterweight and their associated components and the screen.

The bottom of the screen shall be designed to assure easy access to the buffers, and to permit checking of run-by clearances, but such as to prevent inadvertent contact between personnel and the counterweight.

Buffers (Energy Accumulation)

The Lift Contractor shall supply and install energy accumulation (spring or polypropylene) buffers below the lift car and below the counterweight.

The design, construction and installation of the buffers shall, in all respects, be in accordance with the requirements of BS EN81-20.

The Lift Contractor shall supply and install all necessary associated steelwork for the mounting and fixing of the buffers.

Concrete supporting piers will NOT be acceptable.

The buffer mounting steelwork shall be of robust construction securely fixed between the respective lift car and counterweight guide rails and be of sufficient height to maintain the overtravels of the lift car and counterweight and the clearances required under BS EN81-20.

The design of the buffers shall be such as to ensure that the rate of retardation applied in order to safely arrest the fully loaded lift car and counterweight, is applied without undue discomfort to passengers or damage to the equipment.

In the case of buffers designs in which the buffers are mounted directly upon the lift car or counterweight a permanently installed, robust, steel pedestal, of not less than 300 mm in height, shall be securely fixed to the floor of the lift well pit in a position corresponding to each buffer impact point.

In the case of hydraulic lifts the stroke of the buffers shall be such that when the buffers are fully compressed that the ram of the hydraulic jack shall not contact the base of the hydraulic cylinder.

In the case of buffers with linear characteristics the stroke of the buffers shall be not less than twice the gravity stopping distance corresponding to 115% of the rated speed of the lift, but in no case shall the stroke be less than 65 mm. The design of the buffers shall be such that the buffer stroke shall be calculated to fall within that arising under the application of a static load of 2.5 and 4 times the mass of the lift car and its rated load, or of the counterweight,

In the case of buffers with non-linear characteristics the average retardation, calculated based upon the fully loaded lift car in free fall striking the buffer at 115% of contract speed, shall not exceed 1 gn; and retardation in excess of 2.5 gn shall be for no longer than 0.04 seconds; and with the return speed of the lift car not exceeding 1.0 m/sec; and without permanent deformation. In any case the maximum peak retardation shall not exceed 6 gn.

In the case of buffers with non-linear characteristics each buffer shall incorporate a permanently fixed data plate which sets out the name of the manufacturer of the buffer; the number of the associated Type Examination Certificate; and the type of the buffer.

A Certificate of Type Test, in accordance with the requirements of Section 5.5 of BS EN81-50, shall be provided in relation to buffers with nonlinear characteristics.

Restricted Headroom (EN81-21)

In all cases of a new lift installation in which the Refuge Spaces above the lift car are not in compliance with the requirements of, and the provisions set out at, Section 5.2.5 of BS EN81-20, the Lifts Regulations 2016 and in Directive 2014/33/EU, the Lift Contractor, in liaison with his Notified Body, shall seek and obtain a Derogation against the particular requirements and provisions from the relevant department of the UK Government. The Lift Contractor shall provide a copy of the Derogation to the Engineer.

In the case of a new lift the aforementioned provisions, together with any additional provisions which may be required, shall be formally approved, in writing, by the Lift Contractor’s Notified Body and any other additional items required from the Lift Contractor’s Risk Assessments.

Where the headroom restrictions of an existing lift well/installation prevent the attainment of the clearances and refuge spaces as are set out in Section 5.2.5.7 of BS EN81-20, the following safety features designed in accordance with the requirements of Section 5.6 of BS EN81-21 shall be provided:-

The Lift Contractor shall supply and install devices providing refuge spaces in the headroom together with and a safety system controlling the operation of the lift.

The devices shall be movable stops, or a pre-triggered stopping system.

The detailed design of the Lift Contractor’s proposed device/s shall be provided to the Engineer for approval.

Moveable Stops

In the case of moveable stops these shall be operated automatically such as to prevent damage due to collision when the stops are moved between the retracted and extended positions.

In the case of traction drive lifts the movable stops shall be installed under the counterweight and arranged to mechanically stop the lift car.

In the case of drum or chain driven lifts the movable stops shall be installed above the lift car and arranged to mechanically stop the lift car.

In each case the moveable stops shall be fitted with suitable buffers which are designed and installed in compliance with the requirements of Sections 5.81 and 5.8.2 of BS EN 81-20.

In the case of hydraulic lifts the movable stops shall consist of one or more devices which are external to the hydraulic jack and which are located outside of the projection of the lift car, but with the resultant force exerted upon the centre line of the hydraulic jack.  The design and construction of the movable stops shall be such that the average retardation of the lift car does not exceed 1 gn and, in the case of indirect acting lifts, such that the retardation does not result in a slack rope or chain situation.

Pre-Triggered Stopping System

Pre-triggered stopping systems shall include a triggering device which shall be designed, constructed and installed complete with a linkage type actuating mechanism which shall operate a mechanical stopping gear when the lift car reaches a fixed tripping point in the upwards direction of travel.

The triggering device shall be easily accessible such that examinations and maintenance may be undertaken in complete safety from the lift well pit, or from the roof of the lift car, or from outside of the lift well.

The pre-triggered stopping system shall be designed and constructed such that;

- the stopping gear is fixed on the lift car and acts upon the lift car guide rails;

- the system is tripped by a mechanical triggering device, formed of a mechanical linkage, for the tripping operation;

- the stopping gear shall be kept tripped by the triggering device and the linkage when the lift car is at any position above the tripping point;

- in the case of a release of the stopping gear due to dynamic effects or rescue operations this shall be reengaged when the car moves again in up direction above the tripping point keeping the required refuge space;

- the stopping gear shall be operated positively. Where springs are used these shall act by compression and where a rope is used the minimum breaking load of the rope shall be related by a minimum safety factor of 8 in terms of the tensile force created during operation of the stopping gear;

- the force required to activate the stopping gear shall be at least twice the engagement force of the stopping gear taking into consideration the tolerances due to friction, and in no case less than 300 N;

- the stopping gear shall operate an electric safety device which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN 81-20 whenever this is engaged;

- when the stopping gear has been tripped its return to normal operation shall require the intervention of a competent maintenance person;

- following its release the stopping gear shall be in a condition to operate;

- the system shall be designed and constructed such that the triggering device shall be protected against the accidental insertion of objects, dirt and corrosion;

- the pre-triggered stopping system shall be able to stop the car and keep it stopped from any speed between zero and the tripping speed of the ascending car overspeed protections means;

- the maximum retardation by the stopping gear shall not exceed 1 gn in the worst condition as validated according to Annex C of BS EN81-21;

- when the stopping gear operates the floor of the lift car, regardless as to whether any load is uniformly distributed, shall not incline by more than 5 % from its normal position;

- the pre-triggered stopping system shall be designed and verified according to the requirements in Annex C of BS EN81-21.

Clearances

When the buffering parts of movable stops are fully compressed, or when the lift car is stopped by the pre-triggered stopping system, the refuge spaces on the lift car roof and the clearances in the headroom shall comply with the requirements of Section 5.2.5.7 of BS EN 81-20.

Operation

The movable stops or the triggering device shall be operated:

- automatically at the latest when the safety system has been activated, or;

- manually.

Power Failure

In the case of power failure:

- in the case of automatic movable stops or an automatic triggering device these shall be activated and maintained in the active position up until the restoration of power supply or until a secondary/emergency power supply has been activated;

- in the case of manually operated movable stops or manually operated triggering devices a mechanical safety device shall maintain the lift car stationary. The device shall be activated and maintained in the active position at least up to the power restoration.

In the case of traction drive lifts which are equipped with manual operation of moveable stops or manual operation of triggering devices the mechanical safety device shall be operated by the safety system such as to prevent any movement of the lift car in the up direction if the movable stops or the triggering device is not in the active position.

Electrical monitoring

The movable stops or the triggering device shall be provided with electrical safety devices which are designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN 81-20:2014. These shall monitor:

- the fully extended (active) position, and;

- the fully retracted (inactive) position.

Safety system

An electrical safety device which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN 81-20 shall be provided such as to:

- activate a safety system that neutralises lift normal operation;

- be operated when any door/trap door giving access to the lift car roof is opened by means of a key;

- be bi-stable;

- be reset together with the resetting of the safety system.

In the case of lifts with hinged landing doors a second electric safety device according to EN 81-20:2014, 5.11.2 shall prevent any movement of the lift car if any door giving access to the lift car roof is open. This device shall not be accessible without using a tool.

The resetting of the safety system and the return of the lift to normal operation shall by operation of an electrical resetting device.

The resetting shall be effective only when:

- the lift is not in inspection operation;

- the stopping devices in the lift well pit and on the lift car roof are not in the STOP position;

- any door/trap door giving access to the lift car roof is closed and locked;

- the devices providing the refuge spaces are in the inactive position;

- any extendable balustrades on the lift car top are retracted.

A power failure shall not reset the safety system.

The electrical resetting device shall be:

- lockable with the use of a padlock or equivalent such as to ensure no inadvertent operation; and

- placed outside of the lift well and accessible to authorized persons only (maintenance, inspection and rescue); and

- monitored by an electrical safety device which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20 which prevents normal operation of the lift whenever the resetting device remains activated.

An additional electrical safety device which is designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20 shall interrupt movements of the lift car under inspection operation in up direction prior to any contact with the buffering parts of the movable stops and before the triggering device is tripped.

The lift car shall be stopped before the stopping gear is tripped.

This electrical safety switch shall allow the movement of the lift car only in the down direction.

In the position in which the car is stopped examinations, tests and maintenance operations in relation to all components which are located in the headroom shall be possible, in complete safety, from the lift car roof or from outside of the lift well.

Normal operation of the lift shall only be possible if the movable stops or the triggering device are in the inactive position and the safety system is not activated.

When the safety system has been activated, inspection operation shall only be possible if the movable stops or the triggering device are in the active position.

When the safety system has been activated, and the movable stops or the triggering device are not in the active position, emergency electrical operation shall only be possible in the downwards direction.

Visible and/or audible information

On opening, by means of a key of any door/trap door giving access to the lift car roof, a signal visible and/or audible from the landing shall clearly indicate the status (active and not active) of:

- the movable stops; or

- the triggering device.

In cases in which both ends of the lift travel are protected by movable stops and/or by pre-triggered stopping systems, the signal shall clearly indicate the status of the equipment at the top and bottom of the lift well.

The audible signal may be switched off after 60 s provided that the movable stops or the triggering devices are in the active position.

Groups of lifts

Where the horizontal distance between the edge of a lift car roof of a lift having reduced top clearances and the edge of the lift car roof of an adjacent lift(s) is less than 2.0 M a partition, which is designed and constructed in accordance with the requirements of Section 5.2.5.5.2 of BS EN81-20 shall prevent access to the lift(s) having reduced top clearances. The partition shall extend through the full depth of the lift well.

Car roof balustrade

Where the design of a lift is such that a balustrade is necessary on the lift car roof in accordance with the requirements of BS EN81-20, an easily and safely extendable balustrade shall be permanently installed.

The extendable balustrade shall meet the following requirements:

- the design and construction of the balustrade shall be in accordance with the requirements of Section 5.4.7.4 of BS EN 81-20, and shall be such that its fixings ensure that the balustrade remains in its extended position under the foreseeable vertical forces.

- the balustrade shall be designed in such a way that it can be totally unfolded/folded or extended/retracted while standing on a safe area;

- if the standing area is on the lift car roof this shall be:

      - in accordance with the requirements of Section 5.2.3.7.3 of BS EN 81-20;

      - clearly indicated and visible from the landing;

      - placed at a distance from the edge of the lift car roof not less than 0.5 M from where the risk of falling exists;

- electric safety devices which are designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20 shall prevent the movement of the lift car if:

      - in normal operation the balustrade is not fully retracted;

      - in lift car top inspection operation if the balustrade is not fully extended.

- In the case of emergency electrical operation and in inspection operation a direction dependant electric safety device designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20 shall prevent upward movements in the zone where the balustrade, if not folded or retracted, can collide with the ceiling of the lift well.

Limits and Switches

The Lift Contractor shall incorporate an “UP” limit in the lift control circuit such that when the mechanic’s lift car top control switch is set to the “INSPECTION” position and the “UP” button depressed, the upwards travel of the lift car shall be limited such that inspection and maintenance of any equipment at the top of the lift shaft may be safely undertaken, AND such as to ensure that safe egress is possible through the top floor landing entrance.

The lift control circuits shall incorporate terminal slow down switches and/or shaft limit switches which, in the event of a circuitry or selector malfunction, shall operate such as to safely slow and stop the lift, in a safe and controlled manner, at each of the terminal floors.

The electrical switches and/or devices used shall be designed and constructed in accordance with the requirements of Section 5.11.2 of BS EN81-20. The Lift Contractor shall identify the switches/devices and outlined the proposed operation of these, in the appropriate section of the Schedule of Technical and Constructional details of this Specification.

Stop Switches (Pit)

The Lift Contractor shall supply and install two stop switches in the lift well pit. One stop switch shall be installed in a position that is readily visible and easily accessible from the landing entrance and at a height of 1 M above the landing sill level and at a horizontal distance not greater than 0.75 M from the inner edge of the landing entrance door frame.

The second switch shall be installed such that this is visible and readily accessible and may be safely operated from a pit refuge space, and in no case shall the stop switch be position in excess of 1.2 M above the pit floor.

The stop switches shall be designed and constructed in accordance with the requirements of Section 5.12.1.11 of BS EN81-20 and shall be of mushroom headed, “push to stop, pull to release” type.

Restricted Headroom

Where the headroom restrictions of an existing installation prevent the attainment of the correct clearances and refuge spaces set out in Section 5.2.5.7 of BS EN81-20, the following safety features shall be provided:-

- Reduced headroom notices as detailed in this Specification.

- Suitable warnings in the Operating and Maintenance Manuals/Health and Safety File.

- Test limit as detailed in this Specification to stop the lift when on Inspection control.

- A suitably designed device which is designed, constructed and installed in accordance with the requirements of Section 5.5.2 of BS EN81-21: 2009. The design of the Lift Contractor’s proposed device shall be provided to the Engineer for approval.

- A means to detect the presence of a person on the car roof and prevent the lift from moving unless it is under maintenance control.

In the case of a new lift the aforementioned provisions, together with any additional provisions which may be required, shall be formally approved, in writing, by the Lift Contractor’s Notified Body and any other additional items required from the Lift Contractor’s risk assessments.

In all cases of a new lift installation in which the Refuge Spaces are not in compliance with the requirements of, and the provisions set out at, Section 5.2.5 of BS EN81-20, the Lifts Regulations 2016 and in Directive 2014/33/EU, the Lift Contractor, in liaison with his Notified Body, shall seek and obtain a Derogation against the particular requirements and provisions from the relevant department of the UK Government. The Lift Contractor shall provide a copy of the Derogation to the Engineer.

Pit Communications

A communications unit shall be provided in the lift well pit which will enable two-way communication with a permanently manned rescue service in the event of a person being trapped in the lift pit.

The unit shall meet with the requirements of c.5.2.1.6 of BS EN81-20.

The communication device may form part of the lift car trapped passenger and lift car top communication system.

The communication unit shall meet with the requirements of BS EN81-28.

The communication unit shall be located such that this is readily accessible from the floor loft the pit and that this is readily operable from the refuge spaces.

Clear instructions as to the use of the unit shall be provided on, or in close proximity to, the unit.

ELECTRICAL INSTALLATION METHOD (Conduit and Trunking)

The Lift Contractor shall install all necessary wiring, trunking and conduit for the lift from the main riser termination within the lift machine room.

All cables, except travelling cables in the lift shaft, shall be enclosed throughout their length in heavy gauge steel conduit or in steel trunking.

The use of existing trunking, conduit and fittings will not be acceptable.  All trunking runs shall be at high level and shall not run across the machine room floor.  All new trunking, conduit and associated fittings shall have a galvanised finish and made by a manufacturer having a licence to use the British Standard Institution Mark.

All travelling cables shall run direct from the controller to the lift car termination box.  Each flex shall be suspended from a clamp provided by the cable manufacturer with adequate protection to the cable coverings.  Excessively tight bends will not be acceptable.

In addition to the half way anchorage point for travelling cables, clamps shall be fitted so that there shall be not more than a 3 metre pitch between clamping points above the halfway point up to the machine room.

PVC coated kopex conduit shall be used only in cases where it is necessary to provide for adjustment or to reduce the transmission of noise and vibration.  The conduit shall terminate in suitable couplings which shall positively grip the flexible conduit and an additional earth continuity conductor shall be run inside the conduit between lengths.  Lengths exceeding 450mm shall not be allowed.

These cables shall be 450/750 volt and insulated with high temperature grade polyvinyl chloride and shall comply with BS 6004:2012.

All wiring must comply with the current edition of BS 7671 the IEE Regulations and shall be procured from a reputable manufacturer.

Provision shall be made within the travelling cables for any telephone cables necessary for the car communication system.

Factory manufactured wiring looms for site wiring will be allowed, providing detailed and accurate site dimensions are obtained from site for use during manufacture.  Any looms installed which have excessive length or are not generally neatly finished and installed, will be rejected and will have to be returned to the Lift Contractor’s manufacturing facility for re-manufacture at “the Lift Contractor’s own expense”.

All wiring, including trailing flexes, shall be insulated with low emission of smoke and halogen free cross-linked insulation, in compliance with BS 7211:2012, BS EN50525-1, BS50525-3-1 and IEC 332-1.

The Lift Contractor shall include for connection of all extraneous metalwork to earth bonding and lighting protection systems terminated in the lift pits.

Earthing

A separate electrical earth conductor shall be run in all conduits and trunking to every item of electrical equipment from the earth termination in the control panel.  This termination shall in turn be connected by means of a suitable conductor to the electrical mains supply earth point.

A separate earth conductor in at least one trailing cable shall be connected to the lift car equipment and to the control panel earth termination.

Each section of trunking shall be electrically and mechanically bonded to the earth conductor by means of brass screw, clamp washers, locking washer and nut.

Al of the earth points shall be identified using coloured tags.

Radio and TV Suppression

All electrical equipment shall be provided, as necessary, with suppressers, to prevent interference to radio, television and computer equipment within the premises in accordance with current British Standards and Telecommunications Guidelines.

The lift and lift equipment shall be design and constructed in accordance with the requirements of BS EN12015 in terms of EMC Emission, and with the requirements of BS EN12016 in terms of EMC Immunity.

Painting

All equipment shall be suitably prepared, primed, undercoated and then painted with an approved colour before shipment to site.  All shaft steelwork within the shaft shall be painted in two coats of machine paint following erection.  Any existing steelwork retained within the lift shaft, pit or lift machine room shall be wire-brushed, cleaned, primed, undercoated and then painted with an approved shade of machine paint.  Any damage to the painted surfaces which arises prior to completion shall be made good by the Lift Contractor.

Any new steelwork that will not be readily accessible after erection shall be painted with red oxide paint (or paint of similar protective quality) prior to installation.

7.55C	MRL Lifts Miscellaneous -

Machine room-less lifts shall comply in all respects with the requirements of BS EN81-20: 2014 and BS EN81-50: 2014.

The Lift Contractor’s attention is drawn in particular to the requirements of the above Standards in the case that lift equipment supplied is not contained wholly within the lift well or that the equipment is to be maintained from outside of the lift well, and/or by way of inspection doors, access hatches or similar.

Machinery Spaces Inside the Lift Well

Shall be designed and constructed such as to:

Permit easy and safe working on the equipment;

Provide a clear height of at least 2.1 M at all working areas;

Provide a clear height of at least 1.8 M for moving between one work area and another;

Provide a clear horizontal area of at least 0.5 M x 0.6 M at parts which require maintenance and inspection;

Provide a clear horizontal space at the front of control panels and cabinets which is not less than 0.7 M, measured from the front face of the enclosure, and the full width of the cabinet or panel, and in no case less than 0.5 M.

Include permanent lighting providing a minimum level of illumination 200 lux and incorporate emergency lighting in accordance with the requirements of this Specification.

Working Areas in the Lift Car or on the Lift Car Roof

Shall be designed and constructed such as to:

Include a permanently installed mechanical device which is designed and constructed in accordance with the requirements of c.5.2.6.4.3.1 of BS EN81-20 shall be provided;

Include clear instructions in relation to the safe deployment of the device which shall be provided at the Working Area and in the O&M Manual.

Include permanent lighting providing a minimum level of illumination 200 lux and incorporate emergency lighting in accordance with the requirements of this Specification.

Working Areas in the Lift Pit

Shall be designed and constructed such as to:

Include a permanently installed mechanical device which is designed and constructed in accordance with the requirements of c.5.2.6.4.4.1 of BS EN81-20 shall be provided;

Include clear instructions in relation to the safe deployment of the device which shall be provided at the Working Area and in the O&M Manual.

Include permanent lighting providing a minimum level of illumination 200 lux and incorporate emergency lighting in accordance with the requirements of this Specification.

Working Areas on a Platform

Shall be designed and constructed such that:

The platform shall be permanently installed;

Platforms which are of retractable design include clear instructions in relation to the safe deployment of the platform which shall be provided at the Working Area and in the O&M Manual.

The design and construction of any retractable platform shall be in accordance with the requirements and provisions set out at Section 5.2.6.4.5 of BS EN81-20;

Permanent lighting is installed providing a minimum level of illumination 200 lux and incorporate emergency lighting in accordance with the requirements of this Specification.

Machinery Outside the Lift Well

Shall be designed and constructed such as to:

Include a dedicated and suitably design cabinet which shall be designed and constructed in accordance with the requirements of Section 5.2.6.5 of BS EN81-20;

Permit easy and safe working on the equipment through the open door;

Provide a clear height of at least 2.1 M at all working areas;

Provide a clear height of at least 1.8 M for moving between one work area and another;

Provide a clear horizontal area of at least 0.5 M x 0.6 M at parts which require maintenance and inspection;

Incorporate provisions for emergency operation and test operations;

Provide a clear horizontal space at the front of control panels and cabinets which is not less than 0.7 M, measured from the front face of the enclosure, and the full width of the cabinet or panel, and in no case less than 0.5 M.

Include permanent lighting providing a minimum level of illumination 200 lux and incorporate emergency lighting in accordance with the requirements of this Specification.

Working Areas Outside the Lift Well

Shall be designed and constructed such as to:

Permit easy and safe working on the equipment;

Provide a clear height of at least 2.1 M at all working areas;

Provide a clear height of at least 1.8 M for moving between one work area and another;

Provide a clear horizontal area of at least 0.5 M x 0.6 M at parts which require maintenance and inspection;

Provide a clear horizontal space at the front of control panels and cabinets which is not less than 0.7 M, measured from the front face of the enclosure, and the full width of the cabinet or panel, and in no case less than 0.5 M;

Permit access to the equipment only by way of an Inspection Door which shall be designed and constructed in accordance with the requirements of Section 5.2.3 of BS EN81-20 and which is of dimensions 0.5 M in height and 0.5 M in width and which shall permit the required work to be carried out through the door;

Include permanent lighting providing a minimum level of illumination 200 lux and incorporate emergency lighting in accordance with the requirements of this Specification.

SILENT OPERATION

The Lift Contractor shall include for taking every practical precaution to ensure quiet operation of the new equipment.  Every practical precaution shall also be taken to prevent vibration being transmitted to the building structure from all items of the lift equipment.  The Lift Contractor shall indicate, at Section 10 of this Specification, the proposed methods which he proposes to adopt in order to assure quiet operation, and provide details of the noise and vibration levels which are guaranteed to be achieved by the completed installation.

BRE Environmental Assessment Method (BREEAM) for Buildings

The lift system shall meet the criteria for best practice in sustainable design and hence contribute to the environmental performance of the building.  All of the following features shall be incorporated into the lift installation to maximise the award of BREEAM credits:-

- Provision of PIR control of car lights and ventilation fan to ensure automatic shutdown when not in use.

- Provision of LED car lighting or similar low energy light fitments.

- Standby mode on controllers and drives to reduce power consumption to a minimum during periods of inactivity.

- Regenerative feature on drives (Indicate Optional Cost).

COMMISSIONING, ACCEPTANCE PROCEDURE AND SERVICE MANUALS

SECTION 8

## COMMISSIONING, ACCEPTANCE PROCEDURE AND SERVICE MANUALS

Commissioning and Acceptance Procedure

The Lift Contractor shall agree a full commissioning and testing programme with the Engineer.  Prior to offering the installation to the Engineer for acceptance tests, the Lift Contractor shall carry out full tests in compliance with BS8486-1:2007 (or BS8486-2:2007 in the case of hydraulic lifts), BS EN81-20, BS EN81-50, the Lifts Regulations 2016 and EU Directive 2014/33/EU and the specific requirements of the Specification.  Any defects identified during or arising from the Lift Contractor’s inspection and testing shall be remedied prior to the installation being offered for acceptance tests.  The Lift Contractor shall further ensure that the whole installation fully satisfies the design criteria and functionality in accordance with the requirements of the Specification.

The Lift Contractor shall make complete records of the tests utilising test sheets, which shall are in full compliance with BS 8486-1:2007 or BS8486-2:2007.

The Lift Contractor shall be responsible for providing all of the instruments necessary to undertake the commissioning and the tests as required by the Engineer, including, but not limited to, test weights, thermometers, noise and vibration measurement devices, electrical test meters, force measurement gauges, deflection gauges and jigs, all of which shall be accurately calibrated and accompanied by current (within 12-months) Calibration Certificates, and to the satisfaction of the Engineer.

The Lift Contractor shall provide the Engineer with not less than five full working days prior notice of his intention to offer the installation for acceptance tests. The Lift Contractor shall confirm this in writing.

The Lift Contractor shall be responsible for all the tests to ensure the proper function and operation of the lift under this Contract.  Prior to acceptance and placing into service the lift shall, under the supervision of the Engineer, pass all of the tests detailed within this Specification or as may be required by the Engineer during commissioning.

- 25% overload test.

- 60 minutes full load test.

- Motor current and speed tests.

- Door Inspection and tests.

- Electrical insulation resistance to earth test, earth loop impedance and RCD test.

- Earth continuity resistance test.

- Full load, full speed safety gear test for both downward movement and empty car test for upward movement.

- Full load and empty car test of the unintended movement protection device.

- Buffer test carried out with contract load and at contract speed.

- Overload test (electrical).

- RCD electrical protective device tests.

- Electrical protective device tests.

- Levelling device tests.

- Car balance tests.

- Noise and vibration tests as specified.

- Fire fighting, disabled evacuation and communication system tests.

In cases where the veracity and/or strength of the mechanical design of elements of the lift structure and/or lift equipment or components under the requirements of BS EN81-20 and BS EN81-50 are determined by way of the assessment material deflection the Lift Contractor shall, at the request of the Engineer, demonstrate compliance as part of the commissioning tests, providing all tools and test equipment required to demonstrate compliance.

The Lift Contractor shall also carry out any other tests required by the Engineer in order to prove that the equipment complies with the requirements of the Contract and with all codes and Regulations relating to the equipment supplied and its installation under the Contract.

The Lift Contractor shall generally demonstrate the lift in operation under various loading conditions from no load to 25% overload in order to check the operation and floor levelling accuracy.

The 25% overload test is to ensure that the equipment installed has an ample safety margin above that of the rated load incorporated in the design.

The lift shall also be subject to a 60-minute test such as to prove the adequacy of all components in terms of achieving the rated duty and minimum starts per hour. The test shall be conducted with the lift car fully loaded, during which it shall stop at each floor in the up and down direction, opening and closing its doors at each stop.  The test shall be continuous, the stops being of 10 seconds maximum duration and with the doors operational.  During the test, the equipment should not overheat, spark excessively, become noisy or operate in a faulty or deficient manner.

All the tests shall be carried out in the presence of the Engineer and the results shall be recorded in a tabulated form for easy checking and reference with the form signed by the Lift Contractor’s representative undertaking the tests.

Health & Safety File and Service Manuals

The Lift Contractor shall provide a separate Health & Safety File as is required under the CDM 2015 Regulations, including residual risks, risk assessments, COSHH data, accident records and all other relevant data and information.

The Lift Contractor shall ensure that the Manuals and Certificates are available at the time of hand over of the Lift in accordance with the requirements of the Lifts Regulations 2016 and EU Lifts Directive 2014/33/EU and all applicable UK Regulation.

Duplicate copies of the Manuals are to be provided and these shall comprise the following:-

Documents

Full written general description of the equipment as installed identifying its main operational features.

Sequence of operations applicable to the functioning of all control apparatus.

Nomenclature detailing all symbols and forms of identification used on or in relation to the equipment and to drawings or circuit diagrams applicable to the installation.

Fully descriptive list of components which it is anticipated may require regular or routine replacement due to wear and tear.  The minimum information provided shall ensure that ordering of replacement components can be achieved.

Maintenance schedules detailing all areas of planned preventative maintenance, routine servicing and including all settings and adjustments together with control and component software parameters.

Wherever any hand held or portable device is used to service, interrogate, alter, modify, adjust, reset and/or recalibrate the lift system and/or components the Lift Contractor shall supply one of these devices for each lift together with clear instructions for the use of the device and all necessary data sheets for the interpretation of information shall be included. The device shall be supplied free of license for the duration of the life of the lift installation, and free of any hire, lease, rental or servicing charges.

Full details of recommended methods of cleaning all finishes, including any special materials required.

Test Certificates

The Lift Contractor shall supply a minimum of two copies of each of the site test certificates in respect of the tests carried out at the time of commissioning of the equipment.  These shall be fully completed and signed by a competent person authorised by the Lift Contractor.

a)	Hoisting ropes	)

) Each certificate identified with its lift number

- Governor ropes	)

- Overspeed governor

- Hoisting motor

- Lift machine brake and brake monitoring

- Door gear motor

- Car and counterweight buffers

- Safety gears lift car (ascent and descent) and counterweight

- Unintended movement protection

- Reports of pendulum tests relating to lift car and landing entrances and doors, lift car enclosure panels, shaft enclosure panels and any glass panels

- Fire Certificate for lift landing and car doors

- Lifting beam or eyes (where applicable)

- Electrical completion certificate to BS 7671

- Certificate of Conformity

Drawings and Circuit Wiring Diagrams

The Lift Contractor shall provide a full set of electrical circuit diagrams which shall incorporate any and all amendments which have been carried out prior to the equipment being accepted by the Engineer.

The Lift Contractor shall supply a complete set of wiring and “as fitted” drawings in respect of the completed lift installation.

The Lift Contractor shall supply a complete set of builders work and general arrangement drawings, including landing entrances and lift car interior perspective.

The “as-fitted” drawings shall record details of any significant residual hazards and risks affecting the installation, the works and the design, which could not be eliminated and/or adequately mitigated in the design, on the final “as fitted” record drawings and in the H&S File.

Inspection Certificates

This section shall be provided for the future retention of Inspection Certificates in accordance with SAFed Recommendations.

Maintenance Contract and Inspection Reports

This section shall be provided for the future retention of maintenance reports and the maintenance contract documents.

### Warranties & Guarantees

Each Manual shall include copies of the manufacturer’s or supplier’s guarantees or warranties in relation to products as described in the Preliminaries Section of this Specification.

Noise & Vibration Tests

Where specified, the Lift Contractor shall carry out a Lift Noise & Vibration test in order to verify that the Performance Criteria, which are detailed in Section 9/10 of this Specification, have been met.

Noise

Noise levels shall not exceed those indicated in the Performance Criteria and the Contractor shall demonstrate, using an approved measuring instrument which has a valid Calibration Certificate, that the installation meets those requirements.

Noise measured in the lift car interior shall be measured at 1.5 M above the floor and 1 M from the face of the car door. A precision grade type 1 sound level meter set to “fast” meter response.

Lift Motor Room

Measurements in the lift motor room and/or measurements in machinery spaces shall be made with a precision grade sound level meter fitted with an octave band filter set.  The positions at which measurements are made should be noted on a drawing showing the principal noise-producing elements of the lift machinery.  No measurement shall be taken closer than 1 M from any wall or floor surface. All measurements are to be made using the “fast” meter response.

The dBA level over a complete cycle of lift operation shall not exceed the values indicated in the Performance Criteria.

The Lift Contractor shall allow for all openings between the machine room and the shaft (including rope holes) to be acoustically lined.

Noise levels measured on the lift landings shall be measured 1 M from the face of the landing doors at a height of 1.5 M above the floor.

Lift Car

The noise levels in the lift car shall be measured in the centre of the lift car, 1.5 M above floor level, and during a full cycle in each direction of travel, as defined below, with both vent fan running and with this switched off.

Lift Vibration

Vibration measurements are to be taken at the centre of the lift car, on the floor, and reflecting three mutually perpendicular axes corresponding to vertical, front-to-back, and side-to-side.  Measurements shall be made, using an approved measuring instrument which has a valid Calibration Certificate, of noise and vibration levels in each direction of travel and over two complete travel cycles, one from the lowest floor of the building to the top, and one from the highest floor to the bottom.

A cycle is defined as the period from just prior to the doors starting to close at one level, to just after the doors open at the destination level.

Vibration levels shall be measured in mg, as r.m.s. values using a time constant of 0.125 seconds (“fast”), and with the maximum values recorded in each 1/3 octave band from 1 Hz to 80 Hz inclusive over each complete cycle.

Levels of acceleration, deceleration and jerk rate shall also be measured and recorded.

Handover Procedure

Prior to offering the equipment for acceptance, the Lift Contractor shall ensure that all works identified during the witness tests as remedial items have been satisfactorily completed and that the Operating and Maintenance Manuals with complete with all Certification and the complete CDM 2015 H&S File are available.

Should the handover be delayed because remedial items are outstanding, the commencement of the Defects Liability Period shall be deferred until such time as all outstanding works and items are complete to the satisfaction of the Engineer.

Prior to, or during handover, the Lift Contractor shall provide on-site training to the Purchaser’s representatives, comprising of practical instruction and demonstration of safe passenger release procedures and emergency handwinding/lowering.  This shall also include instruction in relation to procedures for calling the Lift Contractor in the case that safe release should be unsuccessful or deemed unsafe for the Purchaser’s representative to undertake.

At handover, the Lift Contractor shall provide for the Purchaser’s use the following:-

- 3 sets of keys for each key switch on each lift installation.

- 3 landing door release keys.

- A typed document, which is encapsulated in plastic, providing full details of the Lift Contractor’s local and national emergency breakdown and call out procedure inclusive of phone numbers.

- Certificates of personnel trained in emergency release and handwinding/lowering procedures.

MAINTENANCE

SECTION 9

# MAINTENANCE

Maintenance and Continuity of Lift Service During the Works

The following provisions and duties will form part of the contracted Works.

On the date of possession the Lift Contractor shall assume full responsibility for the condition and safe operation of all of the lifts until such time as his duties under the Contract are wholly discharged.

Dismantling of equipment and all removals and replacements shall be carried out by the Lift Contractor as part of the Works and shall be so undertaken as to maintain continuity of lift service at all times.

Maintenance of the existing lift/s during the site works shall be undertaken by the Lift Contractor who will provide a service corresponding to the requirements of the Comprehensive Form of Maintenance Contract as detailed in this Specification.

On completion of each lift, and upon the dismantling of the next lift, the newly completed lift will be made available for general use and the maintenance service corresponding to the requirements of the Comprehensive Form of Maintenance Contract, as detailed in this Specification, shall be applied to that lift. These arrangements shall remain in place and continue until the completion of the Works and the commencement of the Defects Liability Period.

The Defects Liability Period is to be deferred and will not commence until the final lift is complete and commissioned.

## Comprehensive Form of Contract

## Maintenance

The Lift Contractor shall provide a price for providing the Comprehensive Form of Maintenance Contract in the Summary of Prices, at Section 9 of this Specification.  The Lift Contractor shall provide samples of the proposed schedule of planned preventative maintenance and record cards with the Tender.  Upon commencement of the Defects Liability Period these shall be in place in the machine room and shall be completed at each maintenance visit.

The Lift Contractor shall provide for monthly maintenance visits and repair service in full compliance with the Comprehensive Form of Contract, for the duration of the Defects Liability Period.

The terms of the comprehensive contract shall apply between the hours of 08.00 – 18.00 7 days per week including bank holidays.

At monthly intervals throughout the Defects Liability Period the Lift Contractor shall provide computer generated reports in relation to breakdowns and call outs for the previous period, with detail of each breakdown.

Comprehensive Form of Contract

Excluded from the Lift Contractor’s responsibility on maintenance are:-

- Decorative finishes of the car enclosure, car and landing entrances except where damage is a result of the Lift Contractor’s own negligence and/or misuse or abuse.

- Cleaning of the lift shaft fabric and enclosure walls.

- Buried (underground) piping and cylinders on hydraulic lifts.

- The incoming electrical mains power supply cable to both power and lighting circuits in connection with the lift installations.

- Failure of the lift equipment due to misuse with such repairs, where established as due to misuse, will be chargeable as an extra to the Contract.

Included in the Lift Contractor’s responsibility is the provision of all labour and materials required for the correct adjustment, repair and/or replacement, as conditions warrant, of all other component parts of the lift installation which are not specifically excluded here above.

Cleaning of all equipment in the lift machine room, machinery spaces, lift shaft and lift pit, such as to ensure that the areas and equipment are kept clean at all times and free of rubbish and potentially inflammable material.

Provision of all cleaning materials and the correct lubricants, which are in accordance with the equipment manufacturer’s specifications, such as to ensure the correct maintenance of the lift equipment.  No stocks of lubricating oil or lubricants of an inflammable nature are to be retained on site at any time.

Whenever the lift is not available for service due to this being in the control of the Lift Contractor during works or inspections, the Lift Contractor shall provide a suitable barrier at each lift entrance under inspection to indicate that the installation is not available for service.  A sample design of the barrier shall be submitted for approval to the Purchaser’s Representative.  When not in use, the barrier shall be retained in the lift machine room or machinery space and mounted on purpose made brackets, or at an agreed location on the site.  At the expiry of the maintenance contract, the barrier shall remain as the property of the Purchaser.  The barrier shall be collapsible in design, painted safety yellow and be fitted with a suitable “DANGER” notice and designed and constructed in accordance with the requirements of BS7255.

“Out of service” indication notices shall be placed on each landing whenever a lift is removed from service for either maintenance or repair.

All inspections in compliance with the SAFed Recommendations, as these are amended from time to time, are to be undertaken as these fall due (Annuall, 5-yearly and 10-yearly) and copies of the Certificates shall be provided to the Purchaser’s Representative.

- Gear box, brake, sheaves and pulleys.

- Safety gear, governor rupture valves and associated devices.

- Unintended movement device

- Leveling and re-leveling devices.

- Locks and interlocks.

- Terminal limits.

- Rams, cylinders and chains/ropes for hydraulic lifts.

- Electrical safety devices.

- Overload devices.

- Electrical tests as required by BS 7671.

A reasonable stock of replacement lamps and fluorescent tubes for use within the motor room, machinery spaces, lift shaft, lift car and all indicators and push units shall be retained in the lift machine room and/or machinery space.

Within one month following each maintenance visit a Report shall be forwarded to the Purchaser’s Representative.  All reports shall:

- Relate to one visit to each of the lifts.

- State clearly the work done and adjustments made and indicate which car and/or landing indicator lamps, if any, were renewed at the time of the visit.

- Certify that the lift is in a satisfactory safe and serviceable condition, or in the alternative suitably advise the Purchaser’s Representative.

- Give details of attendance to any breakdowns during the period since the date of the preceding Report.

The Lift Contractor shall include for providing full instruction as to the running and operation of the lifts to the Purchaser’s appointed staff, including safe passenger release and emergency handwinding/lowering procedures.  Each person trained shall be issued with a Certificate by the Lift Contractor.  This training shall be carried out annually under the Maintenance Contract.

The Lift Contractor shall include for annual re-programming of the auto dialer.

The Comprehensive Contract shall include for operational guarantees by the Lift Contractor to the Employer for:

i)	Response times to breakdowns not exceeding:

45 minutes - at any time when a person is trapped within the car

2 hours – during normal operating hours     ) where no trapping has

3 hours – outside normal operating hours    ) occurred

ii)	Guarantees against failure.  This will be a maximum number of:

5 failures per lift, per annum maximum.

- The Lift Contractor shall refund to the Purchaser as financial compensation a sum equivalent to 1% of the contract sum for the lift for each failure above the agreed rate. This provision shall be operational immediately following the 24 months Defects Liability Period.

- Repair and replacement component availability to be stated, including an agreed schedule of “down” time.

- Maintenance during agreed periods as determined by the Purchaser’s requirements.

- Rebate in full, or rescheduling, at the Purchaser’s discretion, of any missed maintenance visits.

- Maintenance visits planned and advised in advance by means of annual planner provided at handover.

- 6 sets of encapsulated details to be provided at handover giving full details of contact procedure for trappings, breakdowns and routine maintenance.

Tenderer………………..

TENDER PARTICULARS

SECTION 10

The Lift Contractor should note that if at the time of evaluation of his Tender all technical and other details within this document have NOT been completed, this will cause his offer to be invalidated.

- TENDER PARTICULARS – Machine Room-less Lift

The Lift Contractor must submit the following information at the time of Tender.

- Technical and Constructional Details of Equipment

The Tenderer shall supply the following information.

COMPLIANCE WITH STANDARDS

In addition to compliance with the requirements of the Lifts Regulations 2016, BS EN81-20 & BS EN81-50 the Lift Contractor shall confirm compliance in full with the following:

BS EN81-70 Accessibility	Yes/No

BS EN81-71 – Vandal Resistance – Category 1	Yes/No

BS EN81-71 – Vandal Resistance – Category 2	Yes/No

BS EN81-72 – Fire Fighting	Yes/No

BS EN81-73 – Fire Recall	Yes/No

BS EN81-21 – Existing Building (Lift Contractor to include details

of headroom & pit refuge space safety provisions)	Yes/No

BASIS OF LIFT DESIGN

Passenger Lift to BS EN81-20 & 50	Yes/No

Passenger Lift to BS EN81-20 & 50 (with Mobility Scooter loading) 	Yes/No

Goods Passenger Lift to BS EN81-20 & 50	Yes/No

LIFT MACHINE

Machine bearers, type and size	--------------------

Method of vibration isolation	--------------------

Type and size of pockets or pad stones

required for support	--------------------

METHOD OF EMERGENCY OPERATION

Manual means	--------------------

Electrical means	--------------------

Means of driving lift out of balance (if required)	--------------------

MOTOR

Type, including Trade Name Rating

In HP or kW	--------------------

Speed in RPM	--------------------

Duty Cycle (starts per hour)	--------------------

Heat output at full load & duty	--------------------

F.L. starting current	--------------------

F.L. running current	--------------------

Power factor	--------------------

Name of manufacturer	--------------------

MOTOR PROTECTION

Type, state number of protective devices	--------------------

Time for protection to trip on low speed stall	--------------------

Time for protection to trip on high speed stall	--------------------

REGULATOR

Manufacturer	--------------------

Reference	--------------------

Type	--------------------

Starting Current	--------------------

F.L running current	--------------------

Power factor	--------------------

Type of filters	--------------------

EMC compliance?	--------------------

CE marking	--------------------

Method of feedback	--------------------

Regeneration to mains?	--------------------

TRACTION AND DIVERTOR SHEAVES DRIVE

Maximum suspended load on drive sheave	--------------------

Traction sheave diameter	--------------------

Traction sheave hardness	--------------------

Divertor sheave diameter	--------------------

Location of divertor sheave	--------------------

Rope pressure	--------------------

- BRAKE ASSEMBLY

Diameter of brake drum	--------------------

Number of brake shoes	--------------------

Width of brake shoe	--------------------

Number of springs	--------------------

Coil voltage and current	volts------------

Amps-----------

Manufacturer	--------------------

Brake monitoring to EN81-20/50?	--------------------

- OVERSPEED GOVERNOR

Method of tripping at contract speed	--------------------

Method of remote tripping/resetting	--------------------

Electrical trip speed	--------------------

Mechanical trip speed	--------------------

Rope diameter and construction	--------------------

Manufacturer and type No.	--------------------

CE marked?	--------------------

CONTROLLER

Location	--------------------

Dimensions	--------------------

Manufacturer	--------------------

Type	--------------------

Voltage	--------------------

Method of achieving lamp reliability	--------------------

Description – tick as appropriate

Location:	Wall -------------

Floor ------------

Access:	Front ------------

Rear -------------

Expected Life of Solid State Components	--------------------

Method of temperature monitoring	--------------------

Heat output	--------------------

CE Marked?	--------------------

GUIDES	*width/depth/blade

Car: “T” number and size	--------------------

Counterweight:  “T” number and size	--------------------

Maximum pitch of fixing	--------------------

Fixing type	--------------------

GUIDE SHOES

Make and type	--------------------

Dimensions of guide shoe	--------------------

Diameters of rollers (if applicable)	--------------------

Method of self-adjustment	--------------------

Method of lubrication	--------------------

BUFFERS

Car: type and number	--------------------

Counterweight: type and number	--------------------

Rate of retardation	--------------------

CE Marked?	--------------------

CAR AND FRAME

Total weight of car and sling	--------------------

Load weighing devices, type and number	--------------------

Method of car balancing	--------------------

Method of car body isolation	--------------------

Maximum weight of finishes	--------------------

Max force applied at car sill during loading (% of rated load)	-----------------%

SAFETY GEAR

Description	--------------------

Makers name and type number	--------------------

CE Marked?	--------------------

UNINTENDED MOVEMENT

Means of detection	--------------------

Means of prevention	--------------------

Means of actuation	--------------------

CE marked?	--------------------

SUSPENSION ROPES

Number and diameter	--------------------

Tensile strength	--------------------

Construction and lay	--------------------

Breaking force per rope/chain	--------------------

Method of termination	--------------------

Method of rope isolation/equalising	--------------------

Current selling price per/M rope/chain/belt		---------------------

CAR ENCLOSURE

Name of supplier/manufacturer	------------------

Number of car top refuge spaces		-------------------

MECHANICS CAR TOP CONTROL STATION

Name of supplier/manufacturer	------------------

MECHANICS LIFT PIT CONTROL STATION

Name of supplier/manufacturer	------------------

Number of pit refuge spaces	------------------

PIT ACCESS LADDER

Name of supplier/manufacturer	------------------

BS EN81-20 Design Type (Type 1, 2a, 2b, 3a, 3b or 4)	------------------

Electrical Safety Switch	------------------

DOOR OPERATOR/DOOR EQUIPMENT

Make and type number	--------------------

Method of car/landing coupler	--------------------

Rated starts per hour	--------------------

Life expectancy of belts, if used	--------------------

AC or DC	--------------------

Method of speed control and adjustment	--------------------

Opening speed (std)	--------------------

Closing speed (std)	--------------------

Pre-opening? 	--------------------

Type of car door lock	--------------------

CE marked?	--------------------

Means of emergency release	--------------------

Method of isolation from car bodywork	--------------------

Size and construction of bottom guides	--------------------

Construction of door panels	--------------------

Method of sound deadening	--------------------

Method of self-closing	--------------------

Minimum clear opening width	-------------mm

Minimum clear opening height	-------------mm

Hard pendulum shock test to S.5.14 BS EN81-50?	Yes/No

Soft pendulum shock test to S.5.14 BS EN81-50?	Yes/No

DOOR SAFETY DEVICES

Type of landing lock	--------------------

Voltage of lock circuits	--------------------

CE marked?	--------------------

Emergency release type	--------------------

Means of releasing lowest lock from within the lift pit	--------------------

- DOOR PROTECTIVE DEVICE

Manufacturer and reference	--------------------

Number of beams	--------------------

Extent of detector field on to landing	--------------------

Location of device (door edge/

back of sill)	--------------------

LIMITS AND SWITCHES

Type and make of limit switches	--------------------

CE marked?	--------------------

Type and make of inductors	--------------------

Number of inductors used in the system	--------------------

Method of mounting inductors in shaft	--------------------

AUTO RECHARGE UNITS

Make and type number	--------------------

Total power output in watt/hours	--------------------

Consumption of emergency lighting	--------------------

Consumption of alarm bell	--------------------

MAINS SUPPLY

Main switch type and rating	--------------------

Fuses type and rating	--------------------

Mains riser rating and construction	--------------------

WIRING

State method of wiring and protection	--------------------

TRAVELLING CABLES

Type of trailer and construction	--------------------

Manufacturer	--------------------

Number of ways	--------------------

Type of suspension anchorage	--------------------

Make of travelling cable	--------------------

Make of anchorage system	--------------------

PUSHES & FIXTURES

Controller/emergency panel location	--------------------

Size	--------------------

Finish of Door	--------------------

Manufacturer and reference of landing

call units	--------------------

Location of braille/tactile markings	--------------------

Method of illumination	--------------------

IPX rating	--------------------

Manufacturer and reference of position

indicators	--------------------

IPX rating	--------------------

Manufacturer and reference of direction

indicators	--------------------

IPX rating	--------------------

Manufacturer and reference of car

operating panel	--------------------

IPX rating	--------------------

Grade of material and finish	--------------------

Contractor to supply illustrations and

descriptions of all units in the

supporting documents	--------------------

VOICE SYNTHESISER

Manufacturer and model	--------------------

Method of voice reproduction	--------------------

Maximum number of messages	--------------------

On site re-programmable	--------------------

Location of speaker	--------------------

Location of inductive loop	--------------------

- AUTO DIALER

Manufacture and model	--------------------

No. of numbers	--------------------

Message enunciator	--------------------

Line requirements	--------------------

Speaker/Mic location	--------------------

ADDITIONAL INFORMATION

Premises where a similar installation may be

viewed and performance characteristics as

given in 10.2 be checked	---------------------

Forecast of life of the installation based

on anticipated usage	---------------------

- MAXIMUM HEIGHT OF EQUIPMENT

(a)	Hoisting unit	--------------------

(b)	Controller cabinet	--------------------

This Schedule must be completed in every particular, signed and dated and returned with the Tender.  Any deviations from the Specification and any other information relevant to the Tender shall be set out by the Lift Contractor on a separate sheet as an additional Schedule of Particulars.

NAME OR TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE----------------------------------------------------------DATE--------------------------------

NAME-----------------------------------------------------------------------------------------------------------

Noise and Vibration – Machine Room-less

State expected levels of noise and vibration in the various conditions.  The Lift Contractor shall be expected to provide all necessary instrumentation to demonstrate these criteria are met.

Minimum

Standards

Acceptable

Noise level in shaft 1m from

Motor under all load conditions	------dBA		65  dBA

Car interior fan on	------dBA		60  dBA

Car interior fan off	------dBA		50  dBA

1m from landing doors on

landing during lock

engagement	------dBA		55  dBA

Acceleration rate	------m/s²		1.0  m/s²

Jerk rate	------m/s³		1.5  m/s³

Vibration in car mg 2 – 15 Hz

Vertical	------mg		20  mg

Horizontal	------mg		20  mg

# Structural Loadings - Traction

| Horizontal force X (Kilo Newtons) due to thrust of guide shoes on front face of guide rail at any one fixing. |  |
| --- | --- |
| Horizontal force Y (Kilo Newtons) due to thrust of guide shoes on side face of guide rail at any one fixing. |  |
| Downward force Z (Kilo Newtons) due to operation of safety gear imposed on any one fixing. |  |
| Reaction (Equivalent Dead Load) on pit floor under any one guide rail due to operations of the car safety gear. |  |
| Reaction (Equivalent Dead Load) on pit floor under any one buffer due to car buffering. |  |
| Number of buffers |  |
| Reaction (Equivalent Dead Load) on pit floor due to counterweight buffer. |  |
| Number of buffers |  |

NAME OR TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE---------------------------------------------------------------------DATED-------------------

NAME-----------------------------------------------------------------------------------------------------------

## Production Schedule

To be completed by the addition of the appropriate program dates and returned with the Tender).

Lift 1	Lift 2

Date of order instructions to

proceed	-----------	-----------

Builder’s work GA drawings

submitted to Contract

Administrator	-----------	-----------

Lift car construction and design

drawings submitted to

Contract Administrator	-----------	-----------

Commencement of materials

procurement	-----------	-----------

Completion of materials

procurement	-----------	-----------

Completion of manufacturing

Drawings	-----------	-----------

Major components available

for off-site inspection, in

particular the gear/motor

assemblies, controllers, car

frame and safety gear	-----------	-----------

Lift car erected fully

complete and illuminated and

available for off-site

inspection	-----------	-----------

Complete all manufacturing	-----------	-----------

Commence deliveries to site	-----------	-----------

The Lift Contractor, in completing this Schedule, is to state the most favourable deliveries and program he is able to achieve.  It should be noted that in evaluating the submitted Tender, program and delivery will be taken into account.

NAME OR TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE---------------------------------------------------------------------DATED-------------------

NAME-----------------------------------------------------------------------------------------------------------

# Schedule of Site Works

|  | Lift 1 | Lift 2 |
| --- | --- | --- |
| Total No. of Days for Installation Phase |  |  |

Total number of person days on site (CDM 2015 Regulations) _____ Days.

The Lift Contractor to provide separate method statement fully detailing the operations to achieve these periods.

NAME OR TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE---------------------------------------------------------------------DATED-------------------

NAME-----------------------------------------------------------------------------------------------------------

# Schedule of Working Hours

The Lift Contractor is to insert in the Schedule the starting and finishing hours for his operations to achieve the periods detailed in the Schedule of Site works.

Monday – Friday	……………am	……………pm

Saturday	……………am	……………pm

Sunday	……………am	……………pm

NAME OR TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE---------------------------------------------------------------------DATED-------------------

NAME-----------------------------------------------------------------------------------------------------------

# Schedule of Work to be Sub-Let

This Schedule must be completed and returned with the Tender.

Failure to comply may disqualify the Tender.

The Lift Contractor is to give below the names and addresses of those firms to whom it is proposed to sub-let portions of the work not normally carried out by himself.

This Schedule shall not be subsequently modified without prior permission in writing from the Engineer.

The Engineer reserves the right to reject any proposed sub-contractor and to request an alternative.

The Lift Contractor shall provide copies of invoices from vendors or sub-contractors at the Engineer’s request, showing an agreed on cost of ------%.

---------------------------------------------------------------------------------------------------------

Name and address					Work to be sub-let

of proposed Sub-Contractor

---------------------------------------------------------------------------------------------------------

NAME OR TRADING NAME OF TENDERER-------------------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE----------------------------------------------------------DATE--------------------------------

NAME-----------------------------------------------------------------------------------------------------------

# Schedule of Day-work Charges

We undertake to execute any works specifically authorised to be charged at daywork rates at net cost plus the following percentages:

| Labour | Plus % |
| --- | --- |
| Fares & Allowances | Plus % |
| Materials | Plus % |
| Plant | Plus % |
| Sub-Contractors | Plus % |
| Contractor’s percentage to be added to Prime Cost Items (MF/1 Rev 6 c.5.1) if applicable | Plus % |

NOTE:

On-costs include establishment charges and all insurance and holiday with pay contributions.

Labour to be wages of work people (ie chargehands, fitters and mates, but not weekly or monthly paid foreman, supervisors, draughtsmen, storemen and clerks) based on trade union rates including overtime and payments in respect of travelling based on time or distance.

Allowances will comprise outworking lodgings, out of pocket expenses and dirty money payments.  Fares and allowances for broken days are to be calculated on the percentage of a full week’s labour excluding overtime.

Materials to be at net cost (delivered to site) and after deducting all discounts.

The Lift Contractor shall enter below the net basic labour rates on which the tender is based and shall add rates of any work people which it is proposed to bring onto site.

|  |  | Normal Working Hours |  |  | Out of Normal Working Hours |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | a |  | b | c |  | D |
|  | Between 0800-1700 |  | Between 1700-1900 | After 1900 hrs & Sat |  | Sundays & Bank Holidays |
| Fitter | £ p/h |  | £ p/h | £ p/h |  | £ p/h |
| Mate | £ p/h |  | £ p/h | £ p/h |  | £ p/h |
| C/hand | £ p/h |  | £ p/h | £ p/h |  | £ p/h |

NAME OR TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE----------------------------------------------DATE--------------------------------------------

NAME-----------------------------------------------------------------------------------------------------------

# SUMMARY OF PRICES – All costs are totals for both lifts

All prices to be net, fixed for the duration of the contract program.

CONTRACT PRELIMINARIES 	£……………………

COMPLIANCE WITH CDM 2015 REGULATIONS		£……………………

NOTIFIED BODY APPROVALS		£……………………

COMPLIANCE WITH BS EN81-20 & 50, LIFTS

REGULATIONS 2016 & DIRECTIVE 2014/33/EU		£……………………

DESIGN, MANUFACTURE, DELIVER, INSTALL AND

COMMISSION 2 NO. LIFTS		£……………………

REMOVAL OF EXISTING EQUIPMENT		£……………………

BUILDERS WORK		£……………………

ELECTRICAL WORK		£……………………

RETENTION BOND		£……………………

MAINTAIN LIFT EQUIPMENT DURING DEFECTS LIABILITY	£……………………

PROVISIONAL SUM FOR CONTINGENCIES	£15,000.……………

TOTAL SUM TO FORM OF TENDER		£……………………

## OPTIONAL ITEMS

Additional price for electrical emergency operation  	£……………………

Additional price for regenerative drive	£……………………

Additional price for installation of a new electrical mains supply	£……………………

## MAINTENANCE

Comprehensive Maintenance after Expiry of Defects

Liability Period Per 		£……………………

NAME OF TRADING NAME OF LIFT CONTRACTOR--------------------------------------------

ADDRESS-----------------------------------------------------------------------------------------------------

SIGNATURE--------------------------------------------DATE----------------------------------------------

NAME-----------------------------------------------------------------------------------------------------------

FIXED PRICE FORM OF TENDER

FOR

FULL REPLACEMENT OF 2 NO. PASSENGER LIFTS

AT

MERSEYSIDE MARITIME MUSEUM

To:	National Museums Liverpool

I/We the undersigned hereby undertake to execute and complete the whole of the Works described in strict conformity with the Specification and to the satisfaction of the Engineer in a sound and workmanlike manner and to commence work on site within a period of …….. weeks after the placing of the Order and to complete the work within the contract period of …….. weeks

for the sum of :-							£----------------------------

which sum includes for all primary costs, provisional and contingency sums mentioned in the Specification, but is exclusive of Value Added Tax.

It is understood that this tender sum has been prepared on a Fixed Price Basis with all prices fully fixed for the duration of the total programme given above.

This offer will remain open for three months from the date of Tender.

For and on behalf of ----------------------------------------------------------------------------------------

Address --------------------------------------------------------------------------------------------------------

Telephone No ------------------------------------------------------------------------------------------------

Signature ---------------------------------------------- Position --------------------------------------------

Date -------------------------------------------------------------------------------------------------------------

The Lift Contractor shall return the fully completed tender documents via email to;

tenders@liverpoolmuseums.org.uk

subject title 'Merseyside Maritime Museum Passenger Lifts Replacement'

By Thursday 7th December 2017                            by    12 Noon