|  |  |  | Bay 3/21 Spring Place 105 Commercial Road Southampton SO15 1EG United Kingdom |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| All Applicants for the REFURBISHMENT WORKS AT CROSSKILL HOUSE, MCA HULL MO (BEVERLEY) Via Contracts Finder |  | Tel: E-mail: | 020 381 72476 contracts@mcga.gov.uk |  |  |
|  |  | Your ref: Our ref: |  | TCA 3/7/1018 |  |
|  |  | 12 September 2017 |  |  |  |

Dear All

Tender for REFURBISHMENT WORKS AT CROSSKILL HOUSE, MCA HULL MO (BEVERLEY)

Further to the QA document released 11 September, the MCA received a follow up query in response to the clarifications answers provided.

Question (email in full, dated 11/09/17):

“Many thanks for this, the documents refer to the manufacturers of the lighting and lighting control system, yet fails to mention who the manufacturers are, please confirm who the manufacturers are, to enable us to make contact, knowing the type of lighting control system installed will enable us to have a better understanding of possible repair costs.

I was under the impression we were going to receive photographs of the main switchroom and respective switchgear to enable us to determine how we are to feed the proposed new distribution boards, when might these be received?”

Answer:

The MCA are engaging with DVLA/DeFRA to confirm original OEM for the lighting scheme and will publish this as soon as it is available.

During the site visit, a question was raised around access to the plant room and visibility of the distribution boards relating to the ground floor ingoing works for MCA HVAC. Gleeds clarified this as a requirement for pictures of the distribution board for the MCA area of demise on the ground floor.  This has been published.

The MCA now understand the requirement relates to new LV distribution on the first floor and reconfiguration of electrical services, in the area vacated by the MCA (36.04 of the SOW). We have an outstanding query to provide photographs of the main switchgear, distribution arrangement in DeFRAs plant room.  We are awaiting feedback on this from DeFRA and their appointed service agent and would hope to have this available and published prior to Fridays deadline.  In lieu of this information not being available, the MCA would accept tenders that identify a split of the existing services, detailing how this supports separately metered services into each discrete area.

We have obtained photographs of the 2.No existing distribution boards in the vacated MCA first floor demise, please see below: